## All (hidden)
Bidder | Expert | Chapter in RfP | Topic | Subtopic | Clause | Criteria | 1 Vital 2 Valuable 3 Not Important | Link to Bidders Documents | Pass =1 | Fail =1 | Open =1 | Question to bidder for clarification | Comments | Comments QA on Criteria | Comment on "Comments" | Typical Questions to be send to bidders if Open status | Standard Text | Check | Prio | Result
Chint | JBU | AC Cabling | AC Cabling | Design factors to be provided | 1.19.1 | AC cable shall be of Copper. Rated voltage, nominal voltage between phase and neutral and nominal voltage between phases to be specified by the Bidder | 1 |  | 1 | [8 empty] | 1 |  | Pass
Chint | JBU | AC Cabling | AC Cabling | Design factors to be provided | 1.19.1 | Appropriate sizing to minimise voltage drop and losses | 1 |  | 1 |  |  |  |  | What is the appropriate size? | leeway to allow MPP tracking when module voltage drops. At least 10%. Ralf, ist Vital kriterium. |  |  | 1 |  | Pass
Chint | JBU | AC Cabling | AC Cabling | Design factors to be provided | 1.19.1 | Bending radius | 1 |  | 1 | [8 empty] | 1 |  | Pass
Chint | JBU | AC Cabling | AC Cabling | Design factors to be provided | 1.19.1 | Cable installation shall ensure grounding and short-circuit protection | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Chint | JBU | AC Cabling | AC Cabling | Design factors to be provided | 1.19.1 | Cables shall be suitable for the environmental conditions at the project site, including UV protection (The Bidder shall provide certification from manufacturer) | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Chint | JBU | AC Cabling | AC Cabling | Design factors to be provided | 1.19.1 | Installation to be verified by measurement-protocols | 1 |  | 1 | [8 empty] | 1 |  | Pass
Chint | JBU | AC Cabling | AC Cabling | Design factors to be provided | 1.19.1 | Lifetime longer than 25 years | 1 |  | 1 | [8 empty] | 1 |  | Pass
Chint | JBU | AC Cabling | AC Cabling | Design factors to be provided | 1.19.1 | Rated voltage | 1 |  | 1 | [8 empty] | 1 |  | Pass
Chint | JBU | AC Cabling | AC Cabling | Design factors to be provided | 1.19.1 | Sufficient and effective cable protection against attacks of rodents for any cabling underground or above is required | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Chint | JBU | AC Cabling | AC Cabling | Specific Requirements | 1.19.3 | The runs of both the main DC and AC cables, in the System layout, should be adjusted to keep power losses below <1% at STC (Design calculations through cable loss simulation to be provided for review & comment). | 1 |  | 1 |  |  |  |  | Part of system design | Kategorie ? |  |  | 1 |  | Pass
Chint | JBU | AC Cabling | AC Cabling | Standards | 1.19.2 | DIN-VDE-0276 | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Chint | JBU | AC Cabling | AC Cabling | Standards | 1.19.2 | EN 60332-1-1 and EN 60332-2-1 | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Chint | JBU | AC Cabling | AC Cabling | Standards | 1.19.2 | IEC 60364 | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Chint | JBU | AC Cabling | AC Cabling | Standards | 1.19.2 | IEC 60502 | 1 |  | 1 |  |  |  |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  |  |  | 1 |  | Pass
Chint | JBU | AC Combiner Box | AC Combiner Box | Design factors to be provided | 1.20.1 | Class 2 AC surge arrestor | 1 |  | 1 |  |  |  | not applicable |  |  |  |  | 1 |  | Pass
Chint | JBU | AC Combiner Box | AC Combiner Box | Design factors to be provided | 1.20.1 | Flame test | 1 |  | 1 |  |  |  | not applicable |  |  |  |  | 1 |  | Pass
Chint | JBU | AC Combiner Box | AC Combiner Box | Design factors to be provided | 1.20.1 | Load breaker switch of adequate size | 1 |  | 1 |  |  |  | not applicable |  |  |  |  | 1 |  | Pass
Chint | JBU | AC Combiner Box | AC Combiner Box | Design factors to be provided | 1.20.1 | Operating temperature range | 1 |  | 1 |  |  |  | not applicable |  |  |  |  | 1 |  | Pass
Chint | JBU | AC Combiner Box | AC Combiner Box | Design factors to be provided | 1.20.1 | Rated current | 1 |  | 1 |  |  |  | not applicable |  |  |  |  | 1 |  | Pass
Chint | JBU | AC Combiner Box | AC Combiner Box | Design factors to be provided | 1.20.1 | Rated voltage | 1 |  | 1 |  |  |  | not applicable |  |  |  |  | 1 |  | Pass
Chint | JBU | AC Combiner Box | AC Combiner Box | Design factors to be provided | 1.20.1 | Stripping length of the individual wire | 1 |  | 1 |  |  |  | not applicable |  |  |  |  | 1 |  | Pass
Chint | JBU | AC Combiner Box | AC Combiner Box | Design factors to be provided | 1.20.1 | Waterproof test | 1 |  | 1 |  |  |  | not applicable |  |  |  |  | 1 |  | Pass
Chint | JBU | AC Combiner Box | AC Combiner Box | Standards | 1.20.2 | EN 60529, DIN-VDE-0472 | 1 |  | 1 |  |  |  | not applicable | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  |  |  | 1 |  | Pass
Chint | JBU | AC Combiner Box | AC Combiner Box | Standards | 1.20.2 | IP 67 | 1 |  | 1 |  |  |  | not applicable |  |  |  |  | 1 |  | Pass
Chint | JBS | Physical layout | Auxiliary equipment | Specific Requirements | 1.7.8 | All parts of the installation are covered by two high speed protection schemes, which shall be independent to avoid common mode failures | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | [5 empty] | 1 |  | Open
Chint | JBS | Physical layout | Auxiliary equipment | Specific Requirements | 1.7.8 | The outline of protection schemes shall be shown on the single line diagram (SLD) | 1 | Page 449- 453 | 1 |  |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | [5 empty] | 1 |  | Pass
Chint | JBS | Physical layout | Auxiliary equipment | Specific Requirements | 1.7.8 | Provide complete indicating, regulating, controlling, protecting and interlocking equipment necessary for safe and efficient operation of the plant and substation, including complete protection scheme. | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | [5 empty] | 1 |  | Open
Chint | JBS | Physical layout | Auxiliary equipment | Specific Requirements | 1.7.9 | The scope of the documentation shall cover at least the requirements of IEC 62446. | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  |  |  | C |  | 1 |  | Open
Chint | JBS | Physical layout | Auxiliary equipment | Specific Requirements | 1.7.8 | The Bidder shall include a fire prevention and response plan | 1 | Chapter 2 | 1 | [8 empty] | 1 |  | Pass
Chint | JBS | Physical layout | Auxiliary equipment | Specific Requirements | 1.7.9 | The documentation includes clearly labelled objects and figures annotated in English language. | 1 |  | 1 |  |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | [5 empty] | 1 |  | Pass
Chint | JBS | Physical layout | Auxiliary equipment | Specific Requirements | 1.7.8 | The fire prevention and response plan shall include a fire alarm und detection system with a main panel in the control room | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | [5 empty] | 1 |  | Open
Chint | JBU | Other infrastructure | Auxiliary systems | DC Backup System / uninterrupted power supply (UPS) | 1.25.6 | IEC-60051 and IEC-60439 standards apply | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Chint | JBU | Other infrastructure | Auxiliary systems | Design factors to be provided | 1.25.1 | One administration and office building with car port for 10 vehicles shall be provided, with sufficient space for operating personal, control room, security office, regular office rooms for permanent and visiting staff, meeting room, kitchen sanitary systems (toilet, showers separate for male and female), first aid, control room, electrical rooms, etc. The building shall have windows for office rooms and air conditioning system (split units) for all office rooms. | 1 |  | 1 |  |  |  |  | Priority to be discussed |  |  |  | 1 |  | Pass
Chint | JBU | Other infrastructure | Auxiliary systems | Design factors to be provided | 1.25.1 | Service water system sufficiently sized for cleaning cycle of modules | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Chint | JBU | Other infrastructure | Auxiliary systems | Design factors to be provided | 1.25.1 | Sewage system including sewage disposal for Construction and O&M phase | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Chint | JBU | Other infrastructure | Auxiliary systems | Design factors to be provided | 1.25.1 | Warehouse for spare parts and workshop for minor mechanical/electrical works. | 1 |  | 1 | [8 empty] | 1 |  | Pass
Chint | JBU | Other infrastructure | Auxiliary systems | Design factors to be provided | 1.25.1 | Water storage facility for drinking water, sanitary water (sufficient for 1 week) | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Chint | JBU | Other infrastructure | Auxiliary systems | Guarantees | 1.25.4 | All buildings should be designed in accordance with the requirements of the Pakistan Building Code (available at www.pec.org.pk/buildingcode.aspx) and latest Seismic Provisions 2007. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Link to code |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Chint | JBS | Miscellaneous | Auxiliary systems | Power supply | 1.29.1 | An off-grid power station may need to be provided by the Bidder for commencing the work. Diesel generators shall be arranged by the bidder on its own. | 1 | Page 116 | 1 |  |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | [5 empty] | 1 |  | Pass
Chint | JBU | Other infrastructure | Auxiliary systems | Security Surveillance System | 1.25.5 | The Bidder shall provide security personnel for 24 h / 7 days a week for the whole year | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Chint | JBU | Other infrastructure | Auxiliary systems | Security Surveillance System | 1.25.5 | The system shall comply with insurance requirements | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Chint | JBU | Meteorological Sensors | Auxiliary Systems | Specific Requirements | 1.10.1 | Irradiation and temperature measurements are to be recorded at intervals of 15 min or less. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Chint | JBU | Meteorological Sensors | Auxiliary Systems | Specific Requirements | 1.10.2 | Seven pyranometers shall be placed : three for measuring the horizontal plane irradiation and the others for the in-plane irradiation. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | As in 1.10.2, it is seven pyranometer per system, please clarify the word "per system" | 1.1.1: "100 MWp (DC capacity at Standard Testing Conditions, abbreviated STC … hereinafter called 'the System') " | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Chint | JBU | Meteorological Sensors | Auxiliary Systems | Specific Requirements | 1.10.2 | The irradiation measurement equipment should be calibrated by an independent certified third party at least every two years. The calibration must be traceable to international standards. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Should be checked in list of deviations |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Chint | JBU | Meteorological Sensors | Auxiliary Systems | Specific Requirements | 1.10.3 | Ambient air and the module temperature shall be measured at every 5 installed MWp in conformity with IEC 60751 AA | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Chint | JBU | Meteorological Sensors | Auxiliary Systems | Specific Requirements | 1.10.1 | The equipment should have the capability of recording and storing data for 24 hours using auxiliary DC power. | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  | Should be priority 1 question |  | C |  | 1 |  | Open
Chint | JBU | Meteorological Sensors | Auxiliary Systems | Specific Requirements | 1.10.2 | The pyranometers should conform to the standards of ISO 9060 (SR5: secondary standard) or the WMO classification, and IEC 60904. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Do we need to know some parameter values according to standards mentioned or just a statement of comlience with the standard would be sufficient? | compliance will be necessary, no data due diligence right now. | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Chint | GD | PR and System Performance Guarantee | Compensations | O&M | 1.4.6 | If the successful Bidder defaults in being able to provide the O&M services required for the Systems performance guarantee, then it will be liable to cover all costs – but at least in the amount of Liquidated Damages imposed to the Employer by its PPA agreements - incurred by the Employer, including the loss of the guaranteed electricity export to the grid (but at a minimum rate of USD 0.20-per-kWh) for the disrupted period, in finding and hiring a replacement for the purpose. | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  | Cannot be evaluated at this stage. Only to be checked in list of deviations. |  |  |  | 1 | 1 | Open
Chint | GD | PR and System Performance Guarantee | Compensations | O&M | 1.4.5 | For timely compensation the PR Calculation will be carried out provisionally for each quarter whereby the contractor and employer might jointly agree on different PR values for each quarter. In the last quarter of each calendar year the annual PR compensation of the full year will be carried out and any provisions will be offset by the annual compensation. | 3 |  |  |  | 1 |  |  | Cannot be evaluated at this stage. Only to be checked in list of deviations. |  |  |  | 1 |  | Open
Chint | GD | PR and System Performance Guarantee | Compensations | O&M | 1.4.5 | If the annual measured PR falls below the guaranteed PR value according to Table 1.4.1, the liquidated damages will be levied on the successful Bidder at the rate of USD 0.20-per-kWh or the kWh Value the Employer receives for each kWh of shortfall – whichever is higher. Adjustments shall be made for any events outside the control of the O&M operator as grid outages, from grid operator ordered shutdowns, or force majeure events during the year. | 2 |  |  |  | 1 |  |  | Cannot be evaluated at this stage. Only to be checked in list of deviations. | Only to be checked in list of deviations. |  |  | 1 |  | Open
Chint | GD | PR and System Performance Guarantee | Compensations | O&M | 1.4.5 | In case the PR is higher than the guaranteed PR value, the net value of this excess energy will be shared as follows: 50% towards the asset replacement fund, 25% towards the Employer, 25% towards the O&M contractor | 3 |  |  |  | 1 |  |  | Cannot be evaluated at this stage. Only to be checked in list of deviations. |  |  |  | 1 |  | Open
Chint | GD | PR and System Performance Guarantee | Compensations | System PR | 1.4.4 | If the measured PR within further 30 days does not reach the guaranteed PR, the Employer can demand that the price of the system will be reduced by the percentage of shortfall times 1.2 for liquidated damages or the contractor will have to install more power at its own cost or combination of both. | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  | Cannot be evaluated at this stage. Only to be checked in list of deviations. |  |  |  | 1 | 1 | Open
Chint | GD | PR and System Performance Guarantee | Compensations | System PR | 1.4.4 | The successful Bidder shall conduct the initial PR test for the daylight hours of at least 30 consecutive days, recording data at a frequency of fifteen minute intervals or less, to validate the guaranteed PR value for acceptance. Any excused downtime (e.g., from Grid Operator ordered shutdowns, grid failure, theft, force majeure) will be excluded from that calculation by an independent consultant (Auditing Body). That day will be taken out and another day added, if the initial PR falls short of the guaranteed PR value, the successful Bidder shall be obliged to identify and rectify the causes for the performance shortfall at their own cost. | 2 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  | Cannot be evaluated at this stage. Only to be checked in list of deviations. |  |  |  | 1 |  | Open
Chint | GD | Conditions for Disqualification and Additional Information Required | Credentials | EPC | 1.2.6 | Approval from bidder to owners or owner representatives to answer questions freely regarding the past performance of the bidder and performance of the system against contractual obligations. | 2 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | [5 empty] | 1 |  | Open
Chint | GD | Conditions for Disqualification and Additional Information Required | Credentials | EPC | 1.2.6 | Cumulative MWp of ground mounted PV turnkey installations >5 MWp with stating of actual MWp per project, project location, date of commissioning, module type and Inverter type. | 1 |  | 1 | [5 empty] | experience of Bidder / EPC |  |  | 1 | 1 | Pass
Chint | GD | Conditions for Disqualification and Additional Information Required | Credentials | EPC | 1.2.6 | Detailed list of all the sites with the affirmation that the bidder played the leading EPC role in the turnkey installation of these systems. | 3 |  | 1 | [8 empty] | 1 |  | Pass
Chint | GD | Conditions for Disqualification and Additional Information Required | Credentials | EPC | 1.2.6 | References and contact data (mail and phone) from owners of all installations > 5 MW with quotes of the corresponding system Performance Ratios, as well as system performance vs. initial yield assessment per year since the installation. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  | for selection of referenz objects |  |  | 1 | 1 | Open
Chint | GD | Technical Bid Evaluation Criteria | Credentials | EPC | 1.3.1 | the systems have been completed on time and within budget, | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | [5 empty] | 1 | 1 | Open
Chint | GD | Scope of the Bid | Credentials | EPC | 1.1.9 | The bid includes professional experience of the Bidders in ground mounted utility-scale PV and financial information about their long-term stability | 3 |  | 1 | [8 empty] | 1 |  | Pass
Chint | GD | Scope of the Bid | Credentials | EPC | 1.1.10 | The Bidder, or the Lead company in case of JV is a EPC contractor | 1 |  | 1 |  |  |  |  | This is a non-technical question. We suggest such question should be separated from technical questions and placed in checklist for "General/Substantive Responsiveness of Bid" | a question of reliability and experience of solid understanding of the task/System Technology. See also 1.1.10 |  |  | 1 |  | Pass
Chint | GD | Technical Bid Evaluation Criteria | Credentials | Guarantees | 1.3.1 | To have met the contractual requirements of the EPC and O&M deliverables including certificate to the effect that the entire equipment is brand new as required vide notification number NEPRA/UTS-01/777-779 dated Jan 21 ,2014, | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Only to be checked in list of deviations. |  |  |  | 1 | 1 | Open
Chint | GD | Technical Bid Evaluation Criteria | Credentials | O&M | 1.3.1 | In case of a non-performance, comprehensible evidence has to be given why this case will not affect this project. | 3 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | [5 empty] | 1 |  | Open
Chint | GD | Technical Bid Evaluation Criteria | Credentials | O&M | 1.3.1 | that they have started supplying electricity to the grid and are still operating satisfactorily in 9 out of 10 MW for all the cases | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | [5 empty] | 1 | 1 | Open
Chint | GD | Conditions for Disqualification and Additional Information Required | Credentials | O&M | 1.2.6 | Cumulative MWp of ground mounted PV installations for which O&M services have been delivered by the bidder or his O&M subcontractor. | 2 |  | 1 | [8 empty] | 1 |  | Pass
Chint | GD | Technical Bid Evaluation Criteria | Credentials | O&M | 1.3.2 | Prove at least 100 MW of EPC experience and 50 MW of full O&M experience for a period longer than 24 months. | 1 |  | 1 | [8 empty] | 1 |  | Pass
Chint | GD | Conditions for Disqualification and Additional Information Required | Credentials | O&M | 1.2.6 | References, contact data and approval from owners or owner representatives of all installations > 5 MW from bidder or his O&M subcontractor to answer questions freely regarding the past performance of the bidder and performance of the system against contractual obligations. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | [5 empty] | 1 | 1 | Open
Chint | MAW | Modules | Credentials | Project references | 1.14.8 | To show the proven technology a minimum of 500MW of proposed product type series must be in operation and reference projects shall be named. | 1 | Doc 1&2 page 417, doc 3&4 page 105 |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | approx. 450 MWp named | Related to project references |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Chint | MAW | Inverters | Credentials | Project references | 1.18.10 | A minimum of 100 MWp of similar product/type must be in operation and reference projects shall be named. | 1 | Doc 3&4 page 26 | 1 | [8 empty] | 1 |  | Pass
Chint | MAW | DC Cables | DC Cables | Design factors to be provided | 1.15.2 | String cable shall be of the following type: single conductor type, copper, 1000 V / Class II (according to protection class II / 1000V, IEC 61140, single core cable, tinned copper conductor, XLPE Insulation, double EVA jacket (resistant to heat and cold, resistant to ozone, UV, oil and chemicals), Temperature: 90 º C (Temperature Max. Allowable: 120 º C), Halogen free | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | PV1-F 1*4 | It should be in accordance with the inverter values. | possibly 1500V for such system design | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Chint | MAW | DC Cables | DC Cables | Design factors to be provided | 1.15.2 | Balance of electrical potential | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Need to be disscussed | equipotential bonding earthing mesh | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Chint | MAW | DC Cables | DC Cables | Design factors to be provided | 1.15.2 | Clear and systematic labelling required | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Chint | MAW | DC Cables | DC Cables | Design factors to be provided | 1.15.2 | Connectors of Modules and string cables shall be connected of self-locking type, have IP65 rating and shall be from same manufacturer and type | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Chint | MAW | DC Cables | DC Cables | Design factors to be provided | 1.15.2 | Installation to be verified by measurement-protocols | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Cannot be evaluated at this stage. | blanc protocol | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Chint | MAW | DC Cables | DC Cables | Design factors to be provided | 1.15.2 | Lifetime of 30 years is assured | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | What proof is required. | Life time test of nonmetal materials IEC 60811-408:2012 / (DIN EN 60811-408; VDE 0473-811-408:2012-12) 30 y assurance never seen until today | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Chint | MAW | DC Cables | DC Cables | Design factors to be provided | 1.15.2 | Sizing of cables shall be specified according to the number of modules and strings per array | 1 | doc 1&2 page 454 | 1 | [5 empty] | voltage drop calculation |  |  | 1 |  | Pass
Chint | MAW | DC Cables | DC Cables | Design factors to be provided | 1.15.2 | The DC main (downstream of combiner box) wiring harness shall have the quality: Aluminum / Copper / 1000 V / Class II | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | It should be in accordance with the inverter values. | possibly 1500V for such system design | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Chint | MAW | DC Cables | DC Cables | Specific Requirements | 1.15.1 | Are Ohmic losses less than 1% at full power? | 1 |  |  |  | 1 |  | Pvsyst: DC losses at 0.9%, AC losses not considered? |  | DC+AC losses < 2% | U |  | 1 |  | Open
Chint | MAW | DC Cables | DC Cables | Standards | 1.15.3 | IEC 60364-1 | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Chint | MAW | DC Connectors | DC Connectors | Standards | 1.16.2 | EN 50521 | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? | PV Connectors no, just a statement of compliance | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Chint | MAW | DC Connectors | DC Connectors | Standards | 1.16.2 | IEC 60512 | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? | Connectors E-Systems no, just a statement of compliance | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Chint | MAW | DC Junction Box | DC Junction Box | Design factors to be provided | 1.17.1 | At least IP54 | 1 | Doc 1&2 page 19 | 1 |  |  |  |  | DC Junction box is applicable in what conditions? | depending on DC Design |  |  | 1 |  | Pass
Chint | MAW | DC Junction Box | DC Junction Box | Design factors to be provided | 1.17.1 | Class 2 DC surge arrestor | 1 | Doc 1&2 page 19 | 1 | [8 empty] | 1 |  | Pass
Chint | MAW | DC Junction Box | DC Junction Box | Design factors to be provided | 1.17.1 | DC fuses shall permit up to maximum 1000 V (or 1500V if designed). String box design, including all operating elements shall satisfy safety requirements | 1 | Doc 3&4 page 84 | 1 |  |  |  |  | Will inverter voltage(1500V) effect the maximum voltage(1000V)? | depends on spec of inverter. |  |  | 1 |  | Pass
Chint | MAW | DC Junction Box | DC Junction Box | Design factors to be provided | 1.17.1 | Dust and heat protection | 1 | Doc 1&2 page 19 | 1 | [8 empty] | 1 |  | Pass
Chint | MAW | DC Junction Box | DC Junction Box | Design factors to be provided | 1.17.1 | Monitored input-couples | 1 | Doc 1&2 page 19 | 1 | [8 empty] | 1 |  | Pass
Chint | MAW | DC Junction Box | DC Junction Box | Specifications | 1.17.2 | Current monitoring | 1 | Doc 3&4 page 84 | 1 | [8 empty] | 1 |  | Pass
Chint | MAW | DC Junction Box | DC Junction Box | Specifications | 1.17.2, 1.17.1 | Monitoring interface for SCADA | 1 | Doc 1&2 page 19 | 1 | [8 empty] | 1 |  | Pass
Chint | MAW | DC Junction Box | DC Junction Box | Specifications | 1.17.2 | Touch-safe protective cover | 1 | Doc 3&4 page 83 | 1 |  |  |  | transparent cover |  |  |  |  | 1 |  | Pass
Chint | MAW | DC Junction Box | DC Junction Box | Standards | 1.17.3 | EN 50178 | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? | High currat devices no, just a statement of compliance | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Chint | MAW | DC Junction Box | DC Junction Box | Standards | 1.17.3 | EN 60439-1 | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? | arcing fault / Störlichtbogen Verhalten no, just a statement of compliance | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Chint | MAW | DC Junction Box | DC Junction Box | Standards | 1.17.3 | EN 61000-6 | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? | EMV no, just a statement of compliance | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Chint | JBU | Step-up Transformers/MV Switchgear | Due Diligence | Quality Assurance | 1.21.3 | Factory witness testing will be required for MV transformer and switchgear to be installed at this project. The cost of the due diligence to be carried by the Employer through an independent technical consultant will be taken over by the successful bidder up to an amount of 30,000 USD. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Chint | MAW | Inverters | Due diligence | Quality Assurance | 1.18.12 | The Bidder accepts that the cost of the Quality assurance for Inverters to be carried by the Employer through an independent technical consultant shall be taken over by the successful bidder up to an amount of 100,000 USD. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Chint | MAW | Modules | Due Diligence | Quality Assurance | 1.14.6 | The bidder will bear the cost of the Quality assurance for PV modules on-site and in laboratory to be carried out by the Employer through an independent technical consultant up to 150,000 USD. | 1 |  |  |  | 1 |  |  |  |  | C |  | 1 |  | Open
Chint | GD | Technical Bid Evaluation Criteria | Due Diligence | Quality Assurance | 1.3.5 | The cost of the due diligence to be carried out by the Employer through an independent technical consultant before contract signature will be taken over by the successful bidder up to an amount of 50,000 USD independent of the result. The due diligence will cover a module factory visit, an inverter factory inspection and a due diligence on the provided financial, EPC and O&M credentials including up to three site visits. | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  | Only to be checked in list of deviations. |  |  |  | 1 |  | Open
Chint | GD | Scope of the Bid | General items | Guarantees | 1.1.5 | Energy Purchase Agreement (EPA) practices are followed | 1 |  |  |  | 1 | Important reasons: due to current uncertainty of the criteria we accept an open status. Please clarify that yo acknowledge the criteria and comply unless a reason of high importance will not allow you you to comply. In such a situation the parties will seek to agree a compromise. |  | This cannot be evaluated at this stage. | we need a sentence that it should and can only be disregarded for important reasons |  |  | 1 |  | Open
Chint | JBS | Labelling | General items | Labelling | 1.26 | the ID numbering / coding system shall allow unique identification of all components and be understandable | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  | Cannot be evaluated at this stage |  | C |  | 1 |  | Open
Chint | JBS | Labelling | General items | Labelling | 1.26 | Tags shall be weather and UV resistant. | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  | Cannot be evaluated at this stage |  | C |  | 1 |  | Open
Chint | JBS | Labelling | General items | Labelling | 1.26 | The ID’s shall correspond to all drawings, plant documentation and control system. | 1 |  |  |  | 1 |  |  | Cannot be evaluated at this stage |  | C |  | 1 |  | Open
Chint | GD | Scope of the Bid | General items | Quality Assurance | 1.1.3 | Defect components consequences: If one tested sample fails in one criterion, all items of the same category will be regarded as failed and rejected. | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  | Only to be checked in list of deviations. | yes, we need to be sure that they comply as for most of the critera |  |  | 1 | 1 | Open
Chint | GD | Scope of the Bid | General items | Specific Requirements | 1.1.2 | The Offer shall include a list of all vendors and/or sub-contractors for major equipment. | 1 |  | 1 | [8 empty] | 1 |  | Pass
Chint | GD | Scope of the Bid | General items | Specific Requirements | 1.1.9 | The bid covers the planning of the System design, the required functionality of the System in terms of its sub-systems and components, detailed feature-wise descriptions of the components to be used in the System, the planning of the System installation, its integration, testing, monitoring, commissioning and O&M of the System | 3 |  |  |  | 1 | We can not find all of the requested criteria in your documents. Please confirm that your bid is compliant with all expectations and requirements of Section 6 of the RFP and provide a list with ALL exeptions or alterations. This applies to both, the EOPC And the O&M part. |  | This question should be removed as detailed design of every component/sub-system will be checked and evaluated thoroughly in technical evaluation | no, its an overall critera an need to be met |  |  | 1 | 1 | Open
Chint | JBS | Basic Scope of Supply | General items | Specific Requirements | 1.6 | The maximum DC voltage shall not exceed 1500 V | 1 | Page 443-447 | 1 |  |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | [5 empty] | 1 |  | Pass
Chint | JBS | Basic Scope of Supply | General items | Specific Requirements | 1.6 | The required AC voltage / frequency at grid connection shall 132 kV/50 Hz | 1 | Page 443-447 | 1 | [8 empty] | 1 |  | Pass
Chint | JBS | Equipment guarantees | Inverter | Guarantees | 1.28.2 | The Successful Bidder shall provide an Inverter warranty of at least 5 years. A spare parts warranty shall be included for the 25 years operational period. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Chint | JBU | Inverter/Transformer Station | Inverter/Transformer Station | Specific Requirements | 1.22 | All stations shall be equipped with fire and smoke detectors and alarm, connected to security and surveillance system | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Chint | JBU | Inverter/Transformer Station | Inverter/Transformer Station | Specific Requirements | 1.22 | Bidder shall firmly specify the number of stations, manufacturer, capacity and type of equipment. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Chint | JBU | Inverter/Transformer Station | Inverter/Transformer Station | Specific Requirements | 1.22 | Every ten (10) or lesser number of stations shall be equipped with an earthing and short-circuiting equipment | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Chint | JBU | Inverter/Transformer Station | Inverter/Transformer Station | Specific Requirements | 1.22 | Fine sand filters shall be installed | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Chint | JBU | Inverter/Transformer Station | Inverter/Transformer Station | Specific Requirements | 1.22 | The station shall enable the grounding of hardware and neutral will be left ground isolated | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Chint | MAW | Inverters | Inverters | Design factors to be provided | 1.18.7 | Cooling method | 1 | Doc 3&4 page 53 | 1 |  |  |  | Variable speed cooling fans |  |  |  |  | 1 |  | Pass
Chint | MAW | Inverters | Inverters | Design factors to be provided | 1.18.7 | Detection of insulation faults | 1 | Doc 3&4 page 53 |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Chint | MAW | Inverters | Inverters | Design factors to be provided | 1.18.7 | Input voltage range (The voltage window for MPP tracking shall accommodate the expected degradation of the modules.) | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Chint | MAW | Inverters | Inverters | Design factors to be provided | 1.18.7 | Integrated transformer/transformerless / Outside Dry Type Transformer | 1 | Doc 3&4 page 53 | 1 |  |  |  | transformerless |  |  |  |  | 1 |  | Pass
Chint | MAW | Inverters | Inverters | Design factors to be provided | 1.18.7 | Maximum output current | 1 | Doc 3&4 page 53 | 1 | [8 empty] | 1 |  | Pass
Chint | MAW | Inverters | Inverters | Design factors to be provided | 1.18.7 | Nominal output frequency, 3-phase | 1 | Doc 3&4 page 53 | 1 | [8 empty] | 1 |  | Pass
Chint | MAW | Inverters | Inverters | Design factors to be provided | 1.18.7 | Nominal output voltage | 1 | Doc 3&4 page 53 | 1 | [8 empty] | 1 |  | Pass
Chint | MAW | Inverters | Inverters | Design factors to be provided | 1.18.7 | Nominal power | 1 | Doc 3&4 page 53 | 1 | [8 empty] | 1 |  | Pass
Chint | MAW | Inverters | Inverters | Design factors to be provided | 1.18.7 | Operating temperature range | 1 | Doc 3&4 page 53 | 1 |  |  |  |  | What is the acceptable range? | 60°C Derating? |  |  | 1 |  | Pass
Chint | MAW | Inverters | Inverters | Design factors to be provided | 1.18.7 | Output voltage range | 1 | Doc 3&4 page 53 | 1 | [8 empty] | 1 |  | Pass
Chint | MAW | Inverters | Inverters | Design factors to be provided | 1.18.7 | Peak efficiency/ Weighted efficiency | 1 | Doc 3&4 page 53 | 1 | [8 empty] | 1 |  | Pass
Chint | MAW | Inverters | Inverters | Design factors to be provided | 1.18.7 | Protection rating: NEMA 3R, IP54/IP55/IP60 | 1 |  | 1 |  |  |  | IP20 indoor, installed in a station |  |  |  |  | 1 |  | Pass
Chint | MAW | Inverters | Inverters | Design factors to be provided | 1.18.7 | PV array configuration options: positive ground, negative ground | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Chint | MAW | Inverters | Inverters | Functionalities | 1.18.3 | Active power control reduction: remotely set point of control in case of network congestions or risk of system collapse, if deemed necessary | 1 | Doc 3&4 page 53 | 1 |  |  |  | Active power continuously adjustable | 8.2 needs to ensure these questions are answered in the bids. |  |  |  | 1 |  | Pass
Chint | MAW | Inverters | Inverters | Functionalities | 1.18.3 | Anti-islanding protection | 1 | doc 3&4 page 6 | 1 | [8 empty] | 1 |  | Pass
Chint | MAW | Inverters | Inverters | Functionalities | 1.18.3 | Frequency regulation | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | 8.2 needs to ensure these questions are answered in the bids. |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Chint | MAW | Inverters | Inverters | Functionalities | 1.18.3 | Limitation of voltage fluctuation due to switching operations and long-term flicker | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | 8.2 needs to ensure these questions are answered in the bids. |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Chint | MAW | Inverters | Inverters | Functionalities | 1.18.3 | Limitation of current harmonics and higher frequency components up to 9 kHz | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Chint | MAW | Inverters | Inverters | Functionalities | 1.18.3 | Limitation of short-circuit current | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | 8.2 needs to ensure these questions are answered in the bids. |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Chint | MAW | Inverters | Inverters | Functionalities | 1.18.3 | Limitation of steady-stage voltage changes to 2% of the nominal value | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Chint | MAW | Inverters | Inverters | Functionalities | 1.18.3 | Matching grid voltage and frequency at point-of-coupling | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Chint | MAW | Inverters | Inverters | Functionalities | 1.18.3 | Maximum Power Point Tracking (MPPT) and string/sub-array management | 1 | Doc 3&4 page 53 | 1 | [8 empty] | 1 |  | Pass
Chint | MAW | Inverters | Inverters | Functionalities | 1.18.3 | Voltage and frequency fault ride-through: no disconnection of the connection through voltage dip and change of active power generation, feed-in of reactive power during the fault for voltage stabilisation | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | 8.2 needs to ensure these questions are answered in the bids. |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Chint | MAW | Inverters | Inverters | Functionalities | 1.18.3 | Voltage regulation through reactive power support: remotely set point control for voltage stability | 1 | Doc 3&4 page 53 | 1 |  |  |  | Reactive power adjustable and the power factor range from -0.8 to +0.8, Reactive power compensation at night | 8.2 needs to ensure these questions are answered in the bids. |  |  |  | 1 |  | Pass
Chint | MAW | Inverters | Inverters | Manufacturers confirmation | 1.18.9 | The Bidder shall deliver a manufacturer's confirmation in his Bid for the suitability of the inverter for the specific weather conditions applicable in Bahawalpur Pakistan. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Chint | MAW | Inverters | Inverters | Quality Assurance | 1.18.11 | After commissioning, 1 of 10 inverters will be measured on site (power curve and efficiency) by an approved independent technical consultant on behalf of the Employer. The on-site measurements shall be accepted by the Bidder as average values for all inverters | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Cannot be evaluated at this stage | compliance! | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Chint | MAW | Inverters | Inverters | Quality Assurance | 1.18.11 | Check of protection against overload, short-circuit, grid-failure, internal failure, over-temperature (de-rating), surge protection, detection of insulation faults of AC Cables. Bidder shall firmly specify the manufacturer, types and length of cables to be installed | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | 8.2 needs to ensure these questions are answered in the bids. |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Chint | MAW | Inverters | Inverters | Quality Assurance | 1.18.11 | Test run and check of MPP tracking of all inverters | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | 8.2 needs to ensure these questions are answered in the bids. |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Chint | MAW | Inverters | Inverters | Quality Assurance | 1.18.11 | Test run in the field for maximum and EU-efficiency of all Inverters | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | 8.2 needs to ensure these questions are answered in the bids. |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Chint | MAW | Inverters | Inverters | Quality Assurance | 1.18.11 | The Bidder shall deliver detailed protocols of performance test run (warm power test) for every single inverter | 1 |  |  |  | 1 |  |  | Cannot be evaluated at this stage |  | C |  | 1 |  | Open
Chint | MAW | Inverters | Inverters | Specific Requirements | 1.18.6 | Specifications of table in Schedule C shall be met | 1 |  | 1 |  |  |  |  | Link to table |  |  |  | 1 |  | Pass
Chint | MAW | Inverters | Inverters | Standards | 1.18.8 | IEEE 1547 | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? | no, just a statement of compliance Interconnecting Distributed Resources | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Chint | MAW | Inverters | Inverters | Standards | 1.18.8 | TUV, VDE, or equivalent certification of passing the relevant standards | 1 | Doc 3&4 page 4 | 1 | [8 empty] | 1 |  | Pass
Chint | MAW | Inverters | Inverters | Strategic Reason for Inverter Selection | 1.18.2 | Available uptime | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Chint | MAW | Inverters | Inverters | Strategic Reason for Inverter Selection | 1.18.2 | Balance of System (BOS) costs of inverter and labour | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  | financial bid | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Chint | MAW | Inverters | Inverters | Strategic Reason for Inverter Selection | 1.18.2 | Concept of protection against overload, short-circuit, grid-failure, internal failure, over-temperature (de-rating), surge protection | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Its too general, needs to be reviewed. | failure codes and consquences (automatic/manual restart, throw away safety devices) | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Chint | MAW | Inverters | Inverters | Strategic Reason for Inverter Selection | 1.18.2 | Dust and heat protection | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  | derating? | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Chint | MAW | Inverters | Inverters | Strategic Reason for Inverter Selection | 1.18.2 | Timely and effective monitoring at a granular/zoomed-in level | 1 |  | 1 | [8 empty] | 1 |  | Pass
Chint | GD | Scope of the Bid | Layout | Guarantees | 1.1.6 | The bidder confirms that the system complies with all applicable requirements of the NEPRA Grid Code of Pakistan and its Draft Amendment no. 2 for Solar Power Projects. | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  | Only to be checked in list of deviations. |  |  |  | 1 |  | Open
Chint | JBS | Physical layout | Layout | Specific Requirements | 1.7.2 | Provide a schematic electrical Single Line Diagram (SLD) of the entire System layout from the modules to the grid-connection, identifying and listing all of the following DC and AC components. | 1 | Page 449- 453 | 1 | [8 empty] | 1 |  | Pass
Chint | JBS | Physical layout | Layout | Specific Requirements | 1.7.2 | The system design shall be such as to ensure ease of maintenance and a multiple ring main unit (RMU) philosophy (on MV level) must be followed for circuit breaker configuration. | 1 | Page 450 | 1 |  |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | [5 empty] | 1 |  | Pass
Chint | MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Bills of Materials, BoMs: (glass, encapsulant, backsheet, ribbon, adhesives, cable, junction box, connector) | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Chint | MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Current at the maximum current point | 1 | Doc 3&4 page 109 | 1 | [8 empty] | 1 |  | Pass
Chint | MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Degradation Curve from Manufacturer | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Chint | MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Manufacturers confirmation for the suitability of module for specific weather conditions and the high UV-radiation | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  | especially reliability at high UV irridiance / Product warranty | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Chint | MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Manufacturers installation guidelines | 1 |  |  |  | 1 |  |  |  |  | C |  | 1 |  | Open
Chint | MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Materials and workmanship warranty of a minimum of 10 years | 1 | Doc 3&4 page 109 |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | Extended product warranty --> materials and workmanship? |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Chint | MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Maximum rated power | 1 | Doc 3&4 page 109 | 1 | [8 empty] | 1 |  | Pass
Chint | MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Maximum system voltage | 1 | Doc 3&4 page 109 | 1 | [5 empty] | … at SK-II safety class |  |  | 1 |  | Pass
Chint | MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Minimum efficiency at 200 W/m² (25°, AM 1.5) | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Chint | MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Open-circuit voltage | 1 | Doc 3&4 page 109 | 1 | [8 empty] | 1 |  | Pass
Chint | MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Operating temperature range and nominal operating cell temperature NOCT | 1 | Doc 3&4 page 109 | 1 |  |  |  |  | What range is acceptable | There is as small range anyway Will result in the PR losses |  |  | 1 |  | Pass
Chint | MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Power warranty/performance guarantee of a minimum of 25 years: the power output should not fall below 90% within 10 years, and below 80% within 25 years; linear warranty mandatory | 1 | Doc 3&4 page 109 | 1 | [8 empty] | 1 |  | Pass
Chint | MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Provide guarantees and data sheets (to be transferred to Employer upon COD) | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Chint | MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Rated power tolerance | 1 | Doc 3&4 page 109 | 1 | [8 empty] | 1 |  | Pass
Chint | MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Short-circuit current | 1 | Doc 3&4 page 109 | 1 | [8 empty] | 1 |  | Pass
Chint | MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Specify number of modules and total MWp to be provided | 1 | Doc 3&4 page 447 |  |  | 1 |  | Pvsyst: 100MWp + 800kWp (403200 modules) |  |  | U |  | 1 |  | Open
Chint | MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Tolerance to wind (maximum load) impact (mechanical load) | 1 | Doc 3&4 page 109 | 1 | [5 empty] | minimum 2400 Pa |  |  | 1 |  | Pass
Chint | MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Type of cells comprising the module, and number of cells in series | 1 | Doc 3&4 page 109 | 1 | [5 empty] | manufacturer |  |  | 1 |  | Pass
Chint | MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Voltage at the maximum power point | 1 | Doc 3&4 page 109 | 1 | [8 empty] | 1 |  | Pass
Chint | JBS | Equipment guarantees | Modules | Guarantees | 1.28.1 | The Successful bidder shall provide a Module warranty of at least 10 years. The performance warranty of the module shall be linear with a fixed factor over 25 years. | 1 | Page 21 | 1 |  |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  | To be discussed |  |  |  | 1 |  | Pass
Chint | MAW | Modules | Modules | Pre-shipment quality assurance | 1.14.4 | All modules must undergo Electroluminiscense (EL) inspection with a resolution of minimum 4 MPixel prior to shipment. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Cannot be evaluated at this stage. | compliance necessary | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Chint | MAW | Modules | Modules | Pre-shipment quality assurance | 1.14.7 | Warranties and evidence shall be given by the bidder that their selected modules have been tested for susceptibility to Potential Induced Degradation (PID). | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Chint | MAW | Modules | Modules | Pre-shipment quality assurance | 1.14.4 | A sufficient EVA cross linking has to be verified per production line through a gel content test supervised by an accredited (IEC 17025 or national pendant) independent certified module testing agency. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Cannot be evaluated at this stage. | compliance necessary | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Chint | MAW | Modules | Modules | Pre-shipment quality assurance | 1.14.4 | Pre-shipment flash tested data Quality assurance for PV modules on-site and in laboratory simulator must meet the class AAA requirements of IEC 60904-9. The sun simulator must be calibrated with a reference cell, which itself was calibrated by a member of the WPVS scheme, with a maximum uncertainty of Isc of 1%. unique barcode (SNr) and labelled performance headlines (P(mpp), I(sc), U(oc), I(mpp), U(mpp) maximum current, maximum voltage Positive power sorting | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Cannot be evaluated at this stage. | compliance necessary | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Chint | MAW | Modules | Modules | Quality assurance on site | 1.14.5 | The modules shall undergo an incoming inspection at arrival on construction site. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Cannot be evaluated at this stage. | stated and accepted | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Chint | MAW | Modules | Modules | Standards (as applicable to crystalline silicion or thin-film) | 1.14.3 | IEC 60364-4-41 | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? | no, just a statement of compliance 'protection against electric shock | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Chint | MAW | Modules | Modules | Standards (as applicable to crystalline silicion or thin-film) | 1.14.3 | IEC 60904-1, IEC 60904-3 | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? | no, just a statement of compliance | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Chint | MAW | Modules | Modules | Standards (as applicable to crystalline silicion or thin-film) | 1.14.3 | IEC 61215 | 1 | doc 1&2 page 198, 209 | 1 |  |  |  |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? | no, just a statement of compliance |  |  | 1 |  | Pass
Chint | MAW | Modules | Modules | Standards (as applicable to crystalline silicion or thin-film) | 1.14.3 | IEC 61416 | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? | not existing | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Chint | MAW | Modules | Modules | Standards (as applicable to crystalline silicion or thin-film) | 1.14.3 | IEC 61646 | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? | no, just a statement of compliance | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Chint | MAW | Modules | Modules | Standards (as applicable to crystalline silicion or thin-film) | 1.14.3 | IEC 61701 | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? | no, just a statement of compliance | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Chint | MAW | Modules | Modules | Standards (as applicable to crystalline silicion or thin-film) | 1.14.3 | IEC 61730 | 1 |  | 1 |  |  |  |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? | no, just a statement of compliance |  |  | 1 |  | Pass
Chint | MAW | Inverters | Monitoring | Functionalities | 1.18.3 | Advanced communication, with intelligent alerts/warnings, to the SCADA server | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Chint | JBS | Equipment guarantees | Mounting | Guarantees | 1.28.3 | The Successful Bidder shall provide a product warranty for the structure of at least 10 years. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Chint | JBU | Mounting | Mounting | Specific Requirements | 1.13.8 | The mounting structures must be earthed | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Chint | JBU | Mounting | Mounting | Specific Requirements | 1.13.1 | The system is fixed-tilted. Tilt angle is specified. | 1 |  | 1 | [8 empty] | 1 |  | Pass
Chint | JBU | Mounting | Mounting | Specific Requirements | 1.13.5 | All fastening structures must be verified for durability and resistance to environmental degradation for 25 years | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | What sort of mechanism is required for verification? | Sub structure description / materials double to line 172 - 175 | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Chint | JBU | Mounting | Mounting | Specific Requirements | 1.13.3 | Mounting structure is made of durable material, resistant to sandstorms and compatible with the module frame material so as to avoid any adverse electrolytic/galvanic effects. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Information about materials to be known before evaluation. | right | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Chint | JBU | Mounting | Mounting | Specific Requirements | 1.13.3 | Mounting system resists corrosion (passing the salt spray test IEC 61701, among other verification), | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Information about materials to be known before evaluation. | right | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Chint | JBU | Mounting | Mounting | Specific Requirements | 1.13.3 | Mounting system resists high wind speeds (up to 40 m/s) | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Chint | JBU | Mounting | Mounting | Specific Requirements | 1.13.3 | Mounting system resists UV induced degradation | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Chint | JBU | Mounting | Mounting | Specific Requirements | 1.13.9 | Specific site conditions have been considered. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Needs to be discussed. | … specific requirements of the soil conditions Static | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Chint | JBU | Step-up Transformers/MV Switchgear | MV Switchgear | Design factors to be provided | 1.21.4 | Rated lightning impulse voltage | 1 |  | 1 | [8 empty] | 1 |  | Pass
Chint | JBU | Step-up Transformers/MV Switchgear | MV Switchgear | Design factors to be provided | 1.21.4 | Rated power frequency withstand voltage | 1 |  | 1 | [8 empty] | 1 |  | Pass
Chint | JBU | Step-up Transformers/MV Switchgear | MV Switchgear | Design factors to be provided | 1.21.4 | Rated short circuit current | 1 |  | 1 | [8 empty] | 1 |  | Pass
Chint | JBU | Step-up Transformers/MV Switchgear | MV Switchgear | Design factors to be provided | 1.21.4 | System maximum voltage | 1 |  | 1 | [8 empty] | 1 |  | Pass
Chint | JBU | Step-up Transformers/MV Switchgear | MV Switchgear | Design factors to be provided | 1.21.4 | System nominal voltage | 1 |  | 1 | [8 empty] | 1 |  | Pass
Chint | JBU | Step-up Transformers/MV Switchgear | MV Switchgear | Specific Requirements | 1.21.4 | Interlocks will also be mechanically interlocked between line MV switchgears. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Chint | JBU | Step-up Transformers/MV Switchgear | MV Switchgear | Specific Requirements | 1.21.4 | MV Switchgears shall be SF6 gas insulated or VCB (Vacuum circuit breaker). | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Chint | JBU | Step-up Transformers/MV Switchgear | MV Switchgear | Specific Requirements | 1.21.4 | The separating equipment shall be installed with visible disconnection (pivotable disconnectors). | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Cannot be evaluated at this stage |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Chint | JBU | Step-up Transformers/MV Switchgear | MV Switchgear | Standards | 1.21.5 | IEC 60529 | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Chint | JBU | Step-up Transformers/MV Switchgear | MV Switchgear | Standards | 1.21.5 | IEC 62271-200 | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Chint | JBU | Step-up Transformers/MV Switchgear | MV Switchgear | Standards | 1.21.5 | IEC 62446 | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Chint | MAW | Inverters | O&M | Guarantees | 1.18.2 | For central inverters concept: the bidder shall ensure with an undertaking from the manufacturer that the concerned skilled staff will be made available at the site within 24 hours of reporting the defect to the manufacturer. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Chint | JBS | Physical layout | Physical layout plan | Specific Requirements | 1.7.7 | Detailed top view of the PV mounting structure, including module sizes and spacing between the module rows | 1 | Page 455 Page 456 |  |  | 1 | Inconsistency: Second drawing module dimensions inconsistent with datasheet.We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | [5 empty] | 1 | 1 | Open
Chint | JBS | Physical layout | Physical layout plan | Specific Requirements | 1.7.7 | Detailed view of the distribution of inverters and connections to the PV string/array | 1 | Page 449 | 1 |  |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | [5 empty] | 1 |  | Pass
Chint | JBS | Physical layout | Physical layout plan | Specific Requirements | 1.7.7 | Detailed side and front view of the PV mounting structure | 1 | Page 455 | 1 |  |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | [5 empty] | 1 |  | Pass
Chint | JBS | Physical layout | Physical layout plan | Specific Requirements | 1.7.7 | Detailed top view of electrical cabling interconnections | 1 | Page 455 | 1 |  |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | [5 empty] | 1 |  | Pass
Chint | JBS | Physical layout | Physical layout plan | Specific Requirements | 1.7.7 | Floor plans and elevations for all buildings, housing units, containers on site: e.g. , substations, the SCADA operational room, inverters, O&M, storage facilities | 1 | Page 453 | 1 | [8 empty] | 1 |  | Pass
Chint | JBS | Physical layout | Physical layout plan | Specific Requirements | 1.7.7 | Location of the system metering and grid connection point | 1 | Page 452 | 1 |  |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | [5 empty] | 1 |  | Pass
Chint | JBS | Power plant documentation | Power plant documentation | Quality Assurance | 1.27.1 | Flash report list of all modules shall be provided in digital form. | 1 |  |  |  | 1 |  |  |  |  | C |  | 1 |  | Open
Chint | JBS | Power plant documentation | Power plant documentation | Quality Assurance | 1.27.1 | The Bidder shall confirm that the complete as-built documentation of the plant will be provided in compliance with IEC 62446. Additionally all module serial numbers shall be listed with their individual location. | 1 |  |  |  | 1 |  |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  | C |  | 1 |  | Open
Chint | JBS | Workflow, Project Management Plan and Timelines | Project schedule / Project management | Project schedule | 1.8.1 | Interdependencies between the tasks | 1 |  | 1 | [8 empty] | 1 |  | Pass
Chint | JBS | Workflow, Project Management Plan and Timelines | Project schedule / Project management | Project schedule | 1.8.1 | Interdependencies of tasks with equipment order and delivery times | 1 |  | 1 | [8 empty] | 1 |  | Pass
Chint | JBS | Workflow, Project Management Plan and Timelines | Project schedule / Project management | Project schedule | 1.8.1 | Key milestones to indicate that the progress in on schedule | 1 |  |  |  | 1 | [6 empty] | 1 |  | Open
Chint | JBS | Workflow, Project Management Plan and Timelines | Project schedule / Project management | Project schedule | 1.8.1 | Provide installation schedule in compliance with sub-clause 8.2 of Particular Conditions (Time for Completion is 225 days after Commencement Date). | 1 | Page 106 | 1 |  |  |  |  | Find sub-clause 8.2 of Particular Conditions |  |  |  | 1 |  | Pass
Chint | JBS | Workflow, Project Management Plan and Timelines | Project schedule / Project management | Project schedule | 1.8.1 | Provide work breakdown structures, activity decomposition and sequencing and dependability with the baseline schedule clearly showing the critical path | 1 |  | 1 | [8 empty] | 1 |  | Pass
Chint | JBS | Workflow, Project Management Plan and Timelines | Project schedule / Project management | Project schedule | 1.8.1 | Schedule of tasks | 1 |  | 1 | [8 empty] | 1 |  | Pass
Chint | JBS | Workflow, Project Management Plan and Timelines | Project schedule / Project management | Project schedule | 1.8.1 | Teams, the number and skills of personnel to be deployed for each task | 1 |  | 1 | [8 empty] | 1 |  | Pass
Chint | JBS | Workflow, Project Management Plan and Timelines | Project schedule / Project management | Quality Assurance | 1.8.3 | Inspection of equipment delivery | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  |  |  | C |  | 1 |  | Open
Chint | JBS | Workflow, Project Management Plan and Timelines | Project schedule / Project management | Quality Assurance | 1.8.3 | Milestones for the completion of civil, mechanical, and electrical works | 1 |  |  |  | 1 |  |  |  | dobble to 105 and 111 | C |  | 1 |  | Open
Chint | JBS | Workflow, Project Management Plan and Timelines | Project schedule / Project management | Quality Assurance | 1.8.3 | Quality control of delivered modules | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  |  |  | C |  | 1 |  | Open
Chint | JBS | Workflow, Project Management Plan and Timelines | Project schedule / Project management | Quality Assurance | 1.8.3 | Risk analysis and mitigation plan | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  |  |  | C |  | 1 |  | Open
Chint | JBS | Workflow, Project Management Plan and Timelines | Project schedule / Project management | Quality Assurance | 1.8.3 | System acceptance QA procedure by the Employer | 1 |  |  |  | 1 | Unclear: We do not understand your proposal, please detail your proposal. Especially confirm that you are compliant with our requested criteria. |  |  |  | C |  | 1 |  | Open
Chint | JBS | Miscellaneous | Project schedule / Project management | Specific Requirements | 1.29.9 | The Bidder shall submit an organizational chart illustrating management and functional relationships among all project team members including consultants, sub-contractors and vendors at each significant stage of the work, such as permitting, design, construction, testing and commissioning and O&M. | 1 | Page 38/39 | 1 |  |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | [5 empty] | 1 |  | Pass
Chint | JBU | Supervisory Control and Data Acquisition (SCADA) | SCADA | Specific Requirements | 1.9.2 | Alarms/alerts and timely notification of key performance indicators | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Chint | JBU | Supervisory Control and Data Acquisition (SCADA) | SCADA | Specific Requirements | 1.9.2 | All communication/data cables outside of buildings must be fiber-optic cables | 1 |  |  |  | 1 | Unclear: We do not understand your proposal, please detail your proposal. Especially confirm that you are compliant with our requested criteria. |  |  |  | U |  | 1 |  | Open
Chint | JBU | Supervisory Control and Data Acquisition (SCADA) | SCADA | Specific Requirements | 1.9.2 | Back-up power for a minimum of twelve hours | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  |  |  | C |  | 1 |  | Open
Chint | JBU | Supervisory Control and Data Acquisition (SCADA) | SCADA | Specific Requirements | 1.9.2 | Control room to remotely monitor and manage the whole system, on a 24 x 7 basis, with the capability of Web-based information sharing | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  |  |  | C |  | 1 |  | Open
Chint | JBU | Supervisory Control and Data Acquisition (SCADA) | SCADA | Specific Requirements | 1.9.2 | Data must be readily available for the fulfilment of all warranties and performance guarantees | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Cannot be evaluated at this stage. | statement | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Chint | JBU | Supervisory Control and Data Acquisition (SCADA) | SCADA | Specific Requirements | 1.9.2 | Data logging at intervals of not less than one minute, processing, transmission, and back-up | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  |  | not more (!) | C |  | 1 |  | Open
Chint | JBU | Supervisory Control and Data Acquisition (SCADA) | SCADA | Specific Requirements | 1.9.2 | Data shall be provided via FTP (Push/Pull) to the Employer | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Chint | JBU | Supervisory Control and Data Acquisition (SCADA) | SCADA | Specific Requirements | 1.9.1 | Remote access to all operational data for independent monitoring purposes shall be possible (NTDC requirements) | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Chint | JBU | Supervisory Control and Data Acquisition (SCADA) | SCADA | Specific Requirements | 1.9.1 | Safe and redundant archive for operational data. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | General understanding: expressions like "shall", "has to be", "must be" have the meaning of "will be delivered"? Please confirm. |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Chint | JBU | Supervisory Control and Data Acquisition (SCADA) | SCADA | Specific Requirements | 1.9.2 | Separate inverter, zone, and string level (current and voltage) monitoring | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Chint | JBU | Supervisory Control and Data Acquisition (SCADA) | SCADA | Specific Requirements | 1.9.1 | The system has to provide different access-levels with different access rights allocated. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Chint | JBU | Earthworks | Site Preparation and site access | Design factors to be provided | 1.12 | All earth works required have to be specified and included in the offer | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  |  |  | C |  | 1 |  | Open
Chint | JBU | Earthworks | Site Preparation and site access | Specific Requirements | 1.12, 1.13.4, 1.7.7 | Cross-sections of foundations for stations shall be provided, including explanation of the foundations laying down, height, penetration, and method of installing foundation posts, mounting fixtures | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | no layouts of station foundations |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Chint | JBU | Earthworks | Site Preparation and site access | Specific Requirements | 1.12 | Position and specification of underground cable connections must be documented during installation | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  | Cannot be avaluated at this stage. |  | C |  | 1 |  | Open
Chint | JBU | Site Preparation and site access | Site Preparation and site access | Specific Requirements | 1.11.1 | The Bidder shall provide foundations and structures in accordance with the actual soil conditions. | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  |  | refer to Soil study | C |  | 1 |  | Open
Chint | JBU | Earthworks | Site Preparation and site access | Specific Requirements | 1.12 | After completion of construction and all earthworks ground shall be levelled and stabilized. | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  |  | (maintanance, dust) | C |  | 1 |  | Open
Chint | JBU | Earthworks | Site Preparation and site access | Specific Requirements | 1.12 | Within the plant boundary limits, access roads to all stations shall be suitable for heavy load trucks (axle load: min. 12 tonn). | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  |  |  | C |  | 1 |  | Open
Chint | JBS | Power plant documentation | Spare parts | Warranty | 1.27.2 | The successful bidder shall provide all warranty spares for a warranty period of 5 years. | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  |  |  | C |  | 1 |  | Open
Chint | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Design factors to be provided | 1.21.2 | 3-phase, double wound, continuously rated, oil-cooled, enclosed transformers, use of low loss core steel and close coupled copper windings | 1 |  | 1 | [8 empty] | 1 |  | Pass
Chint | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Design factors to be provided | 1.21.2 | Cooling method | 1 |  | 1 | [8 empty] | 1 |  | Pass
Chint | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Design factors to be provided | 1.21.2 | Efficiency | 1 |  | 1 | [8 empty] | 1 |  | Pass
Chint | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Design factors to be provided | 1.21.2 | Humidity tolerance | 1 |  | 1 | [8 empty] | 1 |  | Pass
Chint | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Design factors to be provided | 1.21.2 | Incoming terminals | 1 |  | 1 | [8 empty] | 1 |  | Pass
Chint | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Design factors to be provided | 1.21.2 | Insulation type | 1 |  | 1 | [8 empty] | 1 |  | Pass
Chint | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Design factors to be provided | 1.21.2 | kVA rating | 1 |  | 1 | [8 empty] | 1 |  | Pass
Chint | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Design factors to be provided | 1.21.2 | Maximum ambient temperature and altitude | 1 |  | 1 | [8 empty] | 1 |  | Pass
Chint | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Design factors to be provided | 1.21.2 | No-load losses | 1 |  | 1 | [8 empty] | 1 |  | Pass
Chint | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Design factors to be provided | 1.21.2 | Operating temperature range | 1 |  | 1 | [8 empty] | 1 |  | Pass
Chint | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Design factors to be provided | 1.21.2 | Operational data shall be logged in central operating system (e.g. oil temperature, oil level, pressure, Temperature probes (one per phase): Alarm and trip of cell etc.) | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  |  |  | C |  | 1 |  | Open
Chint | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Design factors to be provided | 1.21.2 | Outgoing terminals | 1 |  | 1 | [8 empty] | 1 |  | Pass
Chint | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Design factors to be provided | 1.21.2 | Primary side voltage | 1 |  | 1 | [8 empty] | 1 |  | Pass
Chint | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Design factors to be provided | 1.21.2 | Protection system | 1 |  | 1 | [8 empty] | 1 |  | Pass
Chint | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Design factors to be provided | 1.21.2 | Secondary side voltage | 1 |  | 1 | [8 empty] | 1 |  | Pass
Chint | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Design factors to be provided | 1.21.2 | Short-circuit impedance | 1 |  | 1 | [8 empty] | 1 |  | Pass
Chint | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Standards | 1.21.3 | IEC 60076 | 1 |  | 1 |  |  |  |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  |  |  | 1 |  | Pass
Chint | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Standards | 1.21.3 | IEC 60085 | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Chint | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Standards | 1.21.3 | IEC 60137 | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Chint | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Standards | 1.21.3 | IEC 60214 | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Chint | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Standards | 1.21.3 | IEC 62446 | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  | C |  | 1 |  | Open
Chint | JBU | Step-up Transformers/MV Switchgear | Step-up Transformers/MV Switchgear | Guarantees | 1.21.1 | Compatibility with NTDC grid connection code must be ensured | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Chint | GD | PR and System Performance Guarantee | System PR | Guarantees | 1.4.1 | A 25 years commitment, in the form of a whole System performance guarantee, is required. The performance guarantee is based on measuring the PR with the actual kWh-AC delivery per year adjusted for the actual POA irradiation for the same period | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  | Only to be checked in list of deviations. |  |  |  | 1 | 1 | Open
Chint | JBS | System PR Specification | System PR | Losses included in PR calculation | 1.5.4 | Auxiliary loads | 1 | Page 443-447 |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | Nicht berücksichtigt | We don’t understand the question. Kindly clarify. | see relevant chapter 1.5.4 List of "losses" = auxilary loads from PV Energy that make the PR | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Chint | JBS | System PR Specification | System PR | Losses included in PR calculation | 1.5.4 | Inverter (operating efficiency, operating voltage variations, power/voltage levels) | 1 |  | 1 |  |  |  | Temperaturverlsute 16,9 | We don’t understand the question. Kindly clarify. | see relevant chapter 1.5.4 List of technical losses that make the PR |  |  | 1 |  | Pass
Chint | JBS | System PR Specification | System PR | Losses included in PR calculation | 1.5.4 | Module Array (temperature dependence, soiling, low light inefficiency, shading, mismatches in array) | 1 |  | 1 |  |  |  |  | We don’t understand the question. Kindly clarify. | we want to see these losses specified. Thos need to be aligned with O+M Startegy and System composition |  |  | 1 |  | Pass
Chint | JBS | System PR Specification | System PR | Losses included in PR calculation | 1.5.4 | Ohmic losses in cables | 1 | Page 443-447 | 1 |  |  |  |  | We don’t understand the question. Kindly clarify. | see relevant chapter 1.5.4 List of technical losses that make the PR |  |  | 1 |  | Pass
Chint | JBS | System PR Specification | System PR | Losses included in PR calculation | 1.5.4 | Transformer losses | 1 | Page 443-447 |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | Trafoverluste nicht berücksichtigt | We don’t understand the question. Kindly clarify. | see relevant chapter 1.5.4 List of technical losses that make the PR | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Chint | JBS | System PR Specification | System PR | O&M | 1.5.2 | The target PR specification at the time of commissioning the System is equal to or greater than 0.75 (75%). | 1 |  | 1 |  |  |  | mit 75% gerade an der Grenze |  |  |  |  | 1 |  | Pass
Chint | JBS | Physical layout | System PR | Specific Requirements | 1.7.1 | Provide a report using Solar GIS data provided by the Employer | 1 | Page 443-447 | 1 |  |  |  |  | Replace 'Report' with ' PV-Syst report'. | 'Report' is original wording in ER in 1.7.1 |  |  | 1 |  | Pass
Chint | JBS | Physical layout | System PR | Specific Requirements | 1.7.1, 1.1.8 | Layout calculations of predicted kWh over the system lifetime and PR using the tool PVSyst V5.62 or higher | 1 | Page 443-447 | 1 | [8 empty] | 1 |  | Pass
Chint | GD | PR and System Performance Guarantee | System PR | System PR | 1.4.2 | Guaranteed PR values in the form of the Table in 1.4.1 for the acceptance phase and annual output of the PV system shall be specified. | 1 |  | 1 |  |  |  |  | Link to table in Documents sheet |  |  |  | 1 | 1 | Pass
Chint | GD | PR and System Performance Guarantee | System PR | System PR | 1.4.1 | The billing system/metering system will be installed at interconnection point of 132 kV bus bar of HV substation to be installed by the EPC Contractor and the 132 kV Transmission line of NTDC existing at site. | 2 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  | Only to be checked in list of deviations. |  |  |  | 1 |  | Open
Chint | GD | PR and System Performance Guarantee | System PR | System PR | 1.4.4 | The initial PR will be first measured after the time of commissioning of the completed PV System during the acceptance phase of 30 days. | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  | Cannot be evaluated at this stage. Only to be checked in list of deviations. |  |  |  | 1 | 1 | Open
Chint | JBS | Equipment guarantees | Warranty | Guarantees | 1.28.4, 1.6 | A detailed list of all guarantee conditions for the main equipments (beside modules and inverters) shall be provided by the Successful Bidder with the technical offer. The product warranty shall be at least 5 years. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Chint | JBS | Equipment guarantees | Warranty | Guarantees | 1.28 | The overall Guarantee and Power Plant Acceptance Procedures required for the Project are described in Sections 1.3, 1.4, 1.14, 1.18 and Schedule D and shall be met. | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  | Link |  | C |  | 1 |  | Open
Chint | JBS | Basic Scope of Supply | Warranty | Quality Assurance | 1.6 | The Product Warranties shall be given for a duration of at least 5 years | 1 |  |  |  | 1 |  |  | Cannot be evaluated at this stage. Only to be checked in list of deviations. |  | C |  | 1 |  | Open
Chint | MAW | Inverters | Warranty | Warranty option | 1.18.1 | The Bidder shall arrange a full-service package for the selected inverters for a product warranty period of 5 years, with an option to cover additional 20 years including provisions for any necessary replacements including O&M service plan guaranteeing 99% availability. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 5 years standard warranty; optional up to 20 years |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Juwi | JBU | AC Cabling | AC Cabling | Design factors to be provided | 1.19.1 | AC cable shall be of Copper. Rated voltage, nominal voltage between phase and neutral and nominal voltage between phases to be specified by the Bidder | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Juwi | JBU | AC Cabling | AC Cabling | Design factors to be provided | 1.19.1 | Appropriate sizing to minimise voltage drop and losses | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | What is the appropriate size? | leeway to allow MPP tracking when module voltage drops. At least 10%. Ralf, ist Vital kriterium. | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Juwi | JBU | AC Cabling | AC Cabling | Design factors to be provided | 1.19.1 | Bending radius | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Juwi | JBU | AC Cabling | AC Cabling | Design factors to be provided | 1.19.1 | Cable installation shall ensure grounding and short-circuit protection | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Juwi | JBU | AC Cabling | AC Cabling | Design factors to be provided | 1.19.1 | Cables shall be suitable for the environmental conditions at the project site, including UV protection (The Bidder shall provide certification from manufacturer) | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Juwi | JBU | AC Cabling | AC Cabling | Design factors to be provided | 1.19.1 | Installation to be verified by measurement-protocols | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Juwi | JBU | AC Cabling | AC Cabling | Design factors to be provided | 1.19.1 | Lifetime longer than 25 years | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Juwi | JBU | AC Cabling | AC Cabling | Design factors to be provided | 1.19.1 | Rated voltage | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Juwi | JBU | AC Cabling | AC Cabling | Design factors to be provided | 1.19.1 | Sufficient and effective cable protection against attacks of rodents for any cabling underground or above is required | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Juwi | JBU | AC Cabling | AC Cabling | Specific Requirements | 1.19.3 | The runs of both the main DC and AC cables, in the System layout, should be adjusted to keep power losses below <1% at STC (Design calculations through cable loss simulation to be provided for review & comment). | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Part of system design | Kategorie ? | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Juwi | JBU | AC Cabling | AC Cabling | Standards | 1.19.2 | DIN-VDE-0276 | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Juwi | JBU | AC Cabling | AC Cabling | Standards | 1.19.2 | EN 60332-1-1 and EN 60332-2-1 | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Juwi | JBU | AC Cabling | AC Cabling | Standards | 1.19.2 | IEC 60364 | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Juwi | JBU | AC Cabling | AC Cabling | Standards | 1.19.2 | IEC 60502 | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Juwi | JBU | AC Combiner Box | AC Combiner Box | Design factors to be provided | 1.20.1 | Class 2 AC surge arrestor | 1 |  | 1 |  |  |  | not applicable |  |  |  |  | 1 |  | Pass
Juwi | JBU | AC Combiner Box | AC Combiner Box | Design factors to be provided | 1.20.1 | Flame test | 1 |  | 1 |  |  |  | not applicable |  |  |  |  | 1 |  | Pass
Juwi | JBU | AC Combiner Box | AC Combiner Box | Design factors to be provided | 1.20.1 | Load breaker switch of adequate size | 1 |  | 1 |  |  |  | not applicable |  |  |  |  | 1 |  | Pass
Juwi | JBU | AC Combiner Box | AC Combiner Box | Design factors to be provided | 1.20.1 | Operating temperature range | 1 |  | 1 |  |  |  | not applicable |  |  |  |  | 1 |  | Pass
Juwi | JBU | AC Combiner Box | AC Combiner Box | Design factors to be provided | 1.20.1 | Rated current | 1 |  | 1 |  |  |  | not applicable |  |  |  |  | 1 |  | Pass
Juwi | JBU | AC Combiner Box | AC Combiner Box | Design factors to be provided | 1.20.1 | Rated voltage | 1 |  | 1 |  |  |  | not applicable |  |  |  |  | 1 |  | Pass
Juwi | JBU | AC Combiner Box | AC Combiner Box | Design factors to be provided | 1.20.1 | Stripping length of the individual wire | 1 |  | 1 |  |  |  | not applicable |  |  |  |  | 1 |  | Pass
Juwi | JBU | AC Combiner Box | AC Combiner Box | Design factors to be provided | 1.20.1 | Waterproof test | 1 |  | 1 |  |  |  | not applicable |  |  |  |  | 1 |  | Pass
Juwi | JBU | AC Combiner Box | AC Combiner Box | Standards | 1.20.2 | EN 60529, DIN-VDE-0472 | 1 |  | 1 |  |  |  | not applicable | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  |  |  | 1 |  | Pass
Juwi | JBU | AC Combiner Box | AC Combiner Box | Standards | 1.20.2 | IP 67 | 1 |  | 1 |  |  |  | not applicable |  |  |  |  | 1 |  | Pass
Juwi | JBS | Physical layout | Auxiliary equipment | Specific Requirements | 1.7.8 | All parts of the installation are covered by two high speed protection schemes, which shall be independent to avoid common mode failures | 1 | Page 309 | 1 | [8 empty] | 1 |  | Pass
Juwi | JBS | Physical layout | Auxiliary equipment | Specific Requirements | 1.7.8 | The outline of protection schemes shall be shown on the single line diagram (SLD) | 1 | Page 309 | 1 | [8 empty] | 1 |  | Pass
Juwi | JBS | Physical layout | Auxiliary equipment | Specific Requirements | 1.7.8 | Provide complete indicating, regulating, controlling, protecting and interlocking equipment necessary for safe and efficient operation of the plant and substation, including complete protection scheme. | 1 | Page 307 - 310 | 1 | [8 empty] | 1 |  | Pass
Juwi | JBS | Physical layout | Auxiliary equipment | Specific Requirements | 1.7.9 | The scope of the documentation shall cover at least the requirements of IEC 62446. | 1 |  |  |  | 1 | Unclear: We do not understand your proposal, please detail your proposal. Especially confirm that you are compliant with our requested criteria. |  |  |  | C |  | 1 |  | Open
Juwi | JBS | Physical layout | Auxiliary equipment | Specific Requirements | 1.7.8 | The Bidder shall include a fire prevention and response plan | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Juwi | JBS | Physical layout | Auxiliary equipment | Specific Requirements | 1.7.9 | The documentation includes clearly labelled objects and figures annotated in English language. | 1 |  |  |  | 1 |  |  |  |  | C |  | 1 |  | Open
Juwi | JBS | Physical layout | Auxiliary equipment | Specific Requirements | 1.7.8 | The fire prevention and response plan shall include a fire alarm und detection system with a main panel in the control room | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Juwi | RM | Other infrastructure | Auxiliary systems | DC Backup System / uninterrupted power supply (UPS) | 1.25.6 | IEC-60051 and IEC-60439 standards apply | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  |  |  | 1 |  | Open
Juwi | RM | Other infrastructure | Auxiliary systems | Design factors to be provided | 1.25.1 | One administration and office building with car port for 10 vehicles shall be provided, with sufficient space for operating personal, control room, security office, regular office rooms for permanent and visiting staff, meeting room, kitchen sanitary systems (toilet, showers separate for male and female), first aid, control room, electrical rooms, etc. The building shall have windows for office rooms and air conditioning system (split units) for all office rooms. | 1 |  | 1 |  |  |  |  | Priority to be discussed |  |  |  | 1 |  | Pass
Juwi | RM | Other infrastructure | Auxiliary systems | Design factors to be provided | 1.25.1 | Service water system sufficiently sized for cleaning cycle of modules | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | [5 empty] | 1 |  | Open
Juwi | RM | Other infrastructure | Auxiliary systems | Design factors to be provided | 1.25.1 | Sewage system including sewage disposal for Construction and O&M phase | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | [5 empty] | 1 |  | Open
Juwi | RM | Other infrastructure | Auxiliary systems | Design factors to be provided | 1.25.1 | Warehouse for spare parts and workshop for minor mechanical/electrical works. | 1 |  | 1 | [8 empty] | 1 |  | Pass
Juwi | RM | Other infrastructure | Auxiliary systems | Design factors to be provided | 1.25.1 | Water storage facility for drinking water, sanitary water (sufficient for 1 week) | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | [5 empty] | 1 |  | Open
Juwi | RM | Other infrastructure | Auxiliary systems | Guarantees | 1.25.4 | All buildings should be designed in accordance with the requirements of the Pakistan Building Code (available at www.pec.org.pk/buildingcode.aspx) and latest Seismic Provisions 2007. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Link to code |  |  |  | 1 |  | Open
Juwi | JBS | Miscellaneous | Auxiliary systems | Power supply | 1.29.1 | An off-grid power station may need to be provided by the Bidder for commencing the work. Diesel generators shall be arranged by the bidder on its own. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Juwi | RM | Other infrastructure | Auxiliary systems | Security Surveillance System | 1.25.5 | The Bidder shall provide security personnel for 24 h / 7 days a week for the whole year | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | [5 empty] | 1 |  | Open
Juwi | RM | Other infrastructure | Auxiliary systems | Security Surveillance System | 1.25.5 | The system shall comply with insurance requirements | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | [5 empty] | 1 |  | Open
Juwi | RM | Meteorological Sensors | Auxiliary Systems | Specific Requirements | 1.10.1 | Irradiation and temperature measurements are to be recorded at intervals of 15 min or less. | 1 |  | 1 |  |  |  | 1 min |  |  |  |  | 1 |  | Pass
Juwi | RM | Meteorological Sensors | Auxiliary Systems | Specific Requirements | 1.10.2 | Seven pyranometers shall be placed : three for measuring the horizontal plane irradiation and the others for the in-plane irradiation. | 1 | p383 5.0 Monitoring SLD |  |  | 1 | SLD is not sharp enough presented Hardware concept not readable |  | As in 1.10.2, it is seven pyranometer per system, please clarify the word "per system" | 1.1.1: "100 MWp (DC capacity at Standard Testing Conditions, abbreviated STC … hereinafter called 'the System') " |  |  | 1 |  | Open
Juwi | RM | Meteorological Sensors | Auxiliary Systems | Specific Requirements | 1.10.2 | The irradiation measurement equipment should be calibrated by an independent certified third party at least every two years. The calibration must be traceable to international standards. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Should be checked in list of deviations |  |  |  | 1 |  | Open
Juwi | RM | Meteorological Sensors | Auxiliary Systems | Specific Requirements | 1.10.3 | Ambient air and the module temperature shall be measured at every 5 installed MWp in conformity with IEC 60751 AA | 1 |  |  |  | 1 | SLD is not sharp enough presented Hardware concept not readable | [5 empty] | 1 |  | Open
Juwi | RM | Meteorological Sensors | Auxiliary Systems | Specific Requirements | 1.10.1 | The equipment should have the capability of recording and storing data for 24 hours using auxiliary DC power. | 1 |  | 1 |  |  |  | min. 2 weeks | Should be priority 1 question |  |  |  | 1 |  | Pass
Juwi | RM | Meteorological Sensors | Auxiliary Systems | Specific Requirements | 1.10.2 | The pyranometers should conform to the standards of ISO 9060 (SR5: secondary standard) or the WMO classification, and IEC 60904. | 1 |  | 1 |  |  |  |  | Do we need to know some parameter values according to standards mentioned or just a statement of comlience with the standard would be sufficient? | compliance will be necessary, no data due diligence right now. |  |  | 1 |  | Pass
Juwi | GD | PR and System Performance Guarantee | Compensations | O&M | 1.4.6 | If the successful Bidder defaults in being able to provide the O&M services required for the Systems performance guarantee, then it will be liable to cover all costs – but at least in the amount of Liquidated Damages imposed to the Employer by its PPA agreements - incurred by the Employer, including the loss of the guaranteed electricity export to the grid (but at a minimum rate of USD 0.20-per-kWh) for the disrupted period, in finding and hiring a replacement for the purpose. | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  | Cannot be evaluated at this stage. Only to be checked in list of deviations. |  |  |  | 1 | 1 | Open
Juwi | GD | PR and System Performance Guarantee | Compensations | O&M | 1.4.5 | For timely compensation the PR Calculation will be carried out provisionally for each quarter whereby the contractor and employer might jointly agree on different PR values for each quarter. In the last quarter of each calendar year the annual PR compensation of the full year will be carried out and any provisions will be offset by the annual compensation. | 3 |  |  |  | 1 |  |  | Cannot be evaluated at this stage. Only to be checked in list of deviations. |  |  |  | 1 |  | Open
Juwi | GD | PR and System Performance Guarantee | Compensations | O&M | 1.4.5 | If the annual measured PR falls below the guaranteed PR value according to Table 1.4.1, the liquidated damages will be levied on the successful Bidder at the rate of USD 0.20-per-kWh or the kWh Value the Employer receives for each kWh of shortfall – whichever is higher. Adjustments shall be made for any events outside the control of the O&M operator as grid outages, from grid operator ordered shutdowns, or force majeure events during the year. | 2 |  |  |  | 1 |  |  | Cannot be evaluated at this stage. Only to be checked in list of deviations. | Only to be checked in list of deviations. |  |  | 1 |  | Open
Juwi | GD | PR and System Performance Guarantee | Compensations | O&M | 1.4.5 | In case the PR is higher than the guaranteed PR value, the net value of this excess energy will be shared as follows: 50% towards the asset replacement fund, 25% towards the Employer, 25% towards the O&M contractor | 3 |  |  |  | 1 |  |  | Cannot be evaluated at this stage. Only to be checked in list of deviations. |  |  |  | 1 |  | Open
Juwi | GD | PR and System Performance Guarantee | Compensations | System PR | 1.4.4 | If the measured PR within further 30 days does not reach the guaranteed PR, the Employer can demand that the price of the system will be reduced by the percentage of shortfall times 1.2 for liquidated damages or the contractor will have to install more power at its own cost or combination of both. | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  | Cannot be evaluated at this stage. Only to be checked in list of deviations. |  |  |  | 1 | 1 | Open
Juwi | GD | PR and System Performance Guarantee | Compensations | System PR | 1.4.4 | The successful Bidder shall conduct the initial PR test for the daylight hours of at least 30 consecutive days, recording data at a frequency of fifteen minute intervals or less, to validate the guaranteed PR value for acceptance. Any excused downtime (e.g., from Grid Operator ordered shutdowns, grid failure, theft, force majeure) will be excluded from that calculation by an independent consultant (Auditing Body). That day will be taken out and another day added, if the initial PR falls short of the guaranteed PR value, the successful Bidder shall be obliged to identify and rectify the causes for the performance shortfall at their own cost. | 2 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  | Cannot be evaluated at this stage. Only to be checked in list of deviations. |  |  |  | 1 |  | Open
Juwi | GD | Conditions for Disqualification and Additional Information Required | Credentials | EPC | 1.2.6 | Approval from bidder to owners or owner representatives to answer questions freely regarding the past performance of the bidder and performance of the system against contractual obligations. | 2 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | [5 empty] | 1 |  | Open
Juwi | GD | Conditions for Disqualification and Additional Information Required | Credentials | EPC | 1.2.6 | Cumulative MWp of ground mounted PV turnkey installations >5 MWp with stating of actual MWp per project, project location, date of commissioning, module type and Inverter type. | 1 |  | 1 | [5 empty] | experience of Bidder / EPC |  |  | 1 | 1 | Pass
Juwi | GD | Conditions for Disqualification and Additional Information Required | Credentials | EPC | 1.2.6 | Detailed list of all the sites with the affirmation that the bidder played the leading EPC role in the turnkey installation of these systems. | 3 |  | 1 | [8 empty] | 1 |  | Pass
Juwi | GD | Conditions for Disqualification and Additional Information Required | Credentials | EPC | 1.2.6 | References and contact data (mail and phone) from owners of all installations > 5 MW with quotes of the corresponding system Performance Ratios, as well as system performance vs. initial yield assessment per year since the installation. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  | for selection of referenz objects |  |  | 1 | 1 | Open
Juwi | GD | Technical Bid Evaluation Criteria | Credentials | EPC | 1.3.1 | the systems have been completed on time and within budget, | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | [5 empty] | 1 | 1 | Open
Juwi | GD | Scope of the Bid | Credentials | EPC | 1.1.9 | The bid includes professional experience of the Bidders in ground mounted utility-scale PV and financial information about their long-term stability | 3 |  | 1 | [8 empty] | 1 |  | Pass
Juwi | GD | Scope of the Bid | Credentials | EPC | 1.1.10 | The Bidder, or the Lead company in case of JV is a EPC contractor | 1 |  | 1 |  |  |  |  | This is a non-technical question. We suggest such question should be separated from technical questions and placed in checklist for "General/Substantive Responsiveness of Bid" | a question of reliability and experience of solid understanding of the task/System Technology. See also 1.1.10 |  |  | 1 |  | Pass
Juwi | GD | Technical Bid Evaluation Criteria | Credentials | Guarantees | 1.3.1 | To have met the contractual requirements of the EPC and O&M deliverables including certificate to the effect that the entire equipment is brand new as required vide notification number NEPRA/UTS-01/777-779 dated Jan 21 ,2014, | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Only to be checked in list of deviations. |  |  |  | 1 | 1 | Open
Juwi | GD | Technical Bid Evaluation Criteria | Credentials | O&M | 1.3.1 | In case of a non-performance, comprehensible evidence has to be given why this case will not affect this project. | 3 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | [5 empty] | 1 |  | Open
Juwi | GD | Technical Bid Evaluation Criteria | Credentials | O&M | 1.3.1 | that they have started supplying electricity to the grid and are still operating satisfactorily in 9 out of 10 MW for all the cases | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | [5 empty] | 1 | 1 | Open
Juwi | GD | Conditions for Disqualification and Additional Information Required | Credentials | O&M | 1.2.6 | Cumulative MWp of ground mounted PV installations for which O&M services have been delivered by the bidder or his O&M subcontractor. | 2 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | [5 empty] | 1 |  | Open
Juwi | GD | Technical Bid Evaluation Criteria | Credentials | O&M | 1.3.2 | Prove at least 100 MW of EPC experience and 50 MW of full O&M experience for a period longer than 24 months. | 1 |  | 1 | [8 empty] | 1 |  | Pass
Juwi | GD | Conditions for Disqualification and Additional Information Required | Credentials | O&M | 1.2.6 | References, contact data and approval from owners or owner representatives of all installations > 5 MW from bidder or his O&M subcontractor to answer questions freely regarding the past performance of the bidder and performance of the system against contractual obligations. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | [5 empty] | 1 | 1 | Open
Juwi | MAW | Modules | Credentials | Project references | 1.14.8 | To show the proven technology a minimum of 500MW of proposed product type series must be in operation and reference projects shall be named. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Related to project references |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Juwi | MAW | Inverters | Credentials | Project references | 1.18.10 | A minimum of 100 MWp of similar product/type must be in operation and reference projects shall be named. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Juwi | JBU MAW | DC Cables | DC Cables | Design factors to be provided | 1.15.2 | String cable shall be of the following type: single conductor type, copper, 1000 V / Class II (according to protection class II / 1000V, IEC 61140, single core cable, tinned copper conductor, XLPE Insulation, double EVA jacket (resistant to heat and cold, resistant to ozone, UV, oil and chemicals), Temperature: 90 º C (Temperature Max. Allowable: 120 º C), Halogen free | 1 |  | 1 |  |  |  |  | It should be in accordance with the inverter values. | possibly 1500V for such system design |  |  | 1 |  | Pass
Juwi | JBU MAW | DC Cables | DC Cables | Design factors to be provided | 1.15.2 | Balance of electrical potential | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Need to be disscussed | equipotential bonding earthing mesh | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Juwi | JBU MAW | DC Cables | DC Cables | Design factors to be provided | 1.15.2 | Clear and systematic labelling required | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Juwi | JBU MAW | DC Cables | DC Cables | Design factors to be provided | 1.15.2 | Connectors of Modules and string cables shall be connected of self-locking type, have IP65 rating and shall be from same manufacturer and type | 1 |  | 1 | [8 empty] | 1 |  | Pass
Juwi | JBU MAW | DC Cables | DC Cables | Design factors to be provided | 1.15.2 | Installation to be verified by measurement-protocols | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Cannot be evaluated at this stage. | blanc protocol | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Juwi | JBU MAW | DC Cables | DC Cables | Design factors to be provided | 1.15.2 | Lifetime of 30 years is assured | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | What proof is required. | Life time test of nonmetal materials IEC 60811-408:2012 / (DIN EN 60811-408; VDE 0473-811-408:2012-12) 30 y assurance never seen until today | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Juwi | JBU MAW | DC Cables | DC Cables | Design factors to be provided | 1.15.2 | Sizing of cables shall be specified according to the number of modules and strings per array | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  | voltage drop calculation | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Juwi | JBU MAW | DC Cables | DC Cables | Design factors to be provided | 1.15.2 | The DC main (downstream of combiner box) wiring harness shall have the quality: Aluminum / Copper / 1000 V / Class II | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | It should be in accordance with the inverter values. | possibly 1500V for such system design | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Juwi | JBU MAW | DC Cables | DC Cables | Specific Requirements | 1.15.1 | Are Ohmic losses less than 1% at full power? Fail | 1 |  |  | 1 |  | Are Ohmic losses less than 1% at full power? | page 392, 2%; page 395, 1,4% |  | DC+AC losses < 2% | U |  | 1 |  | Fail
Juwi | JBU MAW | DC Cables | DC Cables | Standards | 1.15.3 | IEC 60364-1 | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Juwi | MAW | DC Connectors | DC Connectors | Standards | 1.16.2 | EN 50521 | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? | PV Connectors no, just a statement of compliance | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Juwi | MAW | DC Connectors | DC Connectors | Standards | 1.16.2 | IEC 60512 | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? | Connectors E-Systems no, just a statement of compliance | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Juwi | JBU MAW | DC Junction Box | DC Junction Box | Design factors to be provided | 1.17.1 | At least IP54 | 1 |  | 1 |  |  |  |  | DC Junction box is applicable in what conditions? | depending on DC Design |  |  | 1 |  | Pass
Juwi | JBU MAW | DC Junction Box | DC Junction Box | Design factors to be provided | 1.17.1 | Class 2 DC surge arrestor | 1 |  | 1 | [8 empty] | 1 |  | Pass
Juwi | JBU MAW | DC Junction Box | DC Junction Box | Design factors to be provided | 1.17.1 | DC fuses shall permit up to maximum 1000 V (or 1500V if designed). String box design, including all operating elements shall satisfy safety requirements | 1 |  | 1 |  |  |  |  | Will inverter voltage(1500V) effect the maximum voltage(1000V)? | depends on spec of inverter. |  |  | 1 |  | Pass
Juwi | JBU MAW | DC Junction Box | DC Junction Box | Design factors to be provided | 1.17.1 | Dust and heat protection | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Juwi | JBU MAW | DC Junction Box | DC Junction Box | Design factors to be provided | 1.17.1 | Monitored input-couples | 1 |  | 1 | [8 empty] | 1 |  | Pass
Juwi | JBU MAW | DC Junction Box | DC Junction Box | Specifications | 1.17.2 | Current monitoring | 1 |  | 1 | [8 empty] | 1 |  | Pass
Juwi | JBU MAW | DC Junction Box | DC Junction Box | Specifications | 1.17.2, 1.17.1 | Monitoring interface for SCADA | 1 |  | 1 | [8 empty] | 1 |  | Pass
Juwi | JBU MAW | DC Junction Box | DC Junction Box | Specifications | 1.17.2 | Touch-safe protective cover | 1 |  |  |  | 1 |  |  |  |  | C |  | 1 |  | Open
Juwi | JBU MAW | DC Junction Box | DC Junction Box | Standards | 1.17.3 | EN 50178 | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? | High currat devices no, just a statement of compliance | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Juwi | JBU MAW | DC Junction Box | DC Junction Box | Standards | 1.17.3 | EN 60439-1 | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? | arcing fault / Störlichtbogen Verhalten no, just a statement of compliance | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Juwi | JBU MAW | DC Junction Box | DC Junction Box | Standards | 1.17.3 | EN 61000-6 | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? | EMV no, just a statement of compliance | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Juwi | JBU | Step-up Transformers/MV Switchgear | Due Diligence | Quality Assurance | 1.21.3 | Factory witness testing will be required for MV transformer and switchgear to be installed at this project. The cost of the due diligence to be carried by the Employer through an independent technical consultant will be taken over by the successful bidder up to an amount of 30,000 USD. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Juwi | MAW | Inverters | Due diligence | Quality Assurance | 1.18.12 | The Bidder accepts that the cost of the Quality assurance for Inverters to be carried by the Employer through an independent technical consultant shall be taken over by the successful bidder up to an amount of 100,000 USD. | 1 |  |  |  | 1 |  |  |  |  | C |  | 1 |  | Open
Juwi | MAW | Modules | Due Diligence | Quality Assurance | 1.14.6 | The bidder will bear the cost of the Quality assurance for PV modules on-site and in laboratory to be carried out by the Employer through an independent technical consultant up to 150,000 USD. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Juwi | GD | Technical Bid Evaluation Criteria | Due Diligence | Quality Assurance | 1.3.5 | The cost of the due diligence to be carried out by the Employer through an independent technical consultant before contract signature will be taken over by the successful bidder up to an amount of 50,000 USD independent of the result. The due diligence will cover a module factory visit, an inverter factory inspection and a due diligence on the provided financial, EPC and O&M credentials including up to three site visits. | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  | Only to be checked in list of deviations. |  |  |  | 1 |  | Open
Juwi | GD | Scope of the Bid | General items | Guarantees | 1.1.5 | Energy Purchase Agreement (EPA) practices are followed | 1 |  |  |  | 1 | Important reasons: due to current uncertainty of the criteria we accept an open status. Please clarify that yo acknowledge the criteria and comply unless a reason of high importance will not allow you you to comply. In such a situation the parties will seek to agree a compromise. |  | This cannot be evaluated at this stage. | we need a sentence that it should and can only be disregarded for important reasons |  |  | 1 |  | Open
Juwi | JBS | Labelling | General items | Labelling | 1.26 | the ID numbering / coding system shall allow unique identification of all components and be understandable | 1 |  |  |  | 1 | Unclear: We do not understand your proposal, please detail your proposal. Especially confirm that you are compliant with our requested criteria. |  | Cannot be evaluated at this stage |  | C |  | 1 |  | Open
Juwi | JBS | Labelling | General items | Labelling | 1.26 | Tags shall be weather and UV resistant. | 1 |  |  |  | 1 |  |  | Cannot be evaluated at this stage |  | C |  | 1 |  | Open
Juwi | JBS | Labelling | General items | Labelling | 1.26 | The ID’s shall correspond to all drawings, plant documentation and control system. | 1 |  |  |  | 1 |  |  | Cannot be evaluated at this stage |  | C |  | 1 |  | Open
Juwi | GD | Scope of the Bid | General items | Quality Assurance | 1.1.3 | Defect components consequences: If one tested sample fails in one criterion, all items of the same category will be regarded as failed and rejected. | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  | Only to be checked in list of deviations. | yes, we need to be sure that they comply as for most of the critera |  |  | 1 | 1 | Open
Juwi | GD | Scope of the Bid | General items | Specific Requirements | 1.1.2 | The Offer shall include a list of all vendors and/or sub-contractors for major equipment. | 1 |  |  |  | 1 | [6 empty] | 1 |  | Open
Juwi | GD | Scope of the Bid | General items | Specific Requirements | 1.1.9 | The bid covers the planning of the System design, the required functionality of the System in terms of its sub-systems and components, detailed feature-wise descriptions of the components to be used in the System, the planning of the System installation, its integration, testing, monitoring, commissioning and O&M of the System | 1 |  |  | 1 |  | We can not find all of the requested criteria in your documents. Please confirm that your bid is compliant with all expectations and requirements of Section 6 of the RFP and provide a list with ALL exeptions or alterations. This applies to both, the EOPC And the O&M part. |  | This question should be removed as detailed design of every component/sub-system will be checked and evaluated thoroughly in technical evaluation | no, its an overall critera an need to be met |  |  | 1 | 1 | Fail
Juwi | JBS | Basic Scope of Supply | General items | Specific Requirements | 1.6 | The maximum DC voltage shall not exceed 1500 V | 1 | Page 392-395 | 1 | [8 empty] | 1 |  | Pass
Juwi | JBS | Basic Scope of Supply | General items | Specific Requirements | 1.6 | The required AC voltage / frequency at grid connection shall 132 kV/50 Hz | 1 |  | 1 | [8 empty] | 1 |  | Pass
Juwi | JBS | Equipment guarantees | Inverter | Guarantees | 1.28.2 | The Successful Bidder shall provide an Inverter warranty of at least 5 years. A spare parts warranty shall be included for the 25 years operational period. | 1 |  |  |  | 1 |  | kein Hinweis, dass die Verlängerung auf 25 im Angebot enthalten |  |  | C |  | 1 |  | Open
Juwi | JBU | Inverter/Transformer Station | Inverter/Transformer Station | Specific Requirements | 1.22 | All stations shall be equipped with fire and smoke detectors and alarm, connected to security and surveillance system | 1 |  |  |  | 1 | Unclear: We do not understand your proposal, please detail your proposal. Especially confirm that you are compliant with our requested criteria. |  |  |  | U |  | 1 |  | Open
Juwi | JBU | Inverter/Transformer Station | Inverter/Transformer Station | Specific Requirements | 1.22 | Bidder shall firmly specify the number of stations, manufacturer, capacity and type of equipment. | 1 |  | 1 | [8 empty] | 1 |  | Pass
Juwi | JBU | Inverter/Transformer Station | Inverter/Transformer Station | Specific Requirements | 1.22 | Every ten (10) or lesser number of stations shall be equipped with an earthing and short-circuiting equipment | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  |  |  | C |  | 1 |  | Open
Juwi | JBU | Inverter/Transformer Station | Inverter/Transformer Station | Specific Requirements | 1.22 | Fine sand filters shall be installed | 1 |  |  |  | 1 | Unclear: We do not understand your proposal, please detail your proposal. Especially confirm that you are compliant with our requested criteria. |  |  |  | U |  | 1 |  | Open
Juwi | JBU | Inverter/Transformer Station | Inverter/Transformer Station | Specific Requirements | 1.22 | The station shall enable the grounding of hardware and neutral will be left ground isolated | 1 |  |  |  | 1 | Unclear: We do not understand your proposal, please detail your proposal. Especially confirm that you are compliant with our requested criteria. |  |  |  | U |  | 1 |  | Open
Juwi | MAW | Inverters | Inverters | Design factors to be provided | 1.18.7 | Cooling method | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Juwi | MAW | Inverters | Inverters | Design factors to be provided | 1.18.7 | Detection of insulation faults | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Juwi | MAW | Inverters | Inverters | Design factors to be provided | 1.18.7 | Input voltage range (The voltage window for MPP tracking shall accommodate the expected degradation of the modules.) | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Juwi | MAW | Inverters | Inverters | Design factors to be provided | 1.18.7 | Integrated transformer/transformerless / Outside Dry Type Transformer | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Juwi | MAW | Inverters | Inverters | Design factors to be provided | 1.18.7 | Maximum output current | 1 | page 291 | 1 | [8 empty] | 1 |  | Pass
Juwi | MAW | Inverters | Inverters | Design factors to be provided | 1.18.7 | Nominal output frequency, 3-phase | 1 | page 291 | 1 | [8 empty] | 1 |  | Pass
Juwi | MAW | Inverters | Inverters | Design factors to be provided | 1.18.7 | Nominal output voltage | 1 | page 291 | 1 | [8 empty] | 1 |  | Pass
Juwi | MAW | Inverters | Inverters | Design factors to be provided | 1.18.7 | Nominal power | 1 | page 291 | 1 | [8 empty] | 1 |  | Pass
Juwi | MAW | Inverters | Inverters | Design factors to be provided | 1.18.7 | Operating temperature range | 1 | page 291 | 1 |  |  |  |  | What is the acceptable range? | 60°C Derating? |  |  | 1 |  | Pass
Juwi | MAW | Inverters | Inverters | Design factors to be provided | 1.18.7 | Output voltage range | 1 | page 291 | 1 | [8 empty] | 1 |  | Pass
Juwi | MAW | Inverters | Inverters | Design factors to be provided | 1.18.7 | Peak efficiency/ Weighted efficiency | 1 | page 291 | 1 | [8 empty] | 1 |  | Pass
Juwi | MAW | Inverters | Inverters | Design factors to be provided | 1.18.7 | Protection rating: NEMA 3R, IP54/IP55/IP60 | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Juwi | MAW | Inverters | Inverters | Design factors to be provided | 1.18.7 | PV array configuration options: positive ground, negative ground | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Juwi | MAW | Inverters | Inverters | Functionalities | 1.18.3 | Active power control reduction: remotely set point of control in case of network congestions or risk of system collapse, if deemed necessary | 1 | page 291 | 1 |  |  |  |  | 8.2 needs to ensure these questions are answered in the bids. |  |  |  | 1 |  | Pass
Juwi | MAW | Inverters | Inverters | Functionalities | 1.18.3 | Anti-islanding protection | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Juwi | MAW | Inverters | Inverters | Functionalities | 1.18.3 | Frequency regulation | 1 | page 291 | 1 |  |  |  |  | 8.2 needs to ensure these questions are answered in the bids. |  |  |  | 1 |  | Pass
Juwi | MAW | Inverters | Inverters | Functionalities | 1.18.3 | Limitation of voltage fluctuation due to switching operations and long-term flicker | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | 8.2 needs to ensure these questions are answered in the bids. |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Juwi | MAW | Inverters | Inverters | Functionalities | 1.18.3 | Limitation of current harmonics and higher frequency components up to 9 kHz | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Juwi | MAW | Inverters | Inverters | Functionalities | 1.18.3 | Limitation of short-circuit current | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | 8.2 needs to ensure these questions are answered in the bids. |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Juwi | MAW | Inverters | Inverters | Functionalities | 1.18.3 | Limitation of steady-stage voltage changes to 2% of the nominal value | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Juwi | MAW | Inverters | Inverters | Functionalities | 1.18.3 | Matching grid voltage and frequency at point-of-coupling | 1 | page 291 | 1 | [8 empty] | 1 |  | Pass
Juwi | MAW | Inverters | Inverters | Functionalities | 1.18.3 | Maximum Power Point Tracking (MPPT) and string/sub-array management | 1 | page 291 | 1 | [8 empty] | 1 |  | Pass
Juwi | MAW | Inverters | Inverters | Functionalities | 1.18.3 | Voltage and frequency fault ride-through: no disconnection of the connection through voltage dip and change of active power generation, feed-in of reactive power during the fault for voltage stabilisation | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | 8.2 needs to ensure these questions are answered in the bids. |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Juwi | MAW | Inverters | Inverters | Functionalities | 1.18.3 | Voltage regulation through reactive power support: remotely set point control for voltage stability | 1 | page 291 | 1 |  |  |  |  | 8.2 needs to ensure these questions are answered in the bids. |  |  |  | 1 |  | Pass
Juwi | MAW | Inverters | Inverters | Manufacturers confirmation | 1.18.9 | The Bidder shall deliver a manufacturer's confirmation in his Bid for the suitability of the inverter for the specific weather conditions applicable in Bahawalpur Pakistan. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Juwi | MAW | Inverters | Inverters | Quality Assurance | 1.18.11 | After commissioning, 1 of 10 inverters will be measured on site (power curve and efficiency) by an approved independent technical consultant on behalf of the Employer. The on-site measurements shall be accepted by the Bidder as average values for all inverters | 1 |  |  |  | 1 |  |  | Cannot be evaluated at this stage | compliance! | C |  | 1 |  | Open
Juwi | MAW | Inverters | Inverters | Quality Assurance | 1.18.11 | Check of protection against overload, short-circuit, grid-failure, internal failure, over-temperature (de-rating), surge protection, detection of insulation faults of AC Cables. Bidder shall firmly specify the manufacturer, types and length of cables to be installed | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | 8.2 needs to ensure these questions are answered in the bids. |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Juwi | MAW | Inverters | Inverters | Quality Assurance | 1.18.11 | Test run and check of MPP tracking of all inverters | 1 |  |  |  | 1 |  |  | 8.2 needs to ensure these questions are answered in the bids. |  | C |  | 1 |  | Open
Juwi | MAW | Inverters | Inverters | Quality Assurance | 1.18.11 | Test run in the field for maximum and EU-efficiency of all Inverters | 1 |  |  |  | 1 |  |  | 8.2 needs to ensure these questions are answered in the bids. |  | C |  | 1 |  | Open
Juwi | MAW | Inverters | Inverters | Quality Assurance | 1.18.11 | The Bidder shall deliver detailed protocols of performance test run (warm power test) for every single inverter | 1 |  |  |  | 1 |  |  | Cannot be evaluated at this stage |  | C |  | 1 |  | Open
Juwi | MAW | Inverters | Inverters | Specific Requirements | 1.18.6 | Specifications of table in Schedule C shall be met | 1 | page 291 | 1 |  |  |  |  | Link to table |  |  |  | 1 |  | Pass
Juwi | MAW | Inverters | Inverters | Standards | 1.18.8 | IEEE 1547 | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? | no, just a statement of compliance Interconnecting Distributed Resources | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Juwi | MAW | Inverters | Inverters | Standards | 1.18.8 | TUV, VDE, or equivalent certification of passing the relevant standards | 1 | page 291 | 1 | [8 empty] | 1 |  | Pass
Juwi | MAW | Inverters | Inverters | Strategic Reason for Inverter Selection | 1.18.2 | Available uptime | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Juwi | MAW | Inverters | Inverters | Strategic Reason for Inverter Selection | 1.18.2 | Balance of System (BOS) costs of inverter and labour | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  | financial bid | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Juwi | MAW | Inverters | Inverters | Strategic Reason for Inverter Selection | 1.18.2 | Concept of protection against overload, short-circuit, grid-failure, internal failure, over-temperature (de-rating), surge protection | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Its too general, needs to be reviewed. | failure codes and consquences (automatic/manual restart, throw away safety devices) | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Juwi | MAW | Inverters | Inverters | Strategic Reason for Inverter Selection | 1.18.2 | Dust and heat protection | 1 |  | 1 | [5 empty] | derating? |  |  | 1 |  | Pass
Juwi | MAW | Inverters | Inverters | Strategic Reason for Inverter Selection | 1.18.2 | Timely and effective monitoring at a granular/zoomed-in level | 1 |  | 1 | [8 empty] | 1 |  | Pass
Juwi | GD | Scope of the Bid | Layout | Guarantees | 1.1.6 | The bidder confirms that the system complies with all applicable requirements of the NEPRA Grid Code of Pakistan and its Draft Amendment no. 2 for Solar Power Projects. | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  | Only to be checked in list of deviations. |  |  |  | 1 |  | Open
Juwi | JBS | Physical layout | Layout | Specific Requirements | 1.7.2 | Provide a schematic electrical Single Line Diagram (SLD) of the entire System layout from the modules to the grid-connection, identifying and listing all of the following DC and AC components. | 1 | Page 307 - 310 | 1 | [8 empty] | 1 |  | Pass
Juwi | JBS | Physical layout | Layout | Specific Requirements | 1.7.2 | The system design shall be such as to ensure ease of maintenance and a multiple ring main unit (RMU) philosophy (on MV level) must be followed for circuit breaker configuration. | 1 | Page 310 | 1 |  |  |  | Stichleitung mit 5 Stationen max. |  |  | U |  | 1 |  | Pass
Juwi | MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Bills of Materials, BoMs: (glass, encapsulant, backsheet, ribbon, adhesives, cable, junction box, connector) | 1 |  | 1 | [7 empty] | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | 1 |  | Pass
Juwi | MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Current at the maximum current point | 1 | page 59 | 1 | [8 empty] | 1 |  | Pass
Juwi | MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Degradation Curve from Manufacturer | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Juwi | MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Manufacturers confirmation for the suitability of module for specific weather conditions and the high UV-radiation | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  | especially reliability at high UV irridiance / Product warranty | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Juwi | MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Manufacturers installation guidelines | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Juwi | MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Materials and workmanship warranty of a minimum of 10 years | 1 | page 59 | 1 |  |  |  | 12 years |  |  |  |  | 1 |  | Pass
Juwi | MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Maximum rated power | 1 | page 59 | 1 | [8 empty] | 1 |  | Pass
Juwi | MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Maximum system voltage | 1 | page 59 | 1 | [5 empty] | … at SK-II safety class |  |  | 1 |  | Pass
Juwi | MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Minimum efficiency at 200 W/m² (25°, AM 1.5) | 1 | page 59 | 1 | [8 empty] | 1 |  | Pass
Juwi | MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Open-circuit voltage | 1 | page 59 | 1 | [7 empty] | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | 1 |  | Pass
Juwi | MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Operating temperature range and nominal operating cell temperature NOCT | 1 | page 59 | 1 |  |  |  |  | What range is acceptable | There is as small range anyway Will result in the PR losses |  |  | 1 |  | Pass
Juwi | MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Power warranty/performance guarantee of a minimum of 25 years: the power output should not fall below 90% within 10 years, and below 80% within 25 years; linear warranty mandatory | 1 | page 59 | 1 | [7 empty] | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | 1 |  | Pass
Juwi | MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Provide guarantees and data sheets (to be transferred to Employer upon COD) | 1 |  | 1 | [8 empty] | 1 |  | Pass
Juwi | MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Rated power tolerance | 1 | page 59 | 1 | [8 empty] | 1 |  | Pass
Juwi | MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Short-circuit current | 1 | page 59 | 1 | [7 empty] | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | 1 |  | Pass
Juwi | MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Specify number of modules and total MWp to be provided | 1 | page 392 | 1 | [8 empty] | 1 |  | Pass
Juwi | MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Tolerance to wind (maximum load) impact (mechanical load) | 1 | page 59 | 1 | [5 empty] | minimum 2400 Pa |  |  | 1 |  | Pass
Juwi | MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Type of cells comprising the module, and number of cells in series | 1 | page 59 | 1 | [5 empty] | manufacturer |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | 1 |  | Pass
Juwi | MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Voltage at the maximum power point | 1 | page 59 | 1 | [7 empty] | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | 1 |  | Pass
Juwi | JBS | Equipment guarantees | Modules | Guarantees | 1.28.1 | The Successful bidder shall provide a Module warranty of at least 10 years. The performance warranty of the module shall be linear with a fixed factor over 25 years. | 1 | Page 17 | 1 |  |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  | To be discussed |  |  |  | 1 |  | Pass
Juwi | MAW | Modules | Modules | Pre-shipment quality assurance | 1.14.4 | All modules must undergo Electroluminiscense (EL) inspection with a resolution of minimum 4 MPixel prior to shipment. | 1 | page 89 | 1 |  |  |  |  | Cannot be evaluated at this stage. | compliance necessary |  |  | 1 |  | Pass
Juwi | MAW | Modules | Modules | Pre-shipment quality assurance | 1.14.7 | Warranties and evidence shall be given by the bidder that their selected modules have been tested for susceptibility to Potential Induced Degradation (PID). | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | Additional Tests available |  |  | C |  | 1 |  | Open
Juwi | MAW | Modules | Modules | Pre-shipment quality assurance | 1.14.4 | A sufficient EVA cross linking has to be verified per production line through a gel content test supervised by an accredited (IEC 17025 or national pendant) independent certified module testing agency. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Cannot be evaluated at this stage. | compliance necessary | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Juwi | MAW | Modules | Modules | Pre-shipment quality assurance | 1.14.4 | Pre-shipment flash tested data Quality assurance for PV modules on-site and in laboratory simulator must meet the class AAA requirements of IEC 60904-9. The sun simulator must be calibrated with a reference cell, which itself was calibrated by a member of the WPVS scheme, with a maximum uncertainty of Isc of 1%. unique barcode (SNr) and labelled performance headlines (P(mpp), I(sc), U(oc), I(mpp), U(mpp) maximum current, maximum voltage Positive power sorting | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Cannot be evaluated at this stage. | compliance necessary | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Juwi | MAW | Modules | Modules | Quality assurance on site | 1.14.5 | The modules shall undergo an incoming inspection at arrival on construction site. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Cannot be evaluated at this stage. | stated and accepted | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Juwi | MAW | Modules | Modules | Standards (as applicable to crystalline silicion or thin-film) | 1.14.3 | IEC 60364-4-41 | 1 | page 59 |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? | no, just a statement of compliance 'protection against electric shock | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Juwi | MAW | Modules | Modules | Standards (as applicable to crystalline silicion or thin-film) | 1.14.3 | IEC 60904-1, IEC 60904-3 | 1 | page 59 |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? | no, just a statement of compliance | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Juwi | MAW | Modules | Modules | Standards (as applicable to crystalline silicion or thin-film) | 1.14.3 | IEC 61215 | 1 | page 59 | 1 |  |  |  |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? | no, just a statement of compliance |  |  | 1 |  | Pass
Juwi | MAW | Modules | Modules | Standards (as applicable to crystalline silicion or thin-film) | 1.14.3 | IEC 61416 | 1 | page 59 |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? | not existing | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Juwi | MAW | Modules | Modules | Standards (as applicable to crystalline silicion or thin-film) | 1.14.3 | IEC 61646 | 1 | page 59 |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? | no, just a statement of compliance | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Juwi | MAW | Modules | Modules | Standards (as applicable to crystalline silicion or thin-film) | 1.14.3 | IEC 61701 | 1 | page 59 |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? | no, just a statement of compliance | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Juwi | MAW | Modules | Modules | Standards (as applicable to crystalline silicion or thin-film) | 1.14.3 | IEC 61730 | 1 | page 59 | 1 |  |  |  |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? | no, just a statement of compliance |  |  | 1 |  | Pass
Juwi | MAW | Inverters | Monitoring | Functionalities | 1.18.3 | Advanced communication, with intelligent alerts/warnings, to the SCADA server | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Juwi | JBS | Equipment guarantees | Mounting | Guarantees | 1.28.3 | The Successful Bidder shall provide a product warranty for the structure of at least 10 years. | 1 | Page 18 | 1 | [8 empty] | 1 |  | Pass
Juwi | RM | Mounting | Mounting | Specific Requirements | 1.13.8 | The mounting structures must be earthed | 1 |  |  |  | 1 | [6 empty] | 1 |  | Open
Juwi | RM | Mounting | Mounting | Specific Requirements | 1.13.1 | The system is fixed-tilted. Tilt angle is specified. | 1 |  | 1 |  |  | tilt 10° - pleas explain with PVSyst analyse with 20° | [5 empty] | 1 |  | Pass
Juwi | RM | Mounting | Mounting | Specific Requirements | 1.13.5 | All fastening structures must be verified for durability and resistance to environmental degradation for 25 years | 1 |  |  |  | 1 | Location: No information in Annexxure4. We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | What sort of mechanism is required for verification? | Sub structure description / materials double to line 172 - 175 |  |  | 1 |  | Open
Juwi | RM | Mounting | Mounting | Specific Requirements | 1.13.3 | Mounting structure is made of durable material, resistant to sandstorms and compatible with the module frame material so as to avoid any adverse electrolytic/galvanic effects. | 1 |  |  |  | 1 | Location: No information in Annexxure4. We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Information about materials to be known before evaluation. | right |  |  | 1 |  | Open
Juwi | RM | Mounting | Mounting | Specific Requirements | 1.13.3 | Mounting system resists corrosion (passing the salt spray test IEC 61701, among other verification), | 1 |  |  |  | 1 | Location: No information in Annexxure4. We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Information about materials to be known before evaluation. | right |  |  | 1 |  | Open
Juwi | RM | Mounting | Mounting | Specific Requirements | 1.13.3 | Mounting system resists high wind speeds (up to 40 m/s) | 1 |  |  |  | 1 | Location: No information in Annexxure4. We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | [5 empty] | 1 |  | Open
Juwi | RM | Mounting | Mounting | Specific Requirements | 1.13.3 | Mounting system resists UV induced degradation | 1 |  |  |  | 1 | Location: No information in Annexxure4. We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | [5 empty] | 1 |  | Open
Juwi | RM | Mounting | Mounting | Specific Requirements | 1.13.9 | Specific site conditions have been considered. | 1 |  | 1 |  |  |  |  | Needs to be discussed. | … specific requirements of the soil conditions Static |  |  | 1 |  | Pass
Juwi | JBU | Step-up Transformers/MV Switchgear | MV Switchgear | Design factors to be provided | 1.21.4 | Rated lightning impulse voltage | 1 |  | 1 | [8 empty] | 1 |  | Pass
Juwi | JBU | Step-up Transformers/MV Switchgear | MV Switchgear | Design factors to be provided | 1.21.4 | Rated power frequency withstand voltage | 1 |  | 1 | [8 empty] | 1 |  | Pass
Juwi | JBU | Step-up Transformers/MV Switchgear | MV Switchgear | Design factors to be provided | 1.21.4 | Rated short circuit current | 1 |  | 1 | [8 empty] | 1 |  | Pass
Juwi | JBU | Step-up Transformers/MV Switchgear | MV Switchgear | Design factors to be provided | 1.21.4 | System maximum voltage | 1 |  | 1 | [8 empty] | 1 |  | Pass
Juwi | JBU | Step-up Transformers/MV Switchgear | MV Switchgear | Design factors to be provided | 1.21.4 | System nominal voltage | 1 |  | 1 | [8 empty] | 1 |  | Pass
Juwi | JBU | Step-up Transformers/MV Switchgear | MV Switchgear | Specific Requirements | 1.21.4 | Interlocks will also be mechanically interlocked between line MV switchgears. | 1 |  | 1 | [8 empty] | 1 |  | Pass
Juwi | JBU | Step-up Transformers/MV Switchgear | MV Switchgear | Specific Requirements | 1.21.4 | MV Switchgears shall be SF6 gas insulated or VCB (Vacuum circuit breaker). | 1 |  | 1 | [8 empty] | 1 |  | Pass
Juwi | JBU | Step-up Transformers/MV Switchgear | MV Switchgear | Specific Requirements | 1.21.4 | The separating equipment shall be installed with visible disconnection (pivotable disconnectors). | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  | Cannot be evaluated at this stage |  | C |  | 1 |  | Open
Juwi | JBU | Step-up Transformers/MV Switchgear | MV Switchgear | Standards | 1.21.5 | IEC 60529 | 1 |  | 1 |  |  |  |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  |  |  | 1 |  | Pass
Juwi | JBU | Step-up Transformers/MV Switchgear | MV Switchgear | Standards | 1.21.5 | IEC 62271-200 | 1 |  | 1 |  |  |  |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  |  |  | 1 |  | Pass
Juwi | JBU | Step-up Transformers/MV Switchgear | MV Switchgear | Standards | 1.21.5 | IEC 62446 | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Juwi | JUE | Main Annual Inspection | O&M | Auxiliary system | 2.4.5 | Maintenance of all components according to manufacturer instruction | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing |  |  |  |  | 1 |  | Open
Juwi | JUE | Initial Inspection | O&M | General Requirements | 2.2.2 | Maintenance routines, inspection check-lists, working files, | 1 |  | 1 | [8 empty] | 1 |  | Pass
Juwi | JUE | Scope of the Bid | O&M | General Requirements | 2.1.2 | Cleaning of Modules and irradiation sensors to prevent dust accumulation to undesirable level. | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | additional bid for cleaning can be issued is required!! |  |  |  |  | 1 |  | Open
Juwi | JUE | Scope of the Bid | O&M | General Requirements | 2.1.2 | Cleaning of the Plant, preventive and corrective maintenance of the civil works and the fences. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing |  |  |  |  | 1 |  | Open
Juwi | JUE | Scope of the Bid | O&M | General Requirements | 2.1.2 | Coordination and compliance with NTDC requirements | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing |  |  |  |  | 1 |  | Open
Juwi | JUE | Scope of the Bid | O&M | General Requirements | 2.1.2 | Corrective maintenance with guaranteed response times | 1 |  | 1 | [8 empty] | 1 |  | Pass
Juwi | JUE | Scope of the Bid | O&M | General Requirements | 2.1.2 | Daily, monthly and yearly performance and production reporting | 1 |  |  |  | 1 | L | not completely described |  |  |  |  | 1 |  | Open
Juwi | JUE | Initial Inspection | O&M | General Requirements | 2.2.1 | familiarize himself with the specific plant equipment and specific maintenance requirements / training of staff | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing |  |  |  |  | 1 |  | Open
Juwi | JUE | Scope of the Bid | O&M | General Requirements | 2.1.2 | Operation of the Plant (including 24/7 presence of O&M and security staff on the project site). | 1 |  |  |  | 1 |  | only day time |  |  |  |  | 1 |  | Open
Juwi | JUE | Scope of the Bid | O&M | General Requirements | 2.1.2 | Optimal level of SCADA monitoring | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing |  |  |  |  | 1 |  | Open
Juwi | JUE | Scope of the Bid | O&M | General Requirements | 2.1.2 | Performance variance analysis of the module strings and inverters | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing |  |  |  |  | 1 |  | Open
Juwi | JUE | Scope of the Bid | O&M | General Requirements | 2.1.2 | Periodic maintenance of inverter, transformer, combiner boxes etc., according manufacturer's requirements | 1 |  |  |  | 1 | according manufacturer's requirements is confirmable | missing |  |  |  |  | 1 |  | Open
Juwi | JUE | Scope of the Bid | O&M | General Requirements | 2.1.2 | Provide all O&M Staff, trained and certified as far as applicable. For security reasons, a 24 h/ 7 days a week staffing of security and maintenance shall be provided. The staffing concept and selected key employees shall be presented to the Employer for approval. | 1 | Schedule F 1.1 |  |  | 1 | 5 days or 24/7 ? | additional |  |  |  |  | 1 |  | Open
Juwi | JUE | Scope of the Bid | O&M | General Requirements | 2.1.2 | Responsibility to keep Performance Ratio and Availability at highest levels | 1 |  |  |  | 1 | L | missing |  |  |  |  | 1 |  | Open
Juwi | JUE | Scope of the Bid | O&M | General Requirements | 2.1.2 | Scheduled maintenance routines: e.g., inspections of modules with polarized sunglasses to check for discolouration, the first signs of de-lamination, loose wires in the electronics, corrosion of mounting structures, erosion | 1 |  | 1 | [8 empty] | 1 |  | Pass
Juwi | JUE | Scope of the Bid | O&M | General Requirements | 2.1.2 | Warranties and insurance policies should be assignable/transferrable to the Employer in case it decides to take over the O&M | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing |  |  |  |  | 1 |  | Open
Juwi | MAW | Inverters | O&M | Guarantees | 1.18.2 | For central inverters concept: the bidder shall ensure with an undertaking from the manufacturer that the concerned skilled staff will be made available at the site within 24 hours of reporting the defect to the manufacturer. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Juwi | JUE | Main Annual Inspection | O&M | Inverter (100%) | 2.4.2 | Check of the safety circuit for the interruption of the AC-grid protection in the case of failure (emergency shut-off, over-/ under-voltage, over temperature, etc.) based on the local conditions | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | not completely described |  |  |  |  | 1 |  | Open
Juwi | JUE | Main Annual Inspection | O&M | Inverter (100%) | 2.4.2 | Functional check of internal and external over- and under-voltage monitoring through operation of test terminal | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | not completely described |  |  |  |  | 1 |  | Open
Juwi | JUE | Main Annual Inspection | O&M | Inverter (100%) | 2.4.2 | Functional check of insulation monitoring | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | not completely described |  |  |  |  | 1 |  | Open
Juwi | JUE | Bi-annual inspection | O&M | Inverter (100%) | 2.3.2 | Functional check of ventilator system of inverter station | 1 |  | 1 | [8 empty] | 1 |  | Pass
Juwi | JUE | Main Annual Inspection | O&M | Inverter (100%) | 2.4.2 | Inspection of over-voltage protection and upstream fuses regarding external damage | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | not completely described |  |  |  |  | 1 |  | Open
Juwi | JUE | Bi-annual inspection | O&M | Inverter (100%) | 2.3.2 | Inspection of the interior of the electrical cabinet regarding dust deposit, dirtiness, humidity, water penetration from outside. If necessary the cabinet has to be cleaned. | 1 |  | 1 | [8 empty] | 1 |  | Pass
Juwi | JUE | Main Annual Inspection | O&M | Inverter (100%) | 2.4.2 | Maintenance of inverters according to manufacturer instruction | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing |  |  |  |  | 1 |  | Open
Juwi | JUE | Bi-annual inspection | O&M | Inverter (100%) | 2.3.2 | Maintenance of inverters according to manufacturer's instruction. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | L according manufacturer's instruction is confirmable |  |  |  |  | 1 |  | Open
Juwi | JUE | Main Annual Inspection | O&M | Inverter (100%) | 2.4.2 | Test of the internal miniature circuit breakers and power switch, test of emergency shut-off | 1 |  | 1 | [8 empty] | 1 |  | Pass
Juwi | JUE | Bi-annual inspection | O&M | Inverter (100%) | 2.3.2 | Testing of inverter features according to maintenance schedule of manufacturer. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | L according manufacturer's instruction is confirmable |  |  |  |  | 1 |  | Open
Juwi | JUE | Main Annual Inspection | O&M | Inverter (100%) | 2.4.2 | Visual inspection of AC and DC clamps regarding tightness and colouring, tightening of clamps | 1 |  | 1 |  |  | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | [5 empty] | 1 |  | Pass
Juwi | JUE | Main Annual Inspection | O&M | Inverter (100%) | 2.4.2 | Visual inspection of all fuses | 1 |  |  |  | 1 |  | missing |  |  |  |  | 1 |  | Open
Juwi | JUE | Bi-annual inspection | O&M | Maintenance | 2.3.3 | Maintenance of all Power plant components according to manufacturer's instructions | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | L according manufacturer's instruction is confirmable |  |  |  |  | 1 |  | Open
Juwi | JUE | Bi-annual inspection | O&M | PV Generator | 2.3.1 | 100% visual inspection of modules regarding damage in spring | 1 |  |  |  | 1 | 100% visual inspection of modules regarding damage in spring is confirmable | [5 empty] | 1 |  | Open
Juwi | JUE | Bi-annual inspection | O&M | PV Generator | 2.3.1 | Cleaning of all modules | 1 |  |  |  | 1 | additional bid for cleaning can be issued is required!! | additional bid for cleaning can be issued |  |  |  |  | 1 |  | Open
Juwi | JUE | Bi-annual inspection | O&M | PV Generator | 2.3.1 | Cleaning of sensors and switches | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | sensors shall be done by independent Meteo Station Operator |  |  |  |  | 1 |  | Open
Juwi | JUE | Main Annual Inspection | O&M | PV Generator | 2.4.1 | Inspection of DC distribution box: Visual inspection of all clamps and degree of pollution. Testing of over-voltage protection | 1 |  | 1 | [8 empty] | 1 |  | Pass
Juwi | JUE | Main Annual Inspection | O&M | PV Generator | 2.4.1 | Maintenance of sensors based on manufacturer’s instructions | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | L according manufacturer's instruction is confirmable |  |  |  |  | 1 |  | Open
Juwi | JUE | Bi-annual inspection | O&M | PV Generator | 2.3.1 | Random testing of the steadiness of the mounting foundation/system and random inspection regarding corrosion at substructure (min. 10%, documentation of location, during 10 years inspection of whole PV plant) | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing |  |  |  |  | 1 |  | Open
Juwi | JUE | Main Annual Inspection | O&M | PV Generator | 2.4.1 | Visual inspection of all accessible cable trenches and cable trays regarding damage | 1 |  | 1 | [8 empty] | 1 |  | Pass
Juwi | JUE | Main Annual Inspection | O&M | PV Generator | 2.4.1 | Visual inspection and random testing of string connector (min. 10% with Documentation of location , during 10 years testing of whole PV plant) | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | not completely described |  |  |  |  | 1 |  | Open
Juwi | JUE | Reaction to Fault Messages / Response Times | O&M | Specific Requirements | 2.11.1 | Every fault message has to be registered in the monitoring software. According to the fault message, the Bidder shall issue a fault diagnosis within a response time of 2 hours (24/7) | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing |  |  |  |  | 1 |  | Open
Juwi | JUE | Fault Management / Warranty defects | O&M | Specific Requirements | 2.12.5 | Operational defects, which are not considered as warranty defects - see repair works section below | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | Failure Response Time Model not not accepted |  |  |  |  | 1 |  | Open
Juwi | JUE | Fault Calls | O&M | Specific Requirements | 2.13.2 | The minimum response time in case of failure must meet the EPA requirements | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing |  |  |  |  | 1 |  | Open
Juwi | JUE | Spare Parts and Tools | O&M | Specific Requirements | 2.14 | provide the necessary set of spare parts and maintenance tools as required to perform the services | 1 |  | 1 | [8 empty] | 1 |  | Pass
Juwi | JUE | Fault Calls | O&M | Specific Requirements | 2.13.2 | --> Time Model: Response Times for Priorities 1-3 (12h / 24h / 1 week) | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | look at 2.12.5 |  |  |  |  | 1 |  | Open
Juwi | JUE | Working Time | O&M | Specific Requirements | 2.17 | All working times of Bidders personnel shall be included in the Bidders annual remuneration. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing |  |  |  |  | 1 |  | Open
Juwi | JUE | Remote Supervision | O&M | Specific Requirements | 2.10.2 | Any reductions in performance shall have to be logged. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing |  |  |  |  | 1 |  | Open
Juwi | JUE | Performance of maintenance and repair works | O&M | Specific Requirements | 2.8.1 | Corresponding regulations of the respective component manufacturer shall have to be followed during maintenance works | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing |  |  |  |  | 1 |  | Open
Juwi | JUE | Spare Parts and Tools | O&M | Specific Requirements | 2.14.1 | cover all cost for supply and re-stocking of spare parts from his annual remuneration. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing |  |  |  |  | 1 |  | Open
Juwi | JUE | Reduced Output of the Plant | O&M | Specific Requirements | 2.15.1 | Identified reduced output shall be justified. Reduced output shall be recovered and liquidated damages determined. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing liquidated --> means --> performance |  |  |  |  | 1 |  | Open
Juwi | JUE | Remote Supervision | O&M | Specific Requirements | 2.10.8 | Monthly / quarterly and annual reports based on the data of the remote supervision provided to the Employer 4 weeks after the last period of reporting at the latest. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing |  |  |  |  | 1 |  | Open
Juwi | JUE | Reduced Output of the Plant | O&M | Specific Requirements | 2.15 | Monthly comparison of the specific performance of all measuring channels among each other. 5% reduced output results in general check of all the channels and shall be documented. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing |  |  |  |  | 1 |  | Open
Juwi | JUE | Special inspection (every 4 years) | O&M | Specific Requirements | 2.5.1 | Oil check of transformers | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing |  |  |  |  | 1 |  | Open
Juwi | JUE | Remote Supervision | O&M | Specific Requirements | 2.10.1 | On-call service provided for the Employer for availability outside business hours and during weekends (24/7). | 1 |  |  |  | 1 | Unclear: We do not understand your proposal, please detail your proposal. Especially confirm that you are compliant with our requested criteria. | [5 empty] | 1 |  | Open
Juwi | JUE | On-site monitoring | O&M | Specific Requirements | 2.9.1 | Permanent (24/7) staffing of the Power Plant, consisting of security and O&M personnel. | 1 |  |  |  | 1 | Unclear: We do not understand your proposal, please detail your proposal. Especially confirm that you are compliant with our requested criteria. | [5 empty] | 1 |  | Open
Juwi | JUE | Fault Management / Warranty defects | O&M | Specific Requirements | 2.12.4 | Product warranties in favour of contractor / Bidder (responsible) to claim all warranties for at least 5 years | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing |  |  |  |  | 1 |  | Open
Juwi | JUE | Reaction to Fault Messages / Response Times | O&M | Specific Requirements | 2.11.2 | profit relevant Fault Events: Downtime registration/ reasons/ repair/ in monthly report (blanc of monthly report?) | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing |  |  |  |  | 1 |  | Open
Juwi | JUE | Special inspection (every 4 years) | O&M | Specific Requirements | 2.5.1 | Protection systems of medium voltage switching panels of the stations | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing |  |  |  |  | 1 |  | Open
Juwi | JUE | Repair time and cost | O&M | Specific Requirements | 2.16 | Repair times are considered as part of the availability guaranty of the Bidder. All cost of repair shall be part of the Bidders annual remuneration. For the avoidance of doubt that includes any repairs due to lightening, theft and vandalism. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing |  |  |  |  | 1 |  | Open
Juwi | JUE | Performance of maintenance and repair works | O&M | Specific Requirements | 2.8.2 | Report document for maintenance works (blanc sample requiered for bid) | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | Report document for maintenance works is missing |  |  |  |  | 1 |  | Open
Juwi | JUE | Remote Supervision | O&M | Specific Requirements | 2.10.7 | The Bidder shall provide to the Employer permanent online access to the power plant control system for parallel monitoring | 1 |  | 1 | [8 empty] | 1 |  | Pass
Juwi | JUE | Fault Calls | O&M | Specific Requirements | 2.13.1 | The scope of service shall include any working times for all fault calls including travelling times and costs. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing |  |  |  |  | 1 |  | Open
Juwi | JUE | Reporting | O&M | Specific Requirements | 2.23 | The Bidder shall deliver to the Employer regular reports on monthly, quarterly and annual basis. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing |  |  |  |  | 1 |  | Open
Juwi | JUE | Main Annual Inspection | O&M | Substation and Transmission Line | 2.4.4 | Maintenance of substation and transmission line according to manufacturer instruction | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing |  |  |  |  | 1 |  | Open
Juwi | JUE | Main Annual Inspection | O&M | Substation and Transmission Line | 2.4.4 | Visual inspection of transformer and switchboard rooms and cleaning if necessary | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing |  |  |  |  | 1 |  | Open
Juwi | JBS | Physical layout | Physical layout plan | Specific Requirements | 1.7.7 | Detailed top view of the PV mounting structure, including module sizes and spacing between the module rows | 1 | Page 274 | 1 | [8 empty] | 1 |  | Pass
Juwi | JBS | Physical layout | Physical layout plan | Specific Requirements | 1.7.7 | Detailed view of the distribution of inverters and connections to the PV string/array | 1 | Page 307 - 310 | 1 | [8 empty] | 1 |  | Pass
Juwi | JBS | Physical layout | Physical layout plan | Specific Requirements | 1.7.7 | Detailed side and front view of the PV mounting structure | 1 | Page 274 | 1 | [8 empty] | 1 |  | Pass
Juwi | JBS | Physical layout | Physical layout plan | Specific Requirements | 1.7.7 | Detailed top view of electrical cabling interconnections | 1 | Page 307 - 310 | 1 | [8 empty] | 1 |  | Pass
Juwi | JBS | Physical layout | Physical layout plan | Specific Requirements | 1.7.7 | Floor plans and elevations for all buildings, housing units, containers on site: e.g. , substations, the SCADA operational room, inverters, O&M, storage facilities | 1 | Page 37 | 1 | [8 empty] | 1 |  | Pass
Juwi | JBS | Physical layout | Physical layout plan | Specific Requirements | 1.7.7 | Location of the system metering and grid connection point | 1 | Page 307 - 310 | 1 | [8 empty] | 1 |  | Pass
Juwi | JBS | Power plant documentation | Power plant documentation | Quality Assurance | 1.27.1 | Flash report list of all modules shall be provided in digital form. | 1 |  |  |  | 1 |  |  |  |  | C |  | 1 |  | Open
Juwi | JBS | Power plant documentation | Power plant documentation | Quality Assurance | 1.27.1 | The Bidder shall confirm that the complete as-built documentation of the plant will be provided in compliance with IEC 62446. Additionally all module serial numbers shall be listed with their individual location. | 1 |  |  |  | 1 |  |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  | C |  | 1 |  | Open
Juwi | JBS | Workflow, Project Management Plan and Timelines | Project schedule / Project management | Project schedule | 1.8.1 | Interdependencies between the tasks | 1 |  | 1 | [8 empty] | 1 |  | Pass
Juwi | JBS | Workflow, Project Management Plan and Timelines | Project schedule / Project management | Project schedule | 1.8.1 | Interdependencies of tasks with equipment order and delivery times | 1 |  | 1 | [8 empty] | 1 |  | Pass
Juwi | JBS | Workflow, Project Management Plan and Timelines | Project schedule / Project management | Project schedule | 1.8.1 | Key milestones to indicate that the progress in on schedule | 1 |  | 1 |  |  | Unclear: We do not understand your proposal, please detail your proposal. Especially confirm that you are compliant with our requested criteria. | [5 empty] | 1 |  | Pass
Juwi | JBS | Workflow, Project Management Plan and Timelines | Project schedule / Project management | Project schedule | 1.8.1 | Provide installation schedule in compliance with sub-clause 8.2 of Particular Conditions (Time for Completion is 225 days after Commencement Date). | 1 | Page 487 |  | 1 |  | Provide installation schedule in compliance with sub-clause 8.2 of Particular Conditions (Time for Completion is 225 days after Commencement Date). | 341 Tage | Find sub-clause 8.2 of Particular Conditions |  |  |  | 1 |  | Fail
Juwi | JBS | Workflow, Project Management Plan and Timelines | Project schedule / Project management | Project schedule | 1.8.1 | Provide work breakdown structures, activity decomposition and sequencing and dependability with the baseline schedule clearly showing the critical path | 1 | Page 487 | 1 | [8 empty] | 1 |  | Pass
Juwi | JBS | Workflow, Project Management Plan and Timelines | Project schedule / Project management | Project schedule | 1.8.1 | Schedule of tasks | 1 |  | 1 | [8 empty] | 1 |  | Pass
Juwi | JBS | Workflow, Project Management Plan and Timelines | Project schedule / Project management | Project schedule | 1.8.1 | Teams, the number and skills of personnel to be deployed for each task | 1 |  | 1 | [8 empty] | 1 |  | Pass
Juwi | JBS | Workflow, Project Management Plan and Timelines | Project schedule / Project management | Quality Assurance | 1.8.3 | Inspection of equipment delivery | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  |  |  | C |  | 1 |  | Open
Juwi | JBS | Workflow, Project Management Plan and Timelines | Project schedule / Project management | Quality Assurance | 1.8.3 | Milestones for the completion of civil, mechanical, and electrical works | 1 |  |  |  | 1 | Unclear: We do not understand your proposal, please detail your proposal. Especially confirm that you are compliant with our requested criteria. |  |  | dobble to 105 and 111 | C |  | 1 |  | Open
Juwi | JBS | Workflow, Project Management Plan and Timelines | Project schedule / Project management | Quality Assurance | 1.8.3 | Quality control of delivered modules | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  |  |  | C |  | 1 |  | Open
Juwi | JBS | Workflow, Project Management Plan and Timelines | Project schedule / Project management | Quality Assurance | 1.8.3 | Risk analysis and mitigation plan | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  |  |  | C |  | 1 |  | Open
Juwi | JBS | Workflow, Project Management Plan and Timelines | Project schedule / Project management | Quality Assurance | 1.8.3 | System acceptance QA procedure by the Employer | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  |  |  | C |  | 1 |  | Open
Juwi | JBS | Miscellaneous | Project schedule / Project management | Specific Requirements | 1.29.9 | The Bidder shall submit an organizational chart illustrating management and functional relationships among all project team members including consultants, sub-contractors and vendors at each significant stage of the work, such as permitting, design, construction, testing and commissioning and O&M. | 1 | Page 406 | 1 | [8 empty] | 1 |  | Pass
Juwi | RM | Supervisory Control and Data Acquisition (SCADA) | SCADA | Specific Requirements | 1.9.2 | Alarms/alerts and timely notification of key performance indicators | 1 |  | 1 | [8 empty] | 1 |  | Pass
Juwi | RM | Supervisory Control and Data Acquisition (SCADA) | SCADA | Specific Requirements | 1.9.2 | All communication/data cables outside of buildings must be fiber-optic cables | 1 |  | 1 |  |  | general option. Please confirm delivery | [5 empty] | 1 |  | Pass
Juwi | RM | Supervisory Control and Data Acquisition (SCADA) | SCADA | Specific Requirements | 1.9.2 | Back-up power for a minimum of twelve hours | 1 |  | 1 |  |  |  | 40h |  |  |  |  | 1 |  | Pass
Juwi | RM | Supervisory Control and Data Acquisition (SCADA) | SCADA | Specific Requirements | 1.9.2 | Control room to remotely monitor and manage the whole system, on a 24 x 7 basis, with the capability of Web-based information sharing | 1 |  |  |  | 1 | please describe | [5 empty] | 1 |  | Open
Juwi | RM | Supervisory Control and Data Acquisition (SCADA) | SCADA | Specific Requirements | 1.9.2 | Data must be readily available for the fulfilment of all warranties and performance guarantees | 1 |  | 1 |  |  | Please confirm seperately | by description of data management this is most likely possible | Cannot be evaluated at this stage. | statement |  |  | 1 |  | Pass
Juwi | RM | Supervisory Control and Data Acquisition (SCADA) | SCADA | Specific Requirements | 1.9.2 | Data logging at intervals of not less than one minute, processing, transmission, and back-up | 1 |  | 1 |  |  | Correct meaning was: maximum interval length of 1 minute. Please confirm. |  |  | not more (!) |  |  | 1 |  | Pass
Juwi | RM | Supervisory Control and Data Acquisition (SCADA) | SCADA | Specific Requirements | 1.9.2 | Data shall be provided via FTP (Push/Pull) to the Employer | 1 | p385 | 1 |  |  | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | [5 empty] | 1 |  | Pass
Juwi | RM | Supervisory Control and Data Acquisition (SCADA) | SCADA | Specific Requirements | 1.9.1 | Remote access to all operational data for independent monitoring purposes shall be possible (NTDC requirements) | 1 |  | 1 |  |  |  | RS485 and CAN Bus fibre optics Web interface |  |  |  |  | 1 |  | Pass
Juwi | RM | Supervisory Control and Data Acquisition (SCADA) | SCADA | Specific Requirements | 1.9.1 | Safe and redundant archive for operational data. | 1 | Annex 11 | 1 |  |  |  | 1.14 page 25 ff >> Annex 11 on site data logging Analyse, compare, grafics, reports, fault management, overview, web interface, plant map, |  |  |  |  | 1 |  | Pass
Juwi | RM | Supervisory Control and Data Acquisition (SCADA) | SCADA | Specific Requirements | 1.9.2 | Separate inverter, zone, and string level (current and voltage) monitoring | 1 | p384 | 1 | [8 empty] | 1 |  | Pass
Juwi | RM | Supervisory Control and Data Acquisition (SCADA) | SCADA | Specific Requirements | 1.9.1 | The system has to provide different access-levels with different access rights allocated. | 1 |  |  |  | 1 | please confirm and describe "read only", "write" | [5 empty] | 1 |  | Open
Juwi | RM | Earthworks | Site Preparation and site access | Design factors to be provided | 1.12 | All earth works required have to be specified and included in the offer | 1 |  |  |  | 1 | Location: Only nice pictures. We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | [5 empty] | 1 |  | Open
Juwi | RM | Earthworks | Site Preparation and site access | Specific Requirements | 1.12, 1.13.4, 1.7.7 | Cross-sections of foundations for stations shall be provided, including explanation of the foundations laying down, height, penetration, and method of installing foundation posts, mounting fixtures | 1 |  | 1 | [8 empty] | 1 |  | Pass
Juwi | RM | Earthworks | Site Preparation and site access | Specific Requirements | 1.12 | Position and specification of underground cable connections must be documented during installation | 1 |  | 1 |  |  |  |  | Cannot be avaluated at this stage. |  |  |  | 1 |  | Pass
Juwi | RM | Site Preparation and site access | Site Preparation and site access | Specific Requirements | 1.11.1 | The Bidder shall provide foundations and structures in accordance with the actual soil conditions. | 1 | p18 / 1.8 | 1 |  |  | tilt 10° - pleas explain with PVSyst analyse with 20° | additionial geo survey and pull-out test Screw piles tilt 10° (!!) |  | refer to Soil study |  |  | 1 |  | Pass
Juwi | RM | Earthworks | Site Preparation and site access | Specific Requirements | 1.12 | After completion of construction and all earthworks ground shall be levelled and stabilized. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  | (maintanance, dust) |  |  | 1 |  | Open
Juwi | RM | Earthworks | Site Preparation and site access | Specific Requirements | 1.12 | Within the plant boundary limits, access roads to all stations shall be suitable for heavy load trucks (axle load: min. 12 tonn). | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | [5 empty] | 1 |  | Open
Juwi | JBS | Power plant documentation | Spare parts | Warranty | 1.27.2 | The successful bidder shall provide all warranty spares for a warranty period of 5 years. | 1 |  |  |  | 1 |  |  |  |  | C |  | 1 |  | Open
Juwi | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Design factors to be provided | 1.21.2 | 3-phase, double wound, continuously rated, oil-cooled, enclosed transformers, use of low loss core steel and close coupled copper windings | 1 |  | 1 | [8 empty] | 1 |  | Pass
Juwi | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Design factors to be provided | 1.21.2 | Cooling method | 1 |  | 1 | [8 empty] | 1 |  | Pass
Juwi | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Design factors to be provided | 1.21.2 | Efficiency | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | only total eff. Inv+transformer, page 287 |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Juwi | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Design factors to be provided | 1.21.2 | Humidity tolerance | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Juwi | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Design factors to be provided | 1.21.2 | Incoming terminals | 1 |  | 1 | [8 empty] | 1 |  | Pass
Juwi | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Design factors to be provided | 1.21.2 | Insulation type | 1 |  | 1 | [8 empty] | 1 |  | Pass
Juwi | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Design factors to be provided | 1.21.2 | kVA rating | 1 |  | 1 | [8 empty] | 1 |  | Pass
Juwi | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Design factors to be provided | 1.21.2 | Maximum ambient temperature and altitude | 1 |  | 1 | [8 empty] | 1 |  | Pass
Juwi | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Design factors to be provided | 1.21.2 | No-load losses | 1 |  | 1 | [8 empty] | 1 |  | Pass
Juwi | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Design factors to be provided | 1.21.2 | Operating temperature range | 1 |  | 1 | [8 empty] | 1 |  | Pass
Juwi | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Design factors to be provided | 1.21.2 | Operational data shall be logged in central operating system (e.g. oil temperature, oil level, pressure, Temperature probes (one per phase): Alarm and trip of cell etc.) | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  |  |  | C |  | 1 |  | Open
Juwi | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Design factors to be provided | 1.21.2 | Outgoing terminals | 1 |  | 1 | [8 empty] | 1 |  | Pass
Juwi | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Design factors to be provided | 1.21.2 | Primary side voltage | 1 |  | 1 | [8 empty] | 1 |  | Pass
Juwi | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Design factors to be provided | 1.21.2 | Protection system | 1 |  | 1 | [8 empty] | 1 |  | Pass
Juwi | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Design factors to be provided | 1.21.2 | Secondary side voltage | 1 |  | 1 | [8 empty] | 1 |  | Pass
Juwi | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Design factors to be provided | 1.21.2 | Short-circuit impedance | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Juwi | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Standards | 1.21.3 | IEC 60076 | 1 |  | 1 |  |  |  |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  |  |  | 1 |  | Pass
Juwi | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Standards | 1.21.3 | IEC 60085 | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  | C |  | 1 |  | Open
Juwi | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Standards | 1.21.3 | IEC 60137 | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  | C |  | 1 |  | Open
Juwi | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Standards | 1.21.3 | IEC 60214 | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  | C |  | 1 |  | Open
Juwi | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Standards | 1.21.3 | IEC 62446 | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Juwi | JBU | Step-up Transformers/MV Switchgear | Step-up Transformers/MV Switchgear | Guarantees | 1.21.1 | Compatibility with NTDC grid connection code must be ensured | 1 |  |  |  | 1 |  | L |  |  |  |  | 1 |  | Open
Juwi | GD | PR and System Performance Guarantee | System PR | Guarantees | 1.4.1 | A 25 years commitment, in the form of a whole System performance guarantee, is required. The performance guarantee is based on measuring the PR with the actual kWh-AC delivery per year adjusted for the actual POA irradiation for the same period | 1 |  |  | 1 |  | Unclear: We do not understand your proposal, please detail your proposal. Especially confirm that you are compliant with our requested criteria. |  | Only to be checked in list of deviations. |  |  |  | 1 | 1 | Fail
Juwi | JBS | System PR Specification | System PR | Losses included in PR calculation | 1.5.4 | Auxiliary loads | 1 | Page 392-395 |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | Nicht berücksichtigt | We don’t understand the question. Kindly clarify. | see relevant chapter 1.5.4 List of "losses" = auxilary loads from PV Energy that make the PR | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Juwi | JBS | System PR Specification | System PR | Losses included in PR calculation | 1.5.4 | Inverter (operating efficiency, operating voltage variations, power/voltage levels) | 1 | Page 392-395 | 1 |  |  |  |  | We don’t understand the question. Kindly clarify. | see relevant chapter 1.5.4 List of technical losses that make the PR |  |  | 1 |  | Pass
Juwi | JBS | System PR Specification | System PR | Losses included in PR calculation | 1.5.4 | Module Array (temperature dependence, soiling, low light inefficiency, shading, mismatches in array) | 1 | Page 392-395 | 1 |  |  |  |  | We don’t understand the question. Kindly clarify. | we want to see these losses specified. Thos need to be aligned with O+M Startegy and System composition |  |  | 1 |  | Pass
Juwi | JBS | System PR Specification | System PR | Losses included in PR calculation | 1.5.4 | Ohmic losses in cables | 1 | Page 392-395 | 1 |  |  |  |  | We don’t understand the question. Kindly clarify. | see relevant chapter 1.5.4 List of technical losses that make the PR |  |  | 1 |  | Pass
Juwi | JBS | System PR Specification | System PR | Losses included in PR calculation | 1.5.4 | Transformer losses | 1 | Page 392-395 | 1 |  |  |  |  | We don’t understand the question. Kindly clarify. | see relevant chapter 1.5.4 List of technical losses that make the PR |  |  | 1 |  | Pass
Juwi | JBS | System PR Specification | System PR | O&M | 1.5.2 | The target PR specification at the time of commissioning the System is equal to or greater than 0.75 (75%). | 1 | Page 392-395 | 1 |  |  |  | 74.8% |  |  |  |  | 1 |  | Pass
Juwi | JBS | Physical layout | System PR | Specific Requirements | 1.7.1 | Provide a report using Solar GIS data provided by the Employer | 1 | Page 41 | 1 |  |  |  |  | Replace 'Report' with ' PV-Syst report'. | 'Report' is original wording in ER in 1.7.1 |  |  | 1 |  | Pass
Juwi | JBS | Physical layout | System PR | Specific Requirements | 1.7.1, 1.1.8 | Layout calculations of predicted kWh over the system lifetime and PR using the tool PVSyst V5.62 or higher | 1 | Page 392-395 | 1 | [8 empty] | 1 |  | Pass
Juwi | GD | PR and System Performance Guarantee | System PR | System PR | 1.4.2 | Guaranteed PR values in the form of the Table in 1.4.1 for the acceptance phase and annual output of the PV system shall be specified. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Link to table in Documents sheet |  |  |  | 1 | 1 | Open
Juwi | GD | PR and System Performance Guarantee | System PR | System PR | 1.4.1 | The billing system/metering system will be installed at interconnection point of 132 kV bus bar of HV substation to be installed by the EPC Contractor and the 132 kV Transmission line of NTDC existing at site. | 2 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  | Only to be checked in list of deviations. |  |  |  | 1 |  | Open
Juwi | GD | PR and System Performance Guarantee | System PR | System PR | 1.4.4 | The initial PR will be first measured after the time of commissioning of the completed PV System during the acceptance phase of 30 days. | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  | Cannot be evaluated at this stage. Only to be checked in list of deviations. |  |  |  | 1 | 1 | Open
Juwi | JBS | Equipment guarantees | Warranty | Guarantees | 1.28.4, 1.6 | A detailed list of all guarantee conditions for the main equipments (beside modules and inverters) shall be provided by the Successful Bidder with the technical offer. The product warranty shall be at least 5 years. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Juwi | JBS | Equipment guarantees | Warranty | Guarantees | 1.28 | The overall Guarantee and Power Plant Acceptance Procedures required for the Project are described in Sections 1.3, 1.4, 1.14, 1.18 and Schedule D and shall be met. | 1 |  |  |  | 1 |  |  | Link |  | C |  | 1 |  | Open
Juwi | JBS | Basic Scope of Supply | Warranty | Quality Assurance | 1.6 | The Product Warranties shall be given for a duration of at least 5 years | 1 |  |  |  | 1 |  | Nicht für alle gefunden | Cannot be evaluated at this stage. Only to be checked in list of deviations. |  | C |  | 1 |  | Open
Juwi | MAW | Inverters | Warranty | Warranty option | 1.18.1 | The Bidder shall arrange a full-service package for the selected inverters for a product warranty period of 5 years, with an option to cover additional 20 years including provisions for any necessary replacements including O&M service plan guaranteeing 99% availability. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Sumec | JBU | AC Cabling | AC Cabling | Design factors to be provided | 1.19.1 | AC cable shall be of Copper. Rated voltage, nominal voltage between phase and neutral and nominal voltage between phases to be specified by the Bidder | 1 |  | 1 | [8 empty] | 1 |  | Pass
Sumec | JBU | AC Cabling | AC Cabling | Design factors to be provided | 1.19.1 | Appropriate sizing to minimise voltage drop and losses | 1 |  | 1 |  |  |  |  | What is the appropriate size? | leeway to allow MPP tracking when module voltage drops. At least 10%. Ralf, ist Vital kriterium. |  |  | 1 |  | Pass
Sumec | JBU | AC Cabling | AC Cabling | Design factors to be provided | 1.19.1 | Bending radius | 1 |  |  |  | 1 |  | L |  |  |  |  | 1 |  | Open
Sumec | JBU | AC Cabling | AC Cabling | Design factors to be provided | 1.19.1 | Cable installation shall ensure grounding and short-circuit protection | 1 |  |  |  | 1 |  | L |  |  |  |  | 1 |  | Open
Sumec | JBU | AC Cabling | AC Cabling | Design factors to be provided | 1.19.1 | Cables shall be suitable for the environmental conditions at the project site, including UV protection (The Bidder shall provide certification from manufacturer) | 1 |  |  |  | 1 |  | L |  |  |  |  | 1 |  | Open
Sumec | JBU | AC Cabling | AC Cabling | Design factors to be provided | 1.19.1 | Installation to be verified by measurement-protocols | 1 |  |  |  | 1 |  | L |  |  |  |  | 1 |  | Open
Sumec | JBU | AC Cabling | AC Cabling | Design factors to be provided | 1.19.1 | Lifetime longer than 25 years | 1 |  |  |  | 1 |  | L |  |  |  |  | 1 |  | Open
Sumec | JBU | AC Cabling | AC Cabling | Design factors to be provided | 1.19.1 | Rated voltage | 1 |  |  |  | 1 |  | L |  |  |  |  | 1 |  | Open
Sumec | JBU | AC Cabling | AC Cabling | Design factors to be provided | 1.19.1 | Sufficient and effective cable protection against attacks of rodents for any cabling underground or above is required | 1 |  |  |  | 1 |  | L |  |  |  |  | 1 |  | Open
Sumec | JBU | AC Cabling | AC Cabling | Specific Requirements | 1.19.3 | The runs of both the main DC and AC cables, in the System layout, should be adjusted to keep power losses below <1% at STC (Design calculations through cable loss simulation to be provided for review & comment). | 1 |  |  |  | 1 |  | L | Part of system design | Kategorie ? |  |  | 1 |  | Open
Sumec | JBU | AC Cabling | AC Cabling | Standards | 1.19.2 | DIN-VDE-0276 | 1 |  |  |  | 1 |  | L | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  |  |  | 1 |  | Open
Sumec | JBU | AC Cabling | AC Cabling | Standards | 1.19.2 | EN 60332-1-1 and EN 60332-2-1 | 1 |  |  |  | 1 |  | L | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  |  |  | 1 |  | Open
Sumec | JBU | AC Cabling | AC Cabling | Standards | 1.19.2 | IEC 60364 | 1 |  |  |  | 1 |  | L | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  |  |  | 1 |  | Open
Sumec | JBU | AC Cabling | AC Cabling | Standards | 1.19.2 | IEC 60502 | 1 |  |  |  | 1 |  | L | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  |  |  | 1 |  | Open
Sumec | JBU | AC Combiner Box | AC Combiner Box | Design factors to be provided | 1.20.1 | Class 2 AC surge arrestor | 1 |  | 1 |  |  |  | not applicable |  |  |  |  | 1 |  | Pass
Sumec | JBU | AC Combiner Box | AC Combiner Box | Design factors to be provided | 1.20.1 | Flame test | 1 |  | 1 |  |  |  | not applicable |  |  |  |  | 1 |  | Pass
Sumec | JBU | AC Combiner Box | AC Combiner Box | Design factors to be provided | 1.20.1 | Load breaker switch of adequate size | 1 |  | 1 |  |  |  | not applicable |  |  |  |  | 1 |  | Pass
Sumec | JBU | AC Combiner Box | AC Combiner Box | Design factors to be provided | 1.20.1 | Operating temperature range | 1 |  | 1 |  |  |  | not applicable |  |  |  |  | 1 |  | Pass
Sumec | JBU | AC Combiner Box | AC Combiner Box | Design factors to be provided | 1.20.1 | Rated current | 1 |  | 1 |  |  |  | not applicable |  |  |  |  | 1 |  | Pass
Sumec | JBU | AC Combiner Box | AC Combiner Box | Design factors to be provided | 1.20.1 | Rated voltage | 1 |  | 1 |  |  |  | not applicable |  |  |  |  | 1 |  | Pass
Sumec | JBU | AC Combiner Box | AC Combiner Box | Design factors to be provided | 1.20.1 | Stripping length of the individual wire | 1 |  | 1 |  |  |  | not applicable |  |  |  |  | 1 |  | Pass
Sumec | JBU | AC Combiner Box | AC Combiner Box | Design factors to be provided | 1.20.1 | Waterproof test | 1 |  | 1 |  |  |  | not applicable |  |  |  |  | 1 |  | Pass
Sumec | JBU | AC Combiner Box | AC Combiner Box | Standards | 1.20.2 | EN 60529, DIN-VDE-0472 | 1 |  | 1 |  |  |  | not applicable | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  |  |  | 1 |  | Pass
Sumec | JBU | AC Combiner Box | AC Combiner Box | Standards | 1.20.2 | IP 67 | 1 |  | 1 |  |  |  | not applicable |  |  |  |  | 1 |  | Pass
Sumec | JBS | Physical layout | Auxiliary equipment | Specific Requirements | 1.7.8 | All parts of the installation are covered by two high speed protection schemes, which shall be independent to avoid common mode failures | 1 | Vol 3page 9 | 1 | [8 empty] | 1 |  | Pass
Sumec | JBS | Physical layout | Auxiliary equipment | Specific Requirements | 1.7.8 | The outline of protection schemes shall be shown on the single line diagram (SLD) | 1 |  | 1 | [8 empty] | 1 |  | Pass
Sumec | JBS | Physical layout | Auxiliary equipment | Specific Requirements | 1.7.8 | Provide complete indicating, regulating, controlling, protecting and interlocking equipment necessary for safe and efficient operation of the plant and substation, including complete protection scheme. | 1 | Vol 3page 9 | 1 | [8 empty] | 1 |  | Pass
Sumec | JBS | Physical layout | Auxiliary equipment | Specific Requirements | 1.7.9 | The scope of the documentation shall cover at least the requirements of IEC 62446. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Sumec | JBS | Physical layout | Auxiliary equipment | Specific Requirements | 1.7.8 | The Bidder shall include a fire prevention and response plan | 1 | Vol 1 page 161 ff; Vol 2 page 320 ff | 1 | [8 empty] | 1 |  | Pass
Sumec | JBS | Physical layout | Auxiliary equipment | Specific Requirements | 1.7.9 | The documentation includes clearly labelled objects and figures annotated in English language. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Sumec | JBS | Physical layout | Auxiliary equipment | Specific Requirements | 1.7.8 | The fire prevention and response plan shall include a fire alarm und detection system with a main panel in the control room | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Sumec | RM | Other infrastructure | Auxiliary systems | DC Backup System / uninterrupted power supply (UPS) | 1.25.6 | IEC-60051 and IEC-60439 standards apply | 1 | Vol-I, p40 |  |  | 1 | Please confirm requiered international standards | All listed standards arer China | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  |  |  | 1 |  | Open
Sumec | RM | Other infrastructure | Auxiliary systems | Design factors to be provided | 1.25.1 | One administration and office building with car port for 10 vehicles shall be provided, with sufficient space for operating personal, control room, security office, regular office rooms for permanent and visiting staff, meeting room, kitchen sanitary systems (toilet, showers separate for male and female), first aid, control room, electrical rooms, etc. The building shall have windows for office rooms and air conditioning system (split units) for all office rooms. | 1 | Vol-III, F2 F12, F13 | 1 |  |  | not applicable |  | Priority to be discussed |  |  |  | 1 |  | Pass
Sumec | RM | Other infrastructure | Auxiliary systems | Design factors to be provided | 1.25.1 | Service water system sufficiently sized for cleaning cycle of modules | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Sumec | RM | Other infrastructure | Auxiliary systems | Design factors to be provided | 1.25.1 | Sewage system including sewage disposal for Construction and O&M phase | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Sumec | RM | Other infrastructure | Auxiliary systems | Design factors to be provided | 1.25.1 | Warehouse for spare parts and workshop for minor mechanical/electrical works. | 1 | Vol-III, F12-13 | 1 |  |  |  | Standard rooms in office buildings |  |  |  |  | 1 |  | Pass
Sumec | RM | Other infrastructure | Auxiliary systems | Design factors to be provided | 1.25.1 | Water storage facility for drinking water, sanitary water (sufficient for 1 week) | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Sumec | RM | Other infrastructure | Auxiliary systems | Guarantees | 1.25.4 | All buildings should be designed in accordance with the requirements of the Pakistan Building Code (available at www.pec.org.pk/buildingcode.aspx) and latest Seismic Provisions 2007. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Link to code |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Sumec | JBS | Miscellaneous | Auxiliary systems | Power supply | 1.29.1 | An off-grid power station may need to be provided by the Bidder for commencing the work. Diesel generators shall be arranged by the bidder on its own. | 1 | Vol 1 Page 37 | 1 | [8 empty] | 1 |  | Pass
Sumec | RM | Other infrastructure | Auxiliary systems | Security Surveillance System | 1.25.5 | The Bidder shall provide security personnel for 24 h / 7 days a week for the whole year | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Sumec | RM | Other infrastructure | Auxiliary systems | Security Surveillance System | 1.25.5 | The system shall comply with insurance requirements | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Sumec | RM | Meteorological Sensors | Auxiliary Systems | Specific Requirements | 1.10.1 | Irradiation and temperature measurements are to be recorded at intervals of 15 min or less. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Sumec | RM | Meteorological Sensors | Auxiliary Systems | Specific Requirements | 1.10.2 | Seven pyranometers shall be placed : three for measuring the horizontal plane irradiation and the others for the in-plane irradiation. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | As in 1.10.2, it is seven pyranometer per system, please clarify the word "per system" | 1.1.1: "100 MWp (DC capacity at Standard Testing Conditions, abbreviated STC … hereinafter called 'the System') " | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Sumec | RM | Meteorological Sensors | Auxiliary Systems | Specific Requirements | 1.10.2 | The irradiation measurement equipment should be calibrated by an independent certified third party at least every two years. The calibration must be traceable to international standards. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Should be checked in list of deviations |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Sumec | RM | Meteorological Sensors | Auxiliary Systems | Specific Requirements | 1.10.3 | Ambient air and the module temperature shall be measured at every 5 installed MWp in conformity with IEC 60751 AA | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Sumec | RM | Meteorological Sensors | Auxiliary Systems | Specific Requirements | 1.10.1 | The equipment should have the capability of recording and storing data for 24 hours using auxiliary DC power. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Should be priority 1 question |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Sumec | RM | Meteorological Sensors | Auxiliary Systems | Specific Requirements | 1.10.2 | The pyranometers should conform to the standards of ISO 9060 (SR5: secondary standard) or the WMO classification, and IEC 60904. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Do we need to know some parameter values according to standards mentioned or just a statement of comlience with the standard would be sufficient? | compliance will be necessary, no data due diligence right now. | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Sumec | GD | PR and System Performance Guarantee | Compensations | O&M | 1.4.6 | If the successful Bidder defaults in being able to provide the O&M services required for the Systems performance guarantee, then it will be liable to cover all costs – but at least in the amount of Liquidated Damages imposed to the Employer by its PPA agreements - incurred by the Employer, including the loss of the guaranteed electricity export to the grid (but at a minimum rate of USD 0.20-per-kWh) for the disrupted period, in finding and hiring a replacement for the purpose. | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  | Cannot be evaluated at this stage. Only to be checked in list of deviations. |  |  |  | 1 | 1 | Open
Sumec | GD | PR and System Performance Guarantee | Compensations | O&M | 1.4.5 | For timely compensation the PR Calculation will be carried out provisionally for each quarter whereby the contractor and employer might jointly agree on different PR values for each quarter. In the last quarter of each calendar year the annual PR compensation of the full year will be carried out and any provisions will be offset by the annual compensation. | 3 |  |  |  | 1 |  |  | Cannot be evaluated at this stage. Only to be checked in list of deviations. |  |  |  | 1 |  | Open
Sumec | GD | PR and System Performance Guarantee | Compensations | O&M | 1.4.5 | If the annual measured PR falls below the guaranteed PR value according to Table 1.4.1, the liquidated damages will be levied on the successful Bidder at the rate of USD 0.20-per-kWh or the kWh Value the Employer receives for each kWh of shortfall – whichever is higher. Adjustments shall be made for any events outside the control of the O&M operator as grid outages, from grid operator ordered shutdowns, or force majeure events during the year. | 2 |  |  |  | 1 |  |  | Cannot be evaluated at this stage. Only to be checked in list of deviations. | Only to be checked in list of deviations. |  |  | 1 |  | Open
Sumec | GD | PR and System Performance Guarantee | Compensations | O&M | 1.4.5 | In case the PR is higher than the guaranteed PR value, the net value of this excess energy will be shared as follows: 50% towards the asset replacement fund, 25% towards the Employer, 25% towards the O&M contractor | 3 |  |  |  | 1 |  |  | Cannot be evaluated at this stage. Only to be checked in list of deviations. |  |  |  | 1 |  | Open
Sumec | GD | PR and System Performance Guarantee | Compensations | System PR | 1.4.4 | If the measured PR within further 30 days does not reach the guaranteed PR, the Employer can demand that the price of the system will be reduced by the percentage of shortfall times 1.2 for liquidated damages or the contractor will have to install more power at its own cost or combination of both. | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  | Cannot be evaluated at this stage. Only to be checked in list of deviations. |  |  |  | 1 | 1 | Open
Sumec | GD | PR and System Performance Guarantee | Compensations | System PR | 1.4.4 | The successful Bidder shall conduct the initial PR test for the daylight hours of at least 30 consecutive days, recording data at a frequency of fifteen minute intervals or less, to validate the guaranteed PR value for acceptance. Any excused downtime (e.g., from Grid Operator ordered shutdowns, grid failure, theft, force majeure) will be excluded from that calculation by an independent consultant (Auditing Body). That day will be taken out and another day added, if the initial PR falls short of the guaranteed PR value, the successful Bidder shall be obliged to identify and rectify the causes for the performance shortfall at their own cost. | 2 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  | Cannot be evaluated at this stage. Only to be checked in list of deviations. |  |  |  | 1 |  | Open
Sumec | GD | Conditions for Disqualification and Additional Information Required | Credentials | EPC | 1.2.6 | Approval from bidder to owners or owner representatives to answer questions freely regarding the past performance of the bidder and performance of the system against contractual obligations. | 2 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | [5 empty] | 1 |  | Open
Sumec | GD | Conditions for Disqualification and Additional Information Required | Credentials | EPC | 1.2.6 | Cumulative MWp of ground mounted PV turnkey installations >5 MWp with stating of actual MWp per project, project location, date of commissioning, module type and Inverter type. | 1 |  | 1 | [5 empty] | experience of Bidder / EPC |  |  | 1 | 1 | Pass
Sumec | GD | Conditions for Disqualification and Additional Information Required | Credentials | EPC | 1.2.6 | Detailed list of all the sites with the affirmation that the bidder played the leading EPC role in the turnkey installation of these systems. | 3 |  | 1 | [8 empty] | 1 |  | Pass
Sumec | GD | Conditions for Disqualification and Additional Information Required | Credentials | EPC | 1.2.6 | References and contact data (mail and phone) from owners of all installations > 5 MW with quotes of the corresponding system Performance Ratios, as well as system performance vs. initial yield assessment per year since the installation. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  | for selection of referenz objects |  |  | 1 | 1 | Open
Sumec | GD | Technical Bid Evaluation Criteria | Credentials | EPC | 1.3.1 | the systems have been completed on time and within budget, | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | [5 empty] | 1 | 1 | Open
Sumec | GD | Scope of the Bid | Credentials | EPC | 1.1.9 | The bid includes professional experience of the Bidders in ground mounted utility-scale PV and financial information about their long-term stability | 3 |  | 1 | [8 empty] | 1 |  | Pass
Sumec | GD | Scope of the Bid | Credentials | EPC | 1.1.10 | The Bidder, or the Lead company in case of JV is a EPC contractor | 1 |  | 1 |  |  |  |  | This is a non-technical question. We suggest such question should be separated from technical questions and placed in checklist for "General/Substantive Responsiveness of Bid" | a question of reliability and experience of solid understanding of the task/System Technology. See also 1.1.10 |  |  | 1 |  | Pass
Sumec | GD | Technical Bid Evaluation Criteria | Credentials | Guarantees | 1.3.1 | To have met the contractual requirements of the EPC and O&M deliverables including certificate to the effect that the entire equipment is brand new as required vide notification number NEPRA/UTS-01/777-779 dated Jan 21 ,2014, | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Only to be checked in list of deviations. |  |  |  | 1 | 1 | Open
Sumec | GD | Technical Bid Evaluation Criteria | Credentials | O&M | 1.3.1 | In case of a non-performance, comprehensible evidence has to be given why this case will not affect this project. | 3 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | [5 empty] | 1 |  | Open
Sumec | GD | Technical Bid Evaluation Criteria | Credentials | O&M | 1.3.1 | that they have started supplying electricity to the grid and are still operating satisfactorily in 9 out of 10 MW for all the cases | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | [5 empty] | 1 | 1 | Open
Sumec | GD | Conditions for Disqualification and Additional Information Required | Credentials | O&M | 1.2.6 | Cumulative MWp of ground mounted PV installations for which O&M services have been delivered by the bidder or his O&M subcontractor. | 2 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | [5 empty] | 1 |  | Open
Sumec | GD | Technical Bid Evaluation Criteria | Credentials | O&M | 1.3.2 | Prove at least 100 MW of EPC experience and 50 MW of full O&M experience for a period longer than 24 months. | 1 |  | 1 | [8 empty] | 1 |  | Pass
Sumec | GD | Conditions for Disqualification and Additional Information Required | Credentials | O&M | 1.2.6 | References, contact data and approval from owners or owner representatives of all installations > 5 MW from bidder or his O&M subcontractor to answer questions freely regarding the past performance of the bidder and performance of the system against contractual obligations. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | [5 empty] | 1 | 1 | Open
Sumec | MAW | Modules | Credentials | Project references | 1.14.8 | To show the proven technology a minimum of 500MW of proposed product type series must be in operation and reference projects shall be named. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Related to project references |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Sumec | MAW | Inverters | Credentials | Project references | 1.18.10 | A minimum of 100 MWp of similar product/type must be in operation and reference projects shall be named. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Sumec | MAW | DC Cables | DC Cables | Design factors to be provided | 1.15.2 | String cable shall be of the following type: single conductor type, copper, 1000 V / Class II (according to protection class II / 1000V, IEC 61140, single core cable, tinned copper conductor, XLPE Insulation, double EVA jacket (resistant to heat and cold, resistant to ozone, UV, oil and chemicals), Temperature: 90 º C (Temperature Max. Allowable: 120 º C), Halogen free | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | It should be in accordance with the inverter values. | possibly 1500V for such system design | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Sumec | MAW | DC Cables | DC Cables | Design factors to be provided | 1.15.2 | Balance of electrical potential | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Need to be disscussed | equipotential bonding earthing mesh | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Sumec | MAW | DC Cables | DC Cables | Design factors to be provided | 1.15.2 | Clear and systematic labelling required | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Sumec | MAW | DC Cables | DC Cables | Design factors to be provided | 1.15.2 | Connectors of Modules and string cables shall be connected of self-locking type, have IP65 rating and shall be from same manufacturer and type | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Sumec | MAW | DC Cables | DC Cables | Design factors to be provided | 1.15.2 | Installation to be verified by measurement-protocols | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Cannot be evaluated at this stage. | blanc protocol | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Sumec | MAW | DC Cables | DC Cables | Design factors to be provided | 1.15.2 | Lifetime of 30 years is assured | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | What proof is required. | Life time test of nonmetal materials IEC 60811-408:2012 / (DIN EN 60811-408; VDE 0473-811-408:2012-12) 30 y assurance never seen until today | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Sumec | MAW | DC Cables | DC Cables | Design factors to be provided | 1.15.2 | Sizing of cables shall be specified according to the number of modules and strings per array | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  | voltage drop calculation | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Sumec | MAW | DC Cables | DC Cables | Design factors to be provided | 1.15.2 | The DC main (downstream of combiner box) wiring harness shall have the quality: Aluminum / Copper / 1000 V / Class II | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | It should be in accordance with the inverter values. | possibly 1500V for such system design | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Sumec | MAW | DC Cables | DC Cables | Specific Requirements | 1.15.1 | Are Ohmic losses less than 1% at full power? | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | DC: 1.4%, AC: no considered |  | DC+AC losses < 2% | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Sumec | MAW | DC Cables | DC Cables | Standards | 1.15.3 | IEC 60364-1 | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Sumec | MAW | DC Connectors | DC Connectors | Standards | 1.16.2 | EN 50521 | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? | PV Connectors no, just a statement of compliance | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Sumec | MAW | DC Connectors | DC Connectors | Standards | 1.16.2 | IEC 60512 | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? | Connectors E-Systems no, just a statement of compliance | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Sumec | MAW | DC Junction Box | DC Junction Box | Design factors to be provided | 1.17.1 | At least IP54 | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | DC Junction box is applicable in what conditions? | depending on DC Design | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Sumec | MAW | DC Junction Box | DC Junction Box | Design factors to be provided | 1.17.1 | Class 2 DC surge arrestor | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Sumec | MAW | DC Junction Box | DC Junction Box | Design factors to be provided | 1.17.1 | DC fuses shall permit up to maximum 1000 V (or 1500V if designed). String box design, including all operating elements shall satisfy safety requirements | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Will inverter voltage(1500V) effect the maximum voltage(1000V)? | depends on spec of inverter. | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Sumec | MAW | DC Junction Box | DC Junction Box | Design factors to be provided | 1.17.1 | Dust and heat protection | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Sumec | MAW | DC Junction Box | DC Junction Box | Design factors to be provided | 1.17.1 | Monitored input-couples | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Sumec | MAW | DC Junction Box | DC Junction Box | Specifications | 1.17.2 | Current monitoring | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Sumec | MAW | DC Junction Box | DC Junction Box | Specifications | 1.17.2, 1.17.1 | Monitoring interface for SCADA | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Sumec | MAW | DC Junction Box | DC Junction Box | Specifications | 1.17.2 | Touch-safe protective cover | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Sumec | MAW | DC Junction Box | DC Junction Box | Standards | 1.17.3 | EN 50178 | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? | High currat devices no, just a statement of compliance | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Sumec | MAW | DC Junction Box | DC Junction Box | Standards | 1.17.3 | EN 60439-1 | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? | arcing fault / Störlichtbogen Verhalten no, just a statement of compliance | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Sumec | MAW | DC Junction Box | DC Junction Box | Standards | 1.17.3 | EN 61000-6 | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? | EMV no, just a statement of compliance | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Sumec | JBU | Step-up Transformers/MV Switchgear | Due Diligence | Quality Assurance | 1.21.3 | Factory witness testing will be required for MV transformer and switchgear to be installed at this project. The cost of the due diligence to be carried by the Employer through an independent technical consultant will be taken over by the successful bidder up to an amount of 30,000 USD. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Sumec | MAW | Inverters | Due diligence | Quality Assurance | 1.18.12 | The Bidder accepts that the cost of the Quality assurance for Inverters to be carried by the Employer through an independent technical consultant shall be taken over by the successful bidder up to an amount of 100,000 USD. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Sumec | MAW | Modules | Due Diligence | Quality Assurance | 1.14.6 | The bidder will bear the cost of the Quality assurance for PV modules on-site and in laboratory to be carried out by the Employer through an independent technical consultant up to 150,000 USD. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Sumec | GD | Technical Bid Evaluation Criteria | Due Diligence | Quality Assurance | 1.3.5 | The cost of the due diligence to be carried out by the Employer through an independent technical consultant before contract signature will be taken over by the successful bidder up to an amount of 50,000 USD independent of the result. The due diligence will cover a module factory visit, an inverter factory inspection and a due diligence on the provided financial, EPC and O&M credentials including up to three site visits. | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  | Only to be checked in list of deviations. |  |  |  | 1 |  | Open
Sumec | GD | Scope of the Bid | General items | Guarantees | 1.1.5 | Energy Purchase Agreement (EPA) practices are followed | 1 |  |  |  | 1 | Important reasons: due to current uncertainty of the criteria we accept an open status. Please clarify that yo acknowledge the criteria and comply unless a reason of high importance will not allow you you to comply. In such a situation the parties will seek to agree a compromise. |  | This cannot be evaluated at this stage. | we need a sentence that it should and can only be disregarded for important reasons |  |  | 1 |  | Open
Sumec | JBS | Labelling | General items | Labelling | 1.26 | the ID numbering / coding system shall allow unique identification of all components and be understandable | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Cannot be evaluated at this stage |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Sumec | JBS | Labelling | General items | Labelling | 1.26 | Tags shall be weather and UV resistant. | 1 | Vol 1 page 99 | 1 |  |  |  |  | Cannot be evaluated at this stage |  |  |  | 1 |  | Pass
Sumec | JBS | Labelling | General items | Labelling | 1.26 | The ID’s shall correspond to all drawings, plant documentation and control system. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Cannot be evaluated at this stage |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Sumec | GD | Scope of the Bid | General items | Quality Assurance | 1.1.3 | Defect components consequences: If one tested sample fails in one criterion, all items of the same category will be regarded as failed and rejected. | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  | Only to be checked in list of deviations. | yes, we need to be sure that they comply as for most of the critera |  |  | 1 | 1 | Open
Sumec | GD | Scope of the Bid | General items | Specific Requirements | 1.1.2 | The Offer shall include a list of all vendors and/or sub-contractors for major equipment. | 1 |  |  |  | 1 | [6 empty] | 1 |  | Open
Sumec | GD | Scope of the Bid | General items | Specific Requirements | 1.1.9 | The bid covers the planning of the System design, the required functionality of the System in terms of its sub-systems and components, detailed feature-wise descriptions of the components to be used in the System, the planning of the System installation, its integration, testing, monitoring, commissioning and O&M of the System | 1 |  |  |  | 1 | We can not find all of the requested criteria in your documents. Please confirm that your bid is compliant with all expectations and requirements of Section 6 of the RFP and provide a list with ALL exeptions or alterations. This applies to both, the EOPC And the O&M part. |  | This question should be removed as detailed design of every component/sub-system will be checked and evaluated thoroughly in technical evaluation | no, its an overall critera an need to be met |  |  | 1 | 1 | Open
Sumec | JBS | Basic Scope of Supply | General items | Specific Requirements | 1.6 | The maximum DC voltage shall not exceed 1500 V | 1 | Volume 1 page 8 | 1 | [8 empty] | 1 |  | Pass
Sumec | JBS | Basic Scope of Supply | General items | Specific Requirements | 1.6 | The required AC voltage / frequency at grid connection shall 132 kV/50 Hz | 1 | Vol 1page 311 ff | 1 | [8 empty] | 1 |  | Pass
Sumec | JBS | Equipment guarantees | Inverter | Guarantees | 1.28.2 | The Successful Bidder shall provide an Inverter warranty of at least 5 years. A spare parts warranty shall be included for the 25 years operational period. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Sumec | JBU | Inverter/Transformer Station | Inverter/Transformer Station | Specific Requirements | 1.22 | All stations shall be equipped with fire and smoke detectors and alarm, connected to security and surveillance system | 1 |  | 1 | [8 empty] | 1 |  | Pass
Sumec | JBU | Inverter/Transformer Station | Inverter/Transformer Station | Specific Requirements | 1.22 | Bidder shall firmly specify the number of stations, manufacturer, capacity and type of equipment. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Sumec | JBU | Inverter/Transformer Station | Inverter/Transformer Station | Specific Requirements | 1.22 | Every ten (10) or lesser number of stations shall be equipped with an earthing and short-circuiting equipment | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Sumec | JBU | Inverter/Transformer Station | Inverter/Transformer Station | Specific Requirements | 1.22 | Fine sand filters shall be installed | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Sumec | JBU | Inverter/Transformer Station | Inverter/Transformer Station | Specific Requirements | 1.22 | The station shall enable the grounding of hardware and neutral will be left ground isolated | 1 |  | 1 | [8 empty] | 1 |  | Pass
Sumec | MAW | Inverters | Inverters | Design factors to be provided | 1.18.7 | Cooling method | 1 | Vol I page 283 | 1 |  |  |  | Adaptive forced-air cooling |  |  |  |  | 1 |  | Pass
Sumec | MAW | Inverters | Inverters | Design factors to be provided | 1.18.7 | Detection of insulation faults | 1 | Vol I page 283 | 1 | [8 empty] | 1 |  | Pass
Sumec | MAW | Inverters | Inverters | Design factors to be provided | 1.18.7 | Input voltage range (The voltage window for MPP tracking shall accommodate the expected degradation of the modules.) | 1 | Vol I page 283 | 1 | [8 empty] | 1 |  | Pass
Sumec | MAW | Inverters | Inverters | Design factors to be provided | 1.18.7 | Integrated transformer/transformerless / Outside Dry Type Transformer | 1 | Vol I page 283 | 1 | [8 empty] | 1 |  | Pass
Sumec | MAW | Inverters | Inverters | Design factors to be provided | 1.18.7 | Maximum output current | 1 | Vol I page 283 | 1 | [8 empty] | 1 |  | Pass
Sumec | MAW | Inverters | Inverters | Design factors to be provided | 1.18.7 | Nominal output frequency, 3-phase | 1 | Vol I page 283 | 1 | [8 empty] | 1 |  | Pass
Sumec | MAW | Inverters | Inverters | Design factors to be provided | 1.18.7 | Nominal output voltage | 1 | Vol I page 283 | 1 | [8 empty] | 1 |  | Pass
Sumec | MAW | Inverters | Inverters | Design factors to be provided | 1.18.7 | Nominal power | 1 | Vol I page 283 | 1 | [8 empty] | 1 |  | Pass
Sumec | MAW | Inverters | Inverters | Design factors to be provided | 1.18.7 | Operating temperature range | 1 | Vol I page 283 | 1 |  |  |  |  | What is the acceptable range? | 60°C Derating? |  |  | 1 |  | Pass
Sumec | MAW | Inverters | Inverters | Design factors to be provided | 1.18.7 | Output voltage range | 1 | Vol I page 283 | 1 | [8 empty] | 1 |  | Pass
Sumec | MAW | Inverters | Inverters | Design factors to be provided | 1.18.7 | Peak efficiency/ Weighted efficiency | 1 | Vol I page 283 | 1 | [8 empty] | 1 |  | Pass
Sumec | MAW | Inverters | Inverters | Design factors to be provided | 1.18.7 | Protection rating: NEMA 3R, IP54/IP55/IP60 | 1 | Vol I page 283 |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | Datenblatt IP-Wert 20 |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Sumec | MAW | Inverters | Inverters | Design factors to be provided | 1.18.7 | PV array configuration options: positive ground, negative ground | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Sumec | MAW | Inverters | Inverters | Functionalities | 1.18.3 | Active power control reduction: remotely set point of control in case of network congestions or risk of system collapse, if deemed necessary | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | 8.2 needs to ensure these questions are answered in the bids. |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Sumec | MAW | Inverters | Inverters | Functionalities | 1.18.3 | Anti-islanding protection | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Sumec | MAW | Inverters | Inverters | Functionalities | 1.18.3 | Frequency regulation | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | 8.2 needs to ensure these questions are answered in the bids. |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Sumec | MAW | Inverters | Inverters | Functionalities | 1.18.3 | Limitation of voltage fluctuation due to switching operations and long-term flicker | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | 8.2 needs to ensure these questions are answered in the bids. |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Sumec | MAW | Inverters | Inverters | Functionalities | 1.18.3 | Limitation of current harmonics and higher frequency components up to 9 kHz | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Sumec | MAW | Inverters | Inverters | Functionalities | 1.18.3 | Limitation of short-circuit current | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | 8.2 needs to ensure these questions are answered in the bids. |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Sumec | MAW | Inverters | Inverters | Functionalities | 1.18.3 | Limitation of steady-stage voltage changes to 2% of the nominal value | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Sumec | MAW | Inverters | Inverters | Functionalities | 1.18.3 | Matching grid voltage and frequency at point-of-coupling | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Sumec | MAW | Inverters | Inverters | Functionalities | 1.18.3 | Maximum Power Point Tracking (MPPT) and string/sub-array management | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Sumec | MAW | Inverters | Inverters | Functionalities | 1.18.3 | Voltage and frequency fault ride-through: no disconnection of the connection through voltage dip and change of active power generation, feed-in of reactive power during the fault for voltage stabilisation | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | 8.2 needs to ensure these questions are answered in the bids. |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Sumec | MAW | Inverters | Inverters | Functionalities | 1.18.3 | Voltage regulation through reactive power support: remotely set point control for voltage stability | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | 8.2 needs to ensure these questions are answered in the bids. |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Sumec | MAW | Inverters | Inverters | Manufacturers confirmation | 1.18.9 | The Bidder shall deliver a manufacturer's confirmation in his Bid for the suitability of the inverter for the specific weather conditions applicable in Bahawalpur Pakistan. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Sumec | MAW | Inverters | Inverters | Quality Assurance | 1.18.11 | After commissioning, 1 of 10 inverters will be measured on site (power curve and efficiency) by an approved independent technical consultant on behalf of the Employer. The on-site measurements shall be accepted by the Bidder as average values for all inverters | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Cannot be evaluated at this stage | compliance! | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Sumec | MAW | Inverters | Inverters | Quality Assurance | 1.18.11 | Check of protection against overload, short-circuit, grid-failure, internal failure, over-temperature (de-rating), surge protection, detection of insulation faults of AC Cables. Bidder shall firmly specify the manufacturer, types and length of cables to be installed | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | 8.2 needs to ensure these questions are answered in the bids. |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Sumec | MAW | Inverters | Inverters | Quality Assurance | 1.18.11 | Test run and check of MPP tracking of all inverters | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | 8.2 needs to ensure these questions are answered in the bids. |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Sumec | MAW | Inverters | Inverters | Quality Assurance | 1.18.11 | Test run in the field for maximum and EU-efficiency of all Inverters | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | 8.2 needs to ensure these questions are answered in the bids. |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Sumec | MAW | Inverters | Inverters | Quality Assurance | 1.18.11 | The Bidder shall deliver detailed protocols of performance test run (warm power test) for every single inverter | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Cannot be evaluated at this stage |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Sumec | MAW | Inverters | Inverters | Specific Requirements | 1.18.6 | Specifications of table in Schedule C shall be met | 1 |  |  |  | 1 |  |  | Link to table |  | C |  | 1 |  | Open
Sumec | MAW | Inverters | Inverters | Standards | 1.18.8 | IEEE 1547 | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? | no, just a statement of compliance Interconnecting Distributed Resources | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Sumec | MAW | Inverters | Inverters | Standards | 1.18.8 | TUV, VDE, or equivalent certification of passing the relevant standards | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Sumec | MAW | Inverters | Inverters | Strategic Reason for Inverter Selection | 1.18.2 | Available uptime | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Sumec | MAW | Inverters | Inverters | Strategic Reason for Inverter Selection | 1.18.2 | Balance of System (BOS) costs of inverter and labour | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  | financial bid | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Sumec | MAW | Inverters | Inverters | Strategic Reason for Inverter Selection | 1.18.2 | Concept of protection against overload, short-circuit, grid-failure, internal failure, over-temperature (de-rating), surge protection | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Its too general, needs to be reviewed. | failure codes and consquences (automatic/manual restart, throw away safety devices) | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Sumec | MAW | Inverters | Inverters | Strategic Reason for Inverter Selection | 1.18.2 | Dust and heat protection | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  | derating? | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Sumec | MAW | Inverters | Inverters | Strategic Reason for Inverter Selection | 1.18.2 | Timely and effective monitoring at a granular/zoomed-in level | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Sumec | GD | Scope of the Bid | Layout | Guarantees | 1.1.6 | The bidder confirms that the system complies with all applicable requirements of the NEPRA Grid Code of Pakistan and its Draft Amendment no. 2 for Solar Power Projects. | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  | Only to be checked in list of deviations. |  |  |  | 1 |  | Open
Sumec | JBS | Physical layout | Layout | Specific Requirements | 1.7.2 | Provide a schematic electrical Single Line Diagram (SLD) of the entire System layout from the modules to the grid-connection, identifying and listing all of the following DC and AC components. | 1 | Vol 3page 4 | 1 | [8 empty] | 1 |  | Pass
Sumec | JBS | Physical layout | Layout | Specific Requirements | 1.7.2 | The system design shall be such as to ensure ease of maintenance and a multiple ring main unit (RMU) philosophy (on MV level) must be followed for circuit breaker configuration. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Sumec | MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Bills of Materials, BoMs: (glass, encapsulant, backsheet, ribbon, adhesives, cable, junction box, connector) | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Sumec | MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Current at the maximum current point | 1 | Vol I page 270 | 1 | [8 empty] | 1 |  | Pass
Sumec | MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Degradation Curve from Manufacturer | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Sumec | MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Manufacturers confirmation for the suitability of module for specific weather conditions and the high UV-radiation | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  | especially reliability at high UV irridiance / Product warranty | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Sumec | MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Manufacturers installation guidelines | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Sumec | MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Materials and workmanship warranty of a minimum of 10 years | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Sumec | MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Maximum rated power | 1 |  | 1 | [8 empty] | 1 |  | Pass
Sumec | MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Maximum system voltage | 1 | Vol I page 270 | 1 | [5 empty] | … at SK-II safety class |  |  | 1 |  | Pass
Sumec | MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Minimum efficiency at 200 W/m² (25°, AM 1.5) | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Sumec | MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Open-circuit voltage | 1 | Vol I page 270 | 1 | [8 empty] | 1 |  | Pass
Sumec | MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Operating temperature range and nominal operating cell temperature NOCT | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | What range is acceptable | There is as small range anyway Will result in the PR losses | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Sumec | MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Power warranty/performance guarantee of a minimum of 25 years: the power output should not fall below 90% within 10 years, and below 80% within 25 years; linear warranty mandatory | 1 |  | 1 | [8 empty] | 1 |  | Pass
Sumec | MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Provide guarantees and data sheets (to be transferred to Employer upon COD) | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Sumec | MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Rated power tolerance | 1 |  | 1 | [8 empty] | 1 |  | Pass
Sumec | MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Short-circuit current | 1 | Vol I page 270 | 1 | [8 empty] | 1 |  | Pass
Sumec | MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Specify number of modules and total MWp to be provided | 1 |  | 1 |  |  |  | taken from Pvsyst Reports |  |  |  |  | 1 |  | Pass
Sumec | MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Tolerance to wind (maximum load) impact (mechanical load) | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  | minimum 2400 Pa | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Sumec | MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Type of cells comprising the module, and number of cells in series | 1 | Vol I page 270 | 1 | [5 empty] | manufacturer |  |  | 1 |  | Pass
Sumec | MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Voltage at the maximum power point | 1 | Vol I page 270 | 1 | [8 empty] | 1 |  | Pass
Sumec | JBS | Equipment guarantees | Modules | Guarantees | 1.28.1 | The Successful bidder shall provide a Module warranty of at least 10 years. The performance warranty of the module shall be linear with a fixed factor over 25 years. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | To be discussed |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Sumec | MAW | Modules | Modules | Pre-shipment quality assurance | 1.14.4 | All modules must undergo Electroluminiscense (EL) inspection with a resolution of minimum 4 MPixel prior to shipment. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Cannot be evaluated at this stage. | compliance necessary | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Sumec | MAW | Modules | Modules | Pre-shipment quality assurance | 1.14.7 | Warranties and evidence shall be given by the bidder that their selected modules have been tested for susceptibility to Potential Induced Degradation (PID). | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Sumec | MAW | Modules | Modules | Pre-shipment quality assurance | 1.14.4 | A sufficient EVA cross linking has to be verified per production line through a gel content test supervised by an accredited (IEC 17025 or national pendant) independent certified module testing agency. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Cannot be evaluated at this stage. | compliance necessary | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Sumec | MAW | Modules | Modules | Pre-shipment quality assurance | 1.14.4 | Pre-shipment flash tested data Quality assurance for PV modules on-site and in laboratory simulator must meet the class AAA requirements of IEC 60904-9. The sun simulator must be calibrated with a reference cell, which itself was calibrated by a member of the WPVS scheme, with a maximum uncertainty of Isc of 1%. unique barcode (SNr) and labelled performance headlines (P(mpp), I(sc), U(oc), I(mpp), U(mpp) maximum current, maximum voltage Positive power sorting | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Cannot be evaluated at this stage. | compliance necessary | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Sumec | MAW | Modules | Modules | Quality assurance on site | 1.14.5 | The modules shall undergo an incoming inspection at arrival on construction site. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Cannot be evaluated at this stage. | stated and accepted | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Sumec | MAW | Modules | Modules | Standards (as applicable to crystalline silicion or thin-film) | 1.14.3 | IEC 60364-4-41 | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? | no, just a statement of compliance 'protection against electric shock | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Sumec | MAW | Modules | Modules | Standards (as applicable to crystalline silicion or thin-film) | 1.14.3 | IEC 60904-1, IEC 60904-3 | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? | no, just a statement of compliance | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Sumec | MAW | Modules | Modules | Standards (as applicable to crystalline silicion or thin-film) | 1.14.3 | IEC 61215 | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? | no, just a statement of compliance | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Sumec | MAW | Modules | Modules | Standards (as applicable to crystalline silicion or thin-film) | 1.14.3 | IEC 61416 | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? | not existing | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Sumec | MAW | Modules | Modules | Standards (as applicable to crystalline silicion or thin-film) | 1.14.3 | IEC 61646 | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? | no, just a statement of compliance | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Sumec | MAW | Modules | Modules | Standards (as applicable to crystalline silicion or thin-film) | 1.14.3 | IEC 61701 | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? | no, just a statement of compliance | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Sumec | MAW | Modules | Modules | Standards (as applicable to crystalline silicion or thin-film) | 1.14.3 | IEC 61730 | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? | no, just a statement of compliance | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Sumec | MAW | Inverters | Monitoring | Functionalities | 1.18.3 | Advanced communication, with intelligent alerts/warnings, to the SCADA server | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Sumec | JBS | Equipment guarantees | Mounting | Guarantees | 1.28.3 | The Successful Bidder shall provide a product warranty for the structure of at least 10 years. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Sumec | RM | Mounting | Mounting | Specific Requirements | 1.13.8 | The mounting structures must be earthed | 1 | Vol-III, F19 |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Sumec | RM | Mounting | Mounting | Specific Requirements | 1.13.1 | The system is fixed-tilted. Tilt angle is specified. | 1 | Vol-II,p396 Vol-I, p80 | 1 |  |  |  | 27° |  |  |  |  | 1 |  | Pass
Sumec | RM | Mounting | Mounting | Specific Requirements | 1.13.5 | All fastening structures must be verified for durability and resistance to environmental degradation for 25 years | 1 | Vol-III, F19 |  |  | 1 |  | hot dip galv. Steel: Thickness? | What sort of mechanism is required for verification? | Sub structure description / materials double to line 172 - 175 |  |  | 1 |  | Open
Sumec | RM | Mounting | Mounting | Specific Requirements | 1.13.3 | Mounting structure is made of durable material, resistant to sandstorms and compatible with the module frame material so as to avoid any adverse electrolytic/galvanic effects. | 1 | Vol-III, F19 |  |  | 1 |  | hot dip galv. Stee | Information about materials to be known before evaluation. | right |  |  | 1 |  | Open
Sumec | RM | Mounting | Mounting | Specific Requirements | 1.13.3 | Mounting system resists corrosion (passing the salt spray test IEC 61701, among other verification), | 1 | Vol-III, F19 |  |  | 1 |  | hot dip galv. Stee | Information about materials to be known before evaluation. | right |  |  | 1 |  | Open
Sumec | RM | Mounting | Mounting | Specific Requirements | 1.13.3 | Mounting system resists high wind speeds (up to 40 m/s) | 1 | Vol-III, F19 |  |  | 1 | [6 empty] | 1 |  | Open
Sumec | RM | Mounting | Mounting | Specific Requirements | 1.13.3 | Mounting system resists UV induced degradation | 1 | Vol-III, F19 |  |  | 1 |  | hot dip galv. Stee |  |  |  |  | 1 |  | Open
Sumec | RM | Mounting | Mounting | Specific Requirements | 1.13.9 | Specific site conditions have been considered. | 1 | Vol-III, F19 |  |  | 1 |  | "Final geo survey" shall be executed by bidder. Breacket Pile foundation offered | Needs to be discussed. | … specific requirements of the soil conditions Static |  |  | 1 |  | Open
Sumec | JBU | Step-up Transformers/MV Switchgear | MV Switchgear | Design factors to be provided | 1.21.4 | Rated lightning impulse voltage | 1 |  | 1 | [8 empty] | 1 |  | Pass
Sumec | JBU | Step-up Transformers/MV Switchgear | MV Switchgear | Design factors to be provided | 1.21.4 | Rated power frequency withstand voltage | 1 |  | 1 | [8 empty] | 1 |  | Pass
Sumec | JBU | Step-up Transformers/MV Switchgear | MV Switchgear | Design factors to be provided | 1.21.4 | Rated short circuit current | 1 |  | 1 | [8 empty] | 1 |  | Pass
Sumec | JBU | Step-up Transformers/MV Switchgear | MV Switchgear | Design factors to be provided | 1.21.4 | System maximum voltage | 1 |  | 1 | [8 empty] | 1 |  | Pass
Sumec | JBU | Step-up Transformers/MV Switchgear | MV Switchgear | Design factors to be provided | 1.21.4 | System nominal voltage | 1 |  | 1 | [8 empty] | 1 |  | Pass
Sumec | JBU | Step-up Transformers/MV Switchgear | MV Switchgear | Specific Requirements | 1.21.4 | Interlocks will also be mechanically interlocked between line MV switchgears. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Sumec | JBU | Step-up Transformers/MV Switchgear | MV Switchgear | Specific Requirements | 1.21.4 | MV Switchgears shall be SF6 gas insulated or VCB (Vacuum circuit breaker). | 1 |  | 1 | [8 empty] | 1 |  | Pass
Sumec | JBU | Step-up Transformers/MV Switchgear | MV Switchgear | Specific Requirements | 1.21.4 | The separating equipment shall be installed with visible disconnection (pivotable disconnectors). | 1 |  | 1 |  |  |  |  | Cannot be evaluated at this stage |  |  |  | 1 |  | Pass
Sumec | JBU | Step-up Transformers/MV Switchgear | MV Switchgear | Standards | 1.21.5 | IEC 60529 | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Sumec | JBU | Step-up Transformers/MV Switchgear | MV Switchgear | Standards | 1.21.5 | IEC 62271-200 | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Sumec | JBU | Step-up Transformers/MV Switchgear | MV Switchgear | Standards | 1.21.5 | IEC 62446 | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Sumec | MAW | Inverters | O&M | Guarantees | 1.18.2 | For central inverters concept: the bidder shall ensure with an undertaking from the manufacturer that the concerned skilled staff will be made available at the site within 24 hours of reporting the defect to the manufacturer. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Sumec | JBS | Physical layout | Physical layout plan | Specific Requirements | 1.7.7 | Detailed top view of the PV mounting structure, including module sizes and spacing between the module rows | 1 | Vol 3page 21 |  |  | 1 | Is the row distance calculated with the lowest sun elevation angle of the year? | [5 empty] | 1 |  | Open
Sumec | JBS | Physical layout | Physical layout plan | Specific Requirements | 1.7.7 | Detailed view of the distribution of inverters and connections to the PV string/array | 1 | Vol 3page 4 | 1 | [8 empty] | 1 |  | Pass
Sumec | JBS | Physical layout | Physical layout plan | Specific Requirements | 1.7.7 | Detailed side and front view of the PV mounting structure | 1 | Vol 3page 21 | 1 | [8 empty] | 1 |  | Pass
Sumec | JBS | Physical layout | Physical layout plan | Specific Requirements | 1.7.7 | Detailed top view of electrical cabling interconnections | 1 |  | 1 | [8 empty] | 1 |  | Pass
Sumec | JBS | Physical layout | Physical layout plan | Specific Requirements | 1.7.7 | Floor plans and elevations for all buildings, housing units, containers on site: e.g. , substations, the SCADA operational room, inverters, O&M, storage facilities | 1 | Vol 3page 15 | 1 | [8 empty] | 1 |  | Pass
Sumec | JBS | Physical layout | Physical layout plan | Specific Requirements | 1.7.7 | Location of the system metering and grid connection point | 1 |  | 1 | [8 empty] | 1 |  | Pass
Sumec | JBS | Power plant documentation | Power plant documentation | Quality Assurance | 1.27.1 | Flash report list of all modules shall be provided in digital form. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Sumec | JBS | Power plant documentation | Power plant documentation | Quality Assurance | 1.27.1 | The Bidder shall confirm that the complete as-built documentation of the plant will be provided in compliance with IEC 62446. Additionally all module serial numbers shall be listed with their individual location. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Sumec | JBS | Workflow, Project Management Plan and Timelines | Project schedule / Project management | Project schedule | 1.8.1 | Interdependencies between the tasks | 1 | Vol 1 page 170 | 1 | [8 empty] | 1 |  | Pass
Sumec | JBS | Workflow, Project Management Plan and Timelines | Project schedule / Project management | Project schedule | 1.8.1 | Interdependencies of tasks with equipment order and delivery times | 1 |  |  |  | 1 | Please provide a plan with equipment ordering. | [5 empty] | 1 |  | Open
Sumec | JBS | Workflow, Project Management Plan and Timelines | Project schedule / Project management | Project schedule | 1.8.1 | Key milestones to indicate that the progress in on schedule | 1 | Vol 1 page 170 | 1 | [8 empty] | 1 |  | Pass
Sumec | JBS | Workflow, Project Management Plan and Timelines | Project schedule / Project management | Project schedule | 1.8.1 | Provide installation schedule in compliance with sub-clause 8.2 of Particular Conditions (Time for Completion is 225 days after Commencement Date). | 1 | Vol 1 page 170 | 1 |  |  |  | 215 Tage | Find sub-clause 8.2 of Particular Conditions |  |  |  | 1 |  | Pass
Sumec | JBS | Workflow, Project Management Plan and Timelines | Project schedule / Project management | Project schedule | 1.8.1 | Provide work breakdown structures, activity decomposition and sequencing and dependability with the baseline schedule clearly showing the critical path | 1 | Vol 1 page 170 | 1 | [8 empty] | 1 |  | Pass
Sumec | JBS | Workflow, Project Management Plan and Timelines | Project schedule / Project management | Project schedule | 1.8.1 | Schedule of tasks | 1 | Vol 1 page 171 ff | 1 | [8 empty] | 1 |  | Pass
Sumec | JBS | Workflow, Project Management Plan and Timelines | Project schedule / Project management | Project schedule | 1.8.1 | Teams, the number and skills of personnel to be deployed for each task | 1 | Vol 1 page 48 ff | 1 | [8 empty] | 1 |  | Pass
Sumec | JBS | Workflow, Project Management Plan and Timelines | Project schedule / Project management | Quality Assurance | 1.8.3 | Inspection of equipment delivery | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Sumec | JBS | Workflow, Project Management Plan and Timelines | Project schedule / Project management | Quality Assurance | 1.8.3 | Milestones for the completion of civil, mechanical, and electrical works | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  | dobble to 105 and 111 | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Sumec | JBS | Workflow, Project Management Plan and Timelines | Project schedule / Project management | Quality Assurance | 1.8.3 | Quality control of delivered modules | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Sumec | JBS | Workflow, Project Management Plan and Timelines | Project schedule / Project management | Quality Assurance | 1.8.3 | Risk analysis and mitigation plan | 1 | Vol 1 page 133 | 1 | [8 empty] | 1 |  | Pass
Sumec | JBS | Workflow, Project Management Plan and Timelines | Project schedule / Project management | Quality Assurance | 1.8.3 | System acceptance QA procedure by the Employer | 1 | Vol 1 page 142 |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Sumec | JBS | Miscellaneous | Project schedule / Project management | Specific Requirements | 1.29.9 | The Bidder shall submit an organizational chart illustrating management and functional relationships among all project team members including consultants, sub-contractors and vendors at each significant stage of the work, such as permitting, design, construction, testing and commissioning and O&M. | 1 | Vol 1 Page 35, 45 ff | 1 | [8 empty] | 1 |  | Pass
Sumec | RM | Supervisory Control and Data Acquisition (SCADA) | SCADA | Specific Requirements | 1.9.2 | Alarms/alerts and timely notification of key performance indicators | 1 |  | 1 | [8 empty] | 1 |  | Pass
Sumec | RM | Supervisory Control and Data Acquisition (SCADA) | SCADA | Specific Requirements | 1.9.2 | All communication/data cables outside of buildings must be fiber-optic cables | 1 | Vol-I, p23 |  | 1 |  | All communication/data cables outside of buildings must be fiber-optic cables | 45km of DJYVRP2-22-2*1.0 = copper for outside |  |  |  |  | 1 |  | Fail
Sumec | RM | Supervisory Control and Data Acquisition (SCADA) | SCADA | Specific Requirements | 1.9.2 | Back-up power for a minimum of twelve hours | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 200Ah means what? |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Sumec | RM | Supervisory Control and Data Acquisition (SCADA) | SCADA | Specific Requirements | 1.9.2 | Control room to remotely monitor and manage the whole system, on a 24 x 7 basis, with the capability of Web-based information sharing | 1 |  | 1 | [8 empty] | 1 |  | Pass
Sumec | RM | Supervisory Control and Data Acquisition (SCADA) | SCADA | Specific Requirements | 1.9.2 | Data must be readily available for the fulfilment of all warranties and performance guarantees | 1 |  | 1 |  |  |  |  | Cannot be evaluated at this stage. | statement |  |  | 1 |  | Pass
Sumec | RM | Supervisory Control and Data Acquisition (SCADA) | SCADA | Specific Requirements | 1.9.2 | Data logging at intervals of not less than one minute, processing, transmission, and back-up | 1 |  |  |  | 1 |  |  |  | not more (!) |  |  | 1 |  | Open
Sumec | RM | Supervisory Control and Data Acquisition (SCADA) | SCADA | Specific Requirements | 1.9.2 | Data shall be provided via FTP (Push/Pull) to the Employer | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Sumec | RM | Supervisory Control and Data Acquisition (SCADA) | SCADA | Specific Requirements | 1.9.1 | Remote access to all operational data for independent monitoring purposes shall be possible (NTDC requirements) | 1 |  | 1 | [8 empty] | 1 |  | Pass
Sumec | RM | Supervisory Control and Data Acquisition (SCADA) | SCADA | Specific Requirements | 1.9.1 | Safe and redundant archive for operational data. | 1 | Vol-III, F7 Vol-I, p321-328 | 1 |  |  | General understanding: expressions like "shall", "has to be", "must be" have the meaning of "will be delivered"? | 10 Ethernet rings /97 Inv. DataCollectorCabinet |  |  | General understanding: expressions like "shall", "has to be", "must be" have the meaning of "will be delivered"? |  | 1 |  | Pass
Sumec | RM | Supervisory Control and Data Acquisition (SCADA) | SCADA | Specific Requirements | 1.9.2 | Separate inverter, zone, and string level (current and voltage) monitoring | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Sumec | RM | Supervisory Control and Data Acquisition (SCADA) | SCADA | Specific Requirements | 1.9.1 | The system has to provide different access-levels with different access rights allocated. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Sumec | RM | Earthworks | Site Preparation and site access | Design factors to be provided | 1.12 | All earth works required have to be specified and included in the offer | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Sumec | RM | Earthworks | Site Preparation and site access | Specific Requirements | 1.12, 1.13.4, 1.7.7 | Cross-sections of foundations for stations shall be provided, including explanation of the foundations laying down, height, penetration, and method of installing foundation posts, mounting fixtures | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Sumec | RM | Earthworks | Site Preparation and site access | Specific Requirements | 1.12 | Position and specification of underground cable connections must be documented during installation | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Cannot be avaluated at this stage. |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Sumec | RM | Site Preparation and site access | Site Preparation and site access | Specific Requirements | 1.11.1 | The Bidder shall provide foundations and structures in accordance with the actual soil conditions. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | only example for bracket pile not final |  | refer to Soil study | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Sumec | RM | Earthworks | Site Preparation and site access | Specific Requirements | 1.12 | After completion of construction and all earthworks ground shall be levelled and stabilized. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  | (maintanance, dust) | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Sumec | RM | Earthworks | Site Preparation and site access | Specific Requirements | 1.12 | Within the plant boundary limits, access roads to all stations shall be suitable for heavy load trucks (axle load: min. 12 tonn). | 1 | Vol-I, p37 p68 |  |  | 1 |  | Vol-II, p398 exvacation: 42000m³ backfilling: 1500m³ foundation (Stations?): 780m³ |  |  |  |  | 1 |  | Open
Sumec | JBS | Power plant documentation | Spare parts | Warranty | 1.27.2 | The successful bidder shall provide all warranty spares for a warranty period of 5 years. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Sumec | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Design factors to be provided | 1.21.2 | 3-phase, double wound, continuously rated, oil-cooled, enclosed transformers, use of low loss core steel and close coupled copper windings | 1 |  | 1 | [8 empty] | 1 |  | Pass
Sumec | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Design factors to be provided | 1.21.2 | Cooling method | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Sumec | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Design factors to be provided | 1.21.2 | Efficiency | 1 | TECHNICAL OFFER-VOLUME I, page 295 | 1 |  |  |  | 2% of losses |  |  |  |  | 1 |  | Pass
Sumec | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Design factors to be provided | 1.21.2 | Humidity tolerance | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Sumec | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Design factors to be provided | 1.21.2 | Incoming terminals | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Sumec | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Design factors to be provided | 1.21.2 | Insulation type | 1 |  | 1 | [8 empty] | 1 |  | Pass
Sumec | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Design factors to be provided | 1.21.2 | kVA rating | 1 |  | 1 | [8 empty] | 1 |  | Pass
Sumec | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Design factors to be provided | 1.21.2 | Maximum ambient temperature and altitude | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Sumec | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Design factors to be provided | 1.21.2 | No-load losses | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Sumec | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Design factors to be provided | 1.21.2 | Operating temperature range | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Sumec | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Design factors to be provided | 1.21.2 | Operational data shall be logged in central operating system (e.g. oil temperature, oil level, pressure, Temperature probes (one per phase): Alarm and trip of cell etc.) | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Sumec | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Design factors to be provided | 1.21.2 | Outgoing terminals | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Sumec | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Design factors to be provided | 1.21.2 | Primary side voltage | 1 |  | 1 | [8 empty] | 1 |  | Pass
Sumec | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Design factors to be provided | 1.21.2 | Protection system | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Sumec | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Design factors to be provided | 1.21.2 | Secondary side voltage | 1 |  | 1 | [8 empty] | 1 |  | Pass
Sumec | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Design factors to be provided | 1.21.2 | Short-circuit impedance | 1 |  | 1 | [8 empty] | 1 |  | Pass
Sumec | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Standards | 1.21.3 | IEC 60076 | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Sumec | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Standards | 1.21.3 | IEC 60085 | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Sumec | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Standards | 1.21.3 | IEC 60137 | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Sumec | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Standards | 1.21.3 | IEC 60214 | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Sumec | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Standards | 1.21.3 | IEC 62446 | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Sumec | JBU | Step-up Transformers/MV Switchgear | Step-up Transformers/MV Switchgear | Guarantees | 1.21.1 | Compatibility with NTDC grid connection code must be ensured | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Sumec | GD | PR and System Performance Guarantee | System PR | Guarantees | 1.4.1 | A 25 years commitment, in the form of a whole System performance guarantee, is required. The performance guarantee is based on measuring the PR with the actual kWh-AC delivery per year adjusted for the actual POA irradiation for the same period | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  | Only to be checked in list of deviations. |  |  |  | 1 | 1 | Open
Sumec | JBS | System PR Specification | System PR | Losses included in PR calculation | 1.5.4 | Auxiliary loads | 1 | Vol 1 page 296 ff | 1 |  |  |  |  | We don’t understand the question. Kindly clarify. | see relevant chapter 1.5.4 List of "losses" = auxilary loads from PV Energy that make the PR |  |  | 1 |  | Pass
Sumec | JBS | System PR Specification | System PR | Losses included in PR calculation | 1.5.4 | Inverter (operating efficiency, operating voltage variations, power/voltage levels) | 1 | Vol 1 page 296 ff | 1 |  |  |  |  | We don’t understand the question. Kindly clarify. | see relevant chapter 1.5.4 List of technical losses that make the PR |  |  | 1 |  | Pass
Sumec | JBS | System PR Specification | System PR | Losses included in PR calculation | 1.5.4 | Module Array (temperature dependence, soiling, low light inefficiency, shading, mismatches in array) | 1 | Vol 1 page 294 ff |  |  | 1 | Please calculate new considering shading losses and low light inefficiency losses |  | We don’t understand the question. Kindly clarify. | we want to see these losses specified. Thos need to be aligned with O+M Startegy and System composition |  |  | 1 |  | Open
Sumec | JBS | System PR Specification | System PR | Losses included in PR calculation | 1.5.4 | Ohmic losses in cables | 1 | Vol 1 page 294 ff | 1 |  |  |  |  | We don’t understand the question. Kindly clarify. | see relevant chapter 1.5.4 List of technical losses that make the PR |  |  | 1 |  | Pass
Sumec | JBS | System PR Specification | System PR | Losses included in PR calculation | 1.5.4 | Transformer losses | 1 | Vol 1 page 294 ff | 1 |  |  |  |  | We don’t understand the question. Kindly clarify. | see relevant chapter 1.5.4 List of technical losses that make the PR |  |  | 1 |  | Pass
Sumec | JBS | System PR Specification | System PR | O&M | 1.5.2 | The target PR specification at the time of commissioning the System is equal to or greater than 0.75 (75%). | 1 |  |  |  | 1 | The PR of 80.5% does not consider several parameter, see following items. Please calculate new. | [5 empty] | 1 |  | Open
Sumec | JBS | Physical layout | System PR | Specific Requirements | 1.7.1 | Provide a report using Solar GIS data provided by the Employer | 1 | Vol 1page 249 | 1 |  |  |  |  | Replace 'Report' with ' PV-Syst report'. | 'Report' is original wording in ER in 1.7.1 |  |  | 1 |  | Pass
Sumec | JBS | Physical layout | System PR | Specific Requirements | 1.7.1, 1.1.8 | Layout calculations of predicted kWh over the system lifetime and PR using the tool PVSyst V5.62 or higher | 1 |  | 1 | [8 empty] | 1 |  | Pass
Sumec | GD | PR and System Performance Guarantee | System PR | System PR | 1.4.2 | Guaranteed PR values in the form of the Table in 1.4.1 for the acceptance phase and annual output of the PV system shall be specified. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Link to table in Documents sheet |  |  |  | 1 | 1 | Open
Sumec | GD | PR and System Performance Guarantee | System PR | System PR | 1.4.1 | The billing system/metering system will be installed at interconnection point of 132 kV bus bar of HV substation to be installed by the EPC Contractor and the 132 kV Transmission line of NTDC existing at site. | 2 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  | Only to be checked in list of deviations. |  |  |  | 1 |  | Open
Sumec | GD | PR and System Performance Guarantee | System PR | System PR | 1.4.4 | The initial PR will be first measured after the time of commissioning of the completed PV System during the acceptance phase of 30 days. | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  | Cannot be evaluated at this stage. Only to be checked in list of deviations. |  |  |  | 1 | 1 | Open
Sumec | JBS | Equipment guarantees | Warranty | Guarantees | 1.28.4, 1.6 | A detailed list of all guarantee conditions for the main equipments (beside modules and inverters) shall be provided by the Successful Bidder with the technical offer. The product warranty shall be at least 5 years. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Sumec | JBS | Equipment guarantees | Warranty | Guarantees | 1.28 | The overall Guarantee and Power Plant Acceptance Procedures required for the Project are described in Sections 1.3, 1.4, 1.14, 1.18 and Schedule D and shall be met. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Link |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Sumec | JBS | Basic Scope of Supply | Warranty | Quality Assurance | 1.6 | The Product Warranties shall be given for a duration of at least 5 years | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Cannot be evaluated at this stage. Only to be checked in list of deviations. |  |  |  | 1 |  | Open
Sumec | MAW | Inverters | Warranty | Warranty option | 1.18.1 | The Bidder shall arrange a full-service package for the selected inverters for a product warranty period of 5 years, with an option to cover additional 20 years including provisions for any necessary replacements including O&M service plan guaranteeing 99% availability. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Tbea | JBU | AC Cabling | AC Cabling | Design factors to be provided | 1.19.1 | AC cable shall be of Copper. Rated voltage, nominal voltage between phase and neutral and nominal voltage between phases to be specified by the Bidder | 1 |  |  |  | 1 | General understanding: expressions like "shall", "shall be supplied with", "has to be", "must be" have the meaning of "will be delivered"? Please confirm. |  |  |  | G | General understanding: expressions like "shall", "shall be supplied with", "has to be", "must be" have the meaning of "will be delivered"? Please confirm. | 1 |  | Open
Tbea | JBU | AC Cabling | AC Cabling | Design factors to be provided | 1.19.1 | Appropriate sizing to minimise voltage drop and losses | 1 |  |  |  | 1 | General understanding: expressions like "shall", "shall be supplied with", "has to be", "must be" have the meaning of "will be delivered"? Please confirm. |  | What is the appropriate size? | leeway to allow MPP tracking when module voltage drops. At least 10%. Ralf, ist Vital kriterium. | G | General understanding: expressions like "shall", "shall be supplied with", "has to be", "must be" have the meaning of "will be delivered"? Please confirm. | 1 |  | Open
Tbea | JBU | AC Cabling | AC Cabling | Design factors to be provided | 1.19.1 | Bending radius | 1 |  |  |  | 1 | General understanding: expressions like "shall", "shall be supplied with", "has to be", "must be" have the meaning of "will be delivered"? Please confirm. |  |  |  | G | General understanding: expressions like "shall", "shall be supplied with", "has to be", "must be" have the meaning of "will be delivered"? Please confirm. | 1 |  | Open
Tbea | JBU | AC Cabling | AC Cabling | Design factors to be provided | 1.19.1 | Cable installation shall ensure grounding and short-circuit protection | 1 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | JBU | AC Cabling | AC Cabling | Design factors to be provided | 1.19.1 | Cables shall be suitable for the environmental conditions at the project site, including UV protection (The Bidder shall provide certification from manufacturer) | 1 |  |  |  | 1 | General understanding: expressions like "shall", "shall be supplied with", "has to be", "must be" have the meaning of "will be delivered"? Please confirm. |  |  |  | G | General understanding: expressions like "shall", "shall be supplied with", "has to be", "must be" have the meaning of "will be delivered"? Please confirm. | 1 |  | Open
Tbea | JBU | AC Cabling | AC Cabling | Design factors to be provided | 1.19.1 | Installation to be verified by measurement-protocols | 1 |  |  |  | 1 | General understanding: expressions like "shall", "shall be supplied with", "has to be", "must be" have the meaning of "will be delivered"? Please confirm. |  |  |  | G | General understanding: expressions like "shall", "shall be supplied with", "has to be", "must be" have the meaning of "will be delivered"? Please confirm. | 1 |  | Open
Tbea | JBU | AC Cabling | AC Cabling | Design factors to be provided | 1.19.1 | Lifetime longer than 25 years | 1 |  |  |  | 1 | General understanding: expressions like "shall", "shall be supplied with", "has to be", "must be" have the meaning of "will be delivered"? Please confirm. |  |  |  | G | General understanding: expressions like "shall", "shall be supplied with", "has to be", "must be" have the meaning of "will be delivered"? Please confirm. | 1 |  | Open
Tbea | JBU | AC Cabling | AC Cabling | Design factors to be provided | 1.19.1 | Rated voltage | 1 |  |  |  | 1 | General understanding: expressions like "shall", "shall be supplied with", "has to be", "must be" have the meaning of "will be delivered"? Please confirm. |  |  |  | G | General understanding: expressions like "shall", "shall be supplied with", "has to be", "must be" have the meaning of "will be delivered"? Please confirm. | 1 |  | Open
Tbea | JBU | AC Cabling | AC Cabling | Design factors to be provided | 1.19.1 | Sufficient and effective cable protection against attacks of rodents for any cabling underground or above is required | 1 |  |  |  | 1 | General understanding: expressions like "shall", "shall be supplied with", "has to be", "must be" have the meaning of "will be delivered"? Please confirm. |  |  |  | G | General understanding: expressions like "shall", "shall be supplied with", "has to be", "must be" have the meaning of "will be delivered"? Please confirm. | 1 |  | Open
Tbea | JBU | AC Cabling | AC Cabling | Specific Requirements | 1.19.3 | The runs of both the main DC and AC cables, in the System layout, should be adjusted to keep power losses below <1% at STC (Design calculations through cable loss simulation to be provided for review & comment). | 1 |  | 1 |  |  |  |  | Part of system design | Kategorie ? |  |  | 1 |  | Pass
Tbea | JBU | AC Cabling | AC Cabling | Standards | 1.19.2 | DIN-VDE-0276 | 1 |  |  |  | 1 | General understanding: expressions like "shall", "shall be supplied with", "has to be", "must be" have the meaning of "will be delivered"? Please confirm. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  | G | General understanding: expressions like "shall", "shall be supplied with", "has to be", "must be" have the meaning of "will be delivered"? Please confirm. | 1 |  | Open
Tbea | JBU | AC Cabling | AC Cabling | Standards | 1.19.2 | EN 60332-1-1 and EN 60332-2-1 | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Tbea | JBU | AC Cabling | AC Cabling | Standards | 1.19.2 | IEC 60364 | 1 |  |  |  | 1 | General understanding: expressions like "shall", "shall be supplied with", "has to be", "must be" have the meaning of "will be delivered"? Please confirm. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  | G | General understanding: expressions like "shall", "shall be supplied with", "has to be", "must be" have the meaning of "will be delivered"? Please confirm. | 1 |  | Open
Tbea | JBU | AC Cabling | AC Cabling | Standards | 1.19.2 | IEC 60502 | 1 |  |  |  | 1 | General understanding: expressions like "shall", "shall be supplied with", "has to be", "must be" have the meaning of "will be delivered"? Please confirm. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  | G | General understanding: expressions like "shall", "shall be supplied with", "has to be", "must be" have the meaning of "will be delivered"? Please confirm. | 1 |  | Open
Tbea | JBU | AC Combiner Box | AC Combiner Box | Design factors to be provided | 1.20.1 | Class 2 AC surge arrestor | 1 |  | 1 |  |  |  | not applicable |  |  |  |  | 1 |  | Pass
Tbea | JBU | AC Combiner Box | AC Combiner Box | Design factors to be provided | 1.20.1 | Flame test | 1 |  | 1 |  |  |  | not applicable |  |  |  |  | 1 |  | Pass
Tbea | JBU | AC Combiner Box | AC Combiner Box | Design factors to be provided | 1.20.1 | Load breaker switch of adequate size | 1 |  | 1 |  |  |  | not applicable |  |  |  |  | 1 |  | Pass
Tbea | JBU | AC Combiner Box | AC Combiner Box | Design factors to be provided | 1.20.1 | Operating temperature range | 1 |  | 1 |  |  |  | not applicable |  |  |  |  | 1 |  | Pass
Tbea | JBU | AC Combiner Box | AC Combiner Box | Design factors to be provided | 1.20.1 | Rated current | 1 |  | 1 |  |  |  | not applicable |  |  |  |  | 1 |  | Pass
Tbea | JBU | AC Combiner Box | AC Combiner Box | Design factors to be provided | 1.20.1 | Rated voltage | 1 |  | 1 |  |  |  | not applicable |  |  |  |  | 1 |  | Pass
Tbea | JBU | AC Combiner Box | AC Combiner Box | Design factors to be provided | 1.20.1 | Stripping length of the individual wire | 1 |  | 1 |  |  |  | not applicable |  |  |  |  | 1 |  | Pass
Tbea | JBU | AC Combiner Box | AC Combiner Box | Design factors to be provided | 1.20.1 | Waterproof test | 1 |  | 1 |  |  |  | not applicable |  |  |  |  | 1 |  | Pass
Tbea | JBU | AC Combiner Box | AC Combiner Box | Standards | 1.20.2 | EN 60529, DIN-VDE-0472 | 1 |  | 1 |  |  |  | not applicable | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  |  |  | 1 |  | Pass
Tbea | JBU | AC Combiner Box | AC Combiner Box | Standards | 1.20.2 | IP 67 | 1 |  | 1 |  |  |  | not applicable |  |  |  |  | 1 |  | Pass
Tbea | JBS | Physical layout | Auxiliary equipment | Specific Requirements | 1.7.8 | All parts of the installation are covered by two high speed protection schemes, which shall be independent to avoid common mode failures | 1 | page 85 | 1 |  |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | [5 empty] | 1 |  | Pass
Tbea | JBS | Physical layout | Auxiliary equipment | Specific Requirements | 1.7.8 | The outline of protection schemes shall be shown on the single line diagram (SLD) | 1 | page 85 | 1 |  |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | [5 empty] | 1 |  | Pass
Tbea | JBS | Physical layout | Auxiliary equipment | Specific Requirements | 1.7.8 | Provide complete indicating, regulating, controlling, protecting and interlocking equipment necessary for safe and efficient operation of the plant and substation, including complete protection scheme. | 1 | page 85 | 1 |  |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | [5 empty] | 1 |  | Pass
Tbea | JBS | Physical layout | Auxiliary equipment | Specific Requirements | 1.7.9 | The scope of the documentation shall cover at least the requirements of IEC 62446. | 1 | page 87 |  |  | 1 | General understanding: expressions like "shall", "shall be supplied with", "has to be", "must be" have the meaning of "will be delivered"? Please confirm. |  |  |  | G | General understanding: expressions like "shall", "shall be supplied with", "has to be", "must be" have the meaning of "will be delivered"? Please confirm. | 1 |  | Open
Tbea | JBS | Physical layout | Auxiliary equipment | Specific Requirements | 1.7.8 | The Bidder shall include a fire prevention and response plan | 1 | page 86 |  |  | 1 | General understanding: expressions like "shall", "shall be supplied with", "has to be", "must be" have the meaning of "will be delivered"? Please confirm. |  |  |  | G | General understanding: expressions like "shall", "shall be supplied with", "has to be", "must be" have the meaning of "will be delivered"? Please confirm. | 1 |  | Open
Tbea | JBS | Physical layout | Auxiliary equipment | Specific Requirements | 1.7.9 | The documentation includes clearly labelled objects and figures annotated in English language. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | [5 empty] | 1 |  | Open
Tbea | JBS | Physical layout | Auxiliary equipment | Specific Requirements | 1.7.8 | The fire prevention and response plan shall include a fire alarm und detection system with a main panel in the control room | 1 | page 87 |  |  | 1 | General understanding: expressions like "shall", "shall be supplied with", "has to be", "must be" have the meaning of "will be delivered"? Please confirm. |  |  |  | G | General understanding: expressions like "shall", "shall be supplied with", "has to be", "must be" have the meaning of "will be delivered"? Please confirm. | 1 |  | Open
Tbea | RM | Other infrastructure | Auxiliary systems | DC Backup System / uninterrupted power supply (UPS) | 1.25.6 | IEC-60051 and IEC-60439 standards apply | 1 |  |  |  | 1 |  | Wording in Bid is still "IEC-51and IEC-439" insted of 60051 / 60439 | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  |  |  | 1 |  | Open
Tbea | RM | Other infrastructure | Auxiliary systems | Design factors to be provided | 1.25.1 | One administration and office building with car port for 10 vehicles shall be provided, with sufficient space for operating personal, control room, security office, regular office rooms for permanent and visiting staff, meeting room, kitchen sanitary systems (toilet, showers separate for male and female), first aid, control room, electrical rooms, etc. The building shall have windows for office rooms and air conditioning system (split units) for all office rooms. | 1 |  |  |  | 1 |  |  | Priority to be discussed |  |  |  | 1 |  | Open
Tbea | RM | Other infrastructure | Auxiliary systems | Design factors to be provided | 1.25.1 | Service water system sufficiently sized for cleaning cycle of modules | 1 |  |  |  | 1 | [6 empty] | 1 |  | Open
Tbea | RM | Other infrastructure | Auxiliary systems | Design factors to be provided | 1.25.1 | Sewage system including sewage disposal for Construction and O&M phase | 1 |  |  |  | 1 | [6 empty] | 1 |  | Open
Tbea | RM | Other infrastructure | Auxiliary systems | Design factors to be provided | 1.25.1 | Warehouse for spare parts and workshop for minor mechanical/electrical works. | 1 |  |  |  | 1 | [6 empty] | 1 |  | Open
Tbea | RM | Other infrastructure | Auxiliary systems | Design factors to be provided | 1.25.1 | Water storage facility for drinking water, sanitary water (sufficient for 1 week) | 1 |  |  |  | 1 | [6 empty] | 1 |  | Open
Tbea | RM | Other infrastructure | Auxiliary systems | Guarantees | 1.25.4 | All buildings should be designed in accordance with the requirements of the Pakistan Building Code (available at www.pec.org.pk/buildingcode.aspx) and latest Seismic Provisions 2007. | 1 |  |  |  | 1 |  |  | Link to code |  |  |  | 1 |  | Open
Tbea | JBS | Miscellaneous | Auxiliary systems | Power supply | 1.29.1 | An off-grid power station may need to be provided by the Bidder for commencing the work. Diesel generators shall be arranged by the bidder on its own. | 1 | page 51 | 1 | [8 empty] | 1 |  | Pass
Tbea | RM | Other infrastructure | Auxiliary systems | Security Surveillance System | 1.25.5 | The Bidder shall provide security personnel for 24 h / 7 days a week for the whole year | 1 |  |  |  | 1 | [6 empty] | 1 |  | Open
Tbea | RM | Other infrastructure | Auxiliary systems | Security Surveillance System | 1.25.5 | The system shall comply with insurance requirements | 1 |  |  |  | 1 | [6 empty] | 1 |  | Open
Tbea | RM | Meteorological Sensors | Auxiliary Systems | Specific Requirements | 1.10.1 | Irradiation and temperature measurements are to be recorded at intervals of 15 min or less. | 1 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | RM | Meteorological Sensors | Auxiliary Systems | Specific Requirements | 1.10.2 | Seven pyranometers shall be placed : three for measuring the horizontal plane irradiation and the others for the in-plane irradiation. | 1 |  | 1 |  |  |  |  | As in 1.10.2, it is seven pyranometer per system, please clarify the word "per system" | 1.1.1: "100 MWp (DC capacity at Standard Testing Conditions, abbreviated STC … hereinafter called 'the System') " |  |  | 1 |  | Pass
Tbea | RM | Meteorological Sensors | Auxiliary Systems | Specific Requirements | 1.10.2 | The irradiation measurement equipment should be calibrated by an independent certified third party at least every two years. The calibration must be traceable to international standards. | 1 |  | 1 |  |  |  |  | Should be checked in list of deviations |  |  |  | 1 |  | Pass
Tbea | RM | Meteorological Sensors | Auxiliary Systems | Specific Requirements | 1.10.3 | Ambient air and the module temperature shall be measured at every 5 installed MWp in conformity with IEC 60751 AA | 1 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | RM | Meteorological Sensors | Auxiliary Systems | Specific Requirements | 1.10.1 | The equipment should have the capability of recording and storing data for 24 hours using auxiliary DC power. | 1 |  | 1 |  |  |  |  | Should be priority 1 question |  |  |  | 1 |  | Pass
Tbea | RM | Meteorological Sensors | Auxiliary Systems | Specific Requirements | 1.10.2 | The pyranometers should conform to the standards of ISO 9060 (SR5: secondary standard) or the WMO classification, and IEC 60904. | 1 |  | 1 |  |  |  |  | Do we need to know some parameter values according to standards mentioned or just a statement of comlience with the standard would be sufficient? | compliance will be necessary, no data due diligence right now. |  |  | 1 |  | Pass
Tbea | GD | PR and System Performance Guarantee | Compensations | O&M | 1.4.6 | If the successful Bidder defaults in being able to provide the O&M services required for the Systems performance guarantee, then it will be liable to cover all costs – but at least in the amount of Liquidated Damages imposed to the Employer by its PPA agreements - incurred by the Employer, including the loss of the guaranteed electricity export to the grid (but at a minimum rate of USD 0.20-per-kWh) for the disrupted period, in finding and hiring a replacement for the purpose. | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  | Cannot be evaluated at this stage. Only to be checked in list of deviations. |  |  |  | 1 | 1 | Open
Tbea | GD | PR and System Performance Guarantee | Compensations | O&M | 1.4.5 | For timely compensation the PR Calculation will be carried out provisionally for each quarter whereby the contractor and employer might jointly agree on different PR values for each quarter. In the last quarter of each calendar year the annual PR compensation of the full year will be carried out and any provisions will be offset by the annual compensation. | 3 |  |  |  | 1 |  |  | Cannot be evaluated at this stage. Only to be checked in list of deviations. |  |  |  | 1 |  | Open
Tbea | GD | PR and System Performance Guarantee | Compensations | O&M | 1.4.5 | If the annual measured PR falls below the guaranteed PR value according to Table 1.4.1, the liquidated damages will be levied on the successful Bidder at the rate of USD 0.20-per-kWh or the kWh Value the Employer receives for each kWh of shortfall – whichever is higher. Adjustments shall be made for any events outside the control of the O&M operator as grid outages, from grid operator ordered shutdowns, or force majeure events during the year. | 2 |  |  |  | 1 |  |  | Cannot be evaluated at this stage. Only to be checked in list of deviations. | Only to be checked in list of deviations. |  |  | 1 |  | Open
Tbea | GD | PR and System Performance Guarantee | Compensations | O&M | 1.4.5 | In case the PR is higher than the guaranteed PR value, the net value of this excess energy will be shared as follows: 50% towards the asset replacement fund, 25% towards the Employer, 25% towards the O&M contractor | 3 |  |  |  | 1 |  |  | Cannot be evaluated at this stage. Only to be checked in list of deviations. |  |  |  | 1 |  | Open
Tbea | GD | PR and System Performance Guarantee | Compensations | System PR | 1.4.4 | If the measured PR within further 30 days does not reach the guaranteed PR, the Employer can demand that the price of the system will be reduced by the percentage of shortfall times 1.2 for liquidated damages or the contractor will have to install more power at its own cost or combination of both. | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  | Cannot be evaluated at this stage. Only to be checked in list of deviations. |  |  |  | 1 | 1 | Open
Tbea | GD | PR and System Performance Guarantee | Compensations | System PR | 1.4.4 | The successful Bidder shall conduct the initial PR test for the daylight hours of at least 30 consecutive days, recording data at a frequency of fifteen minute intervals or less, to validate the guaranteed PR value for acceptance. Any excused downtime (e.g., from Grid Operator ordered shutdowns, grid failure, theft, force majeure) will be excluded from that calculation by an independent consultant (Auditing Body). That day will be taken out and another day added, if the initial PR falls short of the guaranteed PR value, the successful Bidder shall be obliged to identify and rectify the causes for the performance shortfall at their own cost. | 2 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  | Cannot be evaluated at this stage. Only to be checked in list of deviations. |  |  |  | 1 |  | Open
Tbea | GD | Conditions for Disqualification and Additional Information Required | Credentials | EPC | 1.2.6 | Approval from bidder to owners or owner representatives to answer questions freely regarding the past performance of the bidder and performance of the system against contractual obligations. | 2 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | [5 empty] | 1 |  | Open
Tbea | GD | Conditions for Disqualification and Additional Information Required | Credentials | EPC | 1.2.6 | Cumulative MWp of ground mounted PV turnkey installations >5 MWp with stating of actual MWp per project, project location, date of commissioning, module type and Inverter type. | 1 |  | 1 | [5 empty] | experience of Bidder / EPC |  |  | 1 | 1 | Pass
Tbea | GD | Conditions for Disqualification and Additional Information Required | Credentials | EPC | 1.2.6 | Detailed list of all the sites with the affirmation that the bidder played the leading EPC role in the turnkey installation of these systems. | 3 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | GD | Conditions for Disqualification and Additional Information Required | Credentials | EPC | 1.2.6 | References and contact data (mail and phone) from owners of all installations > 5 MW with quotes of the corresponding system Performance Ratios, as well as system performance vs. initial yield assessment per year since the installation. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  | for selection of referenz objects |  |  | 1 | 1 | Open
Tbea | GD | Technical Bid Evaluation Criteria | Credentials | EPC | 1.3.1 | the systems have been completed on time and within budget, | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | [5 empty] | 1 | 1 | Open
Tbea | GD | Scope of the Bid | Credentials | EPC | 1.1.9 | The bid includes professional experience of the Bidders in ground mounted utility-scale PV and financial information about their long-term stability | 3 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | GD | Scope of the Bid | Credentials | EPC | 1.1.10 | The Bidder, or the Lead company in case of JV is a EPC contractor | 1 |  | 1 |  |  |  |  | This is a non-technical question. We suggest such question should be separated from technical questions and placed in checklist for "General/Substantive Responsiveness of Bid" | a question of reliability and experience of solid understanding of the task/System Technology. See also 1.1.10 |  |  | 1 |  | Pass
Tbea | GD | Technical Bid Evaluation Criteria | Credentials | Guarantees | 1.3.1 | To have met the contractual requirements of the EPC and O&M deliverables including certificate to the effect that the entire equipment is brand new as required vide notification number NEPRA/UTS-01/777-779 dated Jan 21 ,2014, | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Only to be checked in list of deviations. |  |  |  | 1 | 1 | Open
Tbea | GD | Technical Bid Evaluation Criteria | Credentials | O&M | 1.3.1 | In case of a non-performance, comprehensible evidence has to be given why this case will not affect this project. | 3 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | [5 empty] | 1 |  | Open
Tbea | GD | Technical Bid Evaluation Criteria | Credentials | O&M | 1.3.1 | that they have started supplying electricity to the grid and are still operating satisfactorily in 9 out of 10 MW for all the cases | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | [5 empty] | 1 | 1 | Open
Tbea | GD | Conditions for Disqualification and Additional Information Required | Credentials | O&M | 1.2.6 | Cumulative MWp of ground mounted PV installations for which O&M services have been delivered by the bidder or his O&M subcontractor. | 2 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | [5 empty] | 1 |  | Open
Tbea | GD | Technical Bid Evaluation Criteria | Credentials | O&M | 1.3.2 | Prove at least 100 MW of EPC experience and 50 MW of full O&M experience for a period longer than 24 months. | 1 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | GD | Conditions for Disqualification and Additional Information Required | Credentials | O&M | 1.2.6 | References, contact data and approval from owners or owner representatives of all installations > 5 MW from bidder or his O&M subcontractor to answer questions freely regarding the past performance of the bidder and performance of the system against contractual obligations. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | [5 empty] | 1 | 1 | Open
Tbea | MAW | Modules | Credentials | Project references | 1.14.8 | To show the proven technology a minimum of 500MW of proposed product type series must be in operation and reference projects shall be named. | 1 | page 458 |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | many plants with 10-50MWp were realized, but with same proven technology? | Related to project references |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Tbea | MAW | Inverters | Credentials | Project references | 1.18.10 | A minimum of 100 MWp of similar product/type must be in operation and reference projects shall be named. | 1 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | MAW | DC Cables | DC Cables | Design factors to be provided | 1.15.2 | String cable shall be of the following type: single conductor type, copper, 1000 V / Class II (according to protection class II / 1000V, IEC 61140, single core cable, tinned copper conductor, XLPE Insulation, double EVA jacket (resistant to heat and cold, resistant to ozone, UV, oil and chemicals), Temperature: 90 º C (Temperature Max. Allowable: 120 º C), Halogen free | 1 |  |  |  | 1 |  |  | It should be in accordance with the inverter values. | possibly 1500V for such system design | C |  | 1 |  | Open
Tbea | MAW | DC Cables | DC Cables | Design factors to be provided | 1.15.2 | Balance of electrical potential | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Need to be disscussed | equipotential bonding earthing mesh | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Tbea | MAW | DC Cables | DC Cables | Design factors to be provided | 1.15.2 | Clear and systematic labelling required | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Tbea | MAW | DC Cables | DC Cables | Design factors to be provided | 1.15.2 | Connectors of Modules and string cables shall be connected of self-locking type, have IP65 rating and shall be from same manufacturer and type | 1 |  |  |  | 1 | Unclear: We do not understand your proposal, please detail your proposal. Especially confirm that you are compliant with our requested criteria. |  |  |  | C |  | 1 |  | Open
Tbea | MAW | DC Cables | DC Cables | Design factors to be provided | 1.15.2 | Installation to be verified by measurement-protocols | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Cannot be evaluated at this stage. | blanc protocol | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Tbea | MAW | DC Cables | DC Cables | Design factors to be provided | 1.15.2 | Lifetime of 30 years is assured | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | What proof is required. | Life time test of nonmetal materials IEC 60811-408:2012 / (DIN EN 60811-408; VDE 0473-811-408:2012-12) 30 y assurance never seen until today | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Tbea | MAW | DC Cables | DC Cables | Design factors to be provided | 1.15.2 | Sizing of cables shall be specified according to the number of modules and strings per array | 1 |  | 1 | [5 empty] | voltage drop calculation |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | 1 |  | Pass
Tbea | MAW | DC Cables | DC Cables | Design factors to be provided | 1.15.2 | The DC main (downstream of combiner box) wiring harness shall have the quality: Aluminum / Copper / 1000 V / Class II | 1 |  |  |  | 1 |  |  | It should be in accordance with the inverter values. | possibly 1500V for such system design | C |  | 1 |  | Open
Tbea | MAW | DC Cables | DC Cables | Specific Requirements | 1.15.1 | Are Ohmic losses less than 1% at full power? | 1 | page 858 |  |  | 1 |  |  |  | DC+AC losses < 2% | C |  | 1 |  | Open
Tbea | MAW | DC Cables | DC Cables | Standards | 1.15.3 | IEC 60364-1 | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | 1 |  | Open
Tbea | MAW | DC Connectors | DC Connectors | Standards | 1.16.2 | EN 50521 | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? | PV Connectors no, just a statement of compliance |  |  | 1 |  | Open
Tbea | MAW | DC Connectors | DC Connectors | Standards | 1.16.2 | IEC 60512 | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? | Connectors E-Systems no, just a statement of compliance |  |  | 1 |  | Open
Tbea | MAW | DC Junction Box | DC Junction Box | Design factors to be provided | 1.17.1 | At least IP54 | 1 |  | 1 |  |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  | DC Junction box is applicable in what conditions? | depending on DC Design |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | 1 |  | Pass
Tbea | MAW | DC Junction Box | DC Junction Box | Design factors to be provided | 1.17.1 | Class 2 DC surge arrestor | 1 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | MAW | DC Junction Box | DC Junction Box | Design factors to be provided | 1.17.1 | DC fuses shall permit up to maximum 1000 V (or 1500V if designed). String box design, including all operating elements shall satisfy safety requirements | 1 |  | 1 |  |  |  |  | Will inverter voltage(1500V) effect the maximum voltage(1000V)? | depends on spec of inverter. |  |  | 1 |  | Pass
Tbea | MAW | DC Junction Box | DC Junction Box | Design factors to be provided | 1.17.1 | Dust and heat protection | 1 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | MAW | DC Junction Box | DC Junction Box | Design factors to be provided | 1.17.1 | Monitored input-couples | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | Monitoring on string level? |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Tbea | MAW | DC Junction Box | DC Junction Box | Specifications | 1.17.2 | Current monitoring | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | Monitoring on string level? |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Tbea | MAW | DC Junction Box | DC Junction Box | Specifications | 1.17.2, 1.17.1 | Monitoring interface for SCADA | 1 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | MAW | DC Junction Box | DC Junction Box | Specifications | 1.17.2 | Touch-safe protective cover | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Tbea | MAW | DC Junction Box | DC Junction Box | Standards | 1.17.3 | EN 50178 | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? | High currat devices no, just a statement of compliance |  |  | 1 |  | Open
Tbea | MAW | DC Junction Box | DC Junction Box | Standards | 1.17.3 | EN 60439-1 | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? | arcing fault / Störlichtbogen Verhalten no, just a statement of compliance |  |  | 1 |  | Open
Tbea | MAW | DC Junction Box | DC Junction Box | Standards | 1.17.3 | EN 61000-6 | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? | EMV no, just a statement of compliance |  |  | 1 |  | Open
Tbea | JBU | Step-up Transformers/MV Switchgear | Due Diligence | Quality Assurance | 1.21.3 | Factory witness testing will be required for MV transformer and switchgear to be installed at this project. The cost of the due diligence to be carried by the Employer through an independent technical consultant will be taken over by the successful bidder up to an amount of 30,000 USD. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Tbea | MAW | Inverters | Due diligence | Quality Assurance | 1.18.12 | The Bidder accepts that the cost of the Quality assurance for Inverters to be carried by the Employer through an independent technical consultant shall be taken over by the successful bidder up to an amount of 100,000 USD. | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  |  |  | C |  | 1 |  | Open
Tbea | MAW | Modules | Due Diligence | Quality Assurance | 1.14.6 | The bidder will bear the cost of the Quality assurance for PV modules on-site and in laboratory to be carried out by the Employer through an independent technical consultant up to 150,000 USD. | 1 | page 93 | 1 | [8 empty] | 1 |  | Pass
Tbea | GD | Technical Bid Evaluation Criteria | Due Diligence | Quality Assurance | 1.3.5 | The cost of the due diligence to be carried out by the Employer through an independent technical consultant before contract signature will be taken over by the successful bidder up to an amount of 50,000 USD independent of the result. The due diligence will cover a module factory visit, an inverter factory inspection and a due diligence on the provided financial, EPC and O&M credentials including up to three site visits. | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  | Only to be checked in list of deviations. |  |  |  | 1 |  | Open
Tbea | GD | Scope of the Bid | General items | Guarantees | 1.1.5 | Energy Purchase Agreement (EPA) practices are followed | 1 |  |  |  | 1 | Important reasons: due to current uncertainty of the criteria we accept an open status. Please clarify that yo acknowledge the criteria and comply unless a reason of high importance will not allow you you to comply. In such a situation the parties will seek to agree a compromise. |  | This cannot be evaluated at this stage. | we need a sentence that it should and can only be disregarded for important reasons |  |  | 1 |  | Open
Tbea | JBS | Labelling | General items | Labelling | 1.26 | the ID numbering / coding system shall allow unique identification of all components and be understandable | 1 |  |  |  | 1 | General understanding: expressions like "shall", "shall be supplied with", "has to be", "must be" have the meaning of "will be delivered"? Please confirm. |  | Cannot be evaluated at this stage |  | G | General understanding: expressions like "shall", "shall be supplied with", "has to be", "must be" have the meaning of "will be delivered"? Please confirm. | 1 |  | Open
Tbea | JBS | Labelling | General items | Labelling | 1.26 | Tags shall be weather and UV resistant. | 1 |  |  |  | 1 | General understanding: expressions like "shall", "shall be supplied with", "has to be", "must be" have the meaning of "will be delivered"? Please confirm. |  | Cannot be evaluated at this stage |  | G | General understanding: expressions like "shall", "shall be supplied with", "has to be", "must be" have the meaning of "will be delivered"? Please confirm. | 1 |  | Open
Tbea | JBS | Labelling | General items | Labelling | 1.26 | The ID’s shall correspond to all drawings, plant documentation and control system. | 1 |  |  |  | 1 | General understanding: expressions like "shall", "shall be supplied with", "has to be", "must be" have the meaning of "will be delivered"? Please confirm. |  | Cannot be evaluated at this stage |  | G | General understanding: expressions like "shall", "shall be supplied with", "has to be", "must be" have the meaning of "will be delivered"? Please confirm. | 1 |  | Open
Tbea | GD | Scope of the Bid | General items | Quality Assurance | 1.1.3 | Defect components consequences: If one tested sample fails in one criterion, all items of the same category will be regarded as failed and rejected. | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  | Only to be checked in list of deviations. | yes, we need to be sure that they comply as for most of the critera |  |  | 1 | 1 | Open
Tbea | GD | Scope of the Bid | General items | Specific Requirements | 1.1.2 | The Offer shall include a list of all vendors and/or sub-contractors for major equipment. | 1 |  |  |  | 1 | [6 empty] | 1 |  | Open
Tbea | GD | Scope of the Bid | General items | Specific Requirements | 1.1.9 | The bid covers the planning of the System design, the required functionality of the System in terms of its sub-systems and components, detailed feature-wise descriptions of the components to be used in the System, the planning of the System installation, its integration, testing, monitoring, commissioning and O&M of the System | 1 |  |  |  | 1 | We can not find all of the requested criteria in your documents. Please confirm that your bid is compliant with all expectations and requirements of Section 6 of the RFP and provide a list with ALL exeptions or alterations. This applies to both, the EOPC And the O&M part. |  | This question should be removed as detailed design of every component/sub-system will be checked and evaluated thoroughly in technical evaluation | no, its an overall critera an need to be met |  |  | 1 | 1 | Open
Tbea | JBS | Basic Scope of Supply | General items | Specific Requirements | 1.6 | The maximum DC voltage shall not exceed 1500 V | 1 |  | 1 |  |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | [5 empty] | 1 |  | Pass
Tbea | JBS | Basic Scope of Supply | General items | Specific Requirements | 1.6 | The required AC voltage / frequency at grid connection shall 132 kV/50 Hz | 1 |  | 1 |  |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | [5 empty] | 1 |  | Pass
Tbea | JBS | Equipment guarantees | Inverter | Guarantees | 1.28.2 | The Successful Bidder shall provide an Inverter warranty of at least 5 years. A spare parts warranty shall be included for the 25 years operational period. | 1 |  |  |  | 1 | General understanding: expressions like "shall", "shall be supplied with", "has to be", "must be" have the meaning of "will be delivered"? Please confirm. |  |  |  | G | General understanding: expressions like "shall", "shall be supplied with", "has to be", "must be" have the meaning of "will be delivered"? Please confirm. | 1 |  | Open
Tbea | JBU | Inverter/Transformer Station | Inverter/Transformer Station | Specific Requirements | 1.22 | All stations shall be equipped with fire and smoke detectors and alarm, connected to security and surveillance system | 1 |  |  |  | 1 | General understanding: expressions like "shall", "shall be supplied with", "has to be", "must be" have the meaning of "will be delivered"? Please confirm. |  |  |  | G | General understanding: expressions like "shall", "shall be supplied with", "has to be", "must be" have the meaning of "will be delivered"? Please confirm. | 1 |  | Open
Tbea | JBU | Inverter/Transformer Station | Inverter/Transformer Station | Specific Requirements | 1.22 | Bidder shall firmly specify the number of stations, manufacturer, capacity and type of equipment. | 1 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | JBU | Inverter/Transformer Station | Inverter/Transformer Station | Specific Requirements | 1.22 | Every ten (10) or lesser number of stations shall be equipped with an earthing and short-circuiting equipment | 1 |  |  |  | 1 | General understanding: expressions like "shall", "shall be supplied with", "has to be", "must be" have the meaning of "will be delivered"? Please confirm. |  |  |  | G | General understanding: expressions like "shall", "shall be supplied with", "has to be", "must be" have the meaning of "will be delivered"? Please confirm. | 1 |  | Open
Tbea | JBU | Inverter/Transformer Station | Inverter/Transformer Station | Specific Requirements | 1.22 | Fine sand filters shall be installed | 1 |  |  |  | 1 | General understanding: expressions like "shall", "shall be supplied with", "has to be", "must be" have the meaning of "will be delivered"? Please confirm. |  |  |  | G | General understanding: expressions like "shall", "shall be supplied with", "has to be", "must be" have the meaning of "will be delivered"? Please confirm. | 1 |  | Open
Tbea | JBU | Inverter/Transformer Station | Inverter/Transformer Station | Specific Requirements | 1.22 | The station shall enable the grounding of hardware and neutral will be left ground isolated | 1 |  |  |  | 1 | General understanding: expressions like "shall", "shall be supplied with", "has to be", "must be" have the meaning of "will be delivered"? Please confirm. |  |  |  | G | General understanding: expressions like "shall", "shall be supplied with", "has to be", "must be" have the meaning of "will be delivered"? Please confirm. | 1 |  | Open
Tbea | MAW | Inverters | Inverters | Design factors to be provided | 1.18.7 | Cooling method | 1 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | MAW | Inverters | Inverters | Design factors to be provided | 1.18.7 | Detection of insulation faults | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | [5 empty] | 1 |  | Open
Tbea | MAW | Inverters | Inverters | Design factors to be provided | 1.18.7 | Input voltage range (The voltage window for MPP tracking shall accommodate the expected degradation of the modules.) | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Tbea | MAW | Inverters | Inverters | Design factors to be provided | 1.18.7 | Integrated transformer/transformerless / Outside Dry Type Transformer | 1 |  | 1 |  |  |  | transformerless |  |  |  |  | 1 |  | Pass
Tbea | MAW | Inverters | Inverters | Design factors to be provided | 1.18.7 | Maximum output current | 1 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | MAW | Inverters | Inverters | Design factors to be provided | 1.18.7 | Nominal output frequency, 3-phase | 1 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | MAW | Inverters | Inverters | Design factors to be provided | 1.18.7 | Nominal output voltage | 1 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | MAW | Inverters | Inverters | Design factors to be provided | 1.18.7 | Nominal power | 1 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | MAW | Inverters | Inverters | Design factors to be provided | 1.18.7 | Operating temperature range | 1 |  | 1 |  |  |  |  | What is the acceptable range? | 60°C Derating? |  |  | 1 |  | Pass
Tbea | MAW | Inverters | Inverters | Design factors to be provided | 1.18.7 | Output voltage range | 1 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | MAW | Inverters | Inverters | Design factors to be provided | 1.18.7 | Peak efficiency/ Weighted efficiency | 1 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | MAW | Inverters | Inverters | Design factors to be provided | 1.18.7 | Protection rating: NEMA 3R, IP54/IP55/IP60 | 1 |  | 1 |  |  | Unclear: We do not understand your proposal, please detail your proposal. Especially confirm that you are compliant with our requested criteria. | IP54 |  |  |  |  | 1 |  | Pass
Tbea | MAW | Inverters | Inverters | Design factors to be provided | 1.18.7 | PV array configuration options: positive ground, negative ground | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Tbea | MAW | Inverters | Inverters | Functionalities | 1.18.3 | Active power control reduction: remotely set point of control in case of network congestions or risk of system collapse, if deemed necessary | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | 8.2 needs to ensure these questions are answered in the bids. |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Tbea | MAW | Inverters | Inverters | Functionalities | 1.18.3 | Anti-islanding protection | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Tbea | MAW | Inverters | Inverters | Functionalities | 1.18.3 | Frequency regulation | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | 8.2 needs to ensure these questions are answered in the bids. |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Tbea | MAW | Inverters | Inverters | Functionalities | 1.18.3 | Limitation of voltage fluctuation due to switching operations and long-term flicker | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | 8.2 needs to ensure these questions are answered in the bids. |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Tbea | MAW | Inverters | Inverters | Functionalities | 1.18.3 | Limitation of current harmonics and higher frequency components up to 9 kHz | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Tbea | MAW | Inverters | Inverters | Functionalities | 1.18.3 | Limitation of short-circuit current | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | 8.2 needs to ensure these questions are answered in the bids. |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Tbea | MAW | Inverters | Inverters | Functionalities | 1.18.3 | Limitation of steady-stage voltage changes to 2% of the nominal value | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Tbea | MAW | Inverters | Inverters | Functionalities | 1.18.3 | Matching grid voltage and frequency at point-of-coupling | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Tbea | MAW | Inverters | Inverters | Functionalities | 1.18.3 | Maximum Power Point Tracking (MPPT) and string/sub-array management | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Tbea | MAW | Inverters | Inverters | Functionalities | 1.18.3 | Voltage and frequency fault ride-through: no disconnection of the connection through voltage dip and change of active power generation, feed-in of reactive power during the fault for voltage stabilisation | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | 8.2 needs to ensure these questions are answered in the bids. |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Tbea | MAW | Inverters | Inverters | Functionalities | 1.18.3 | Voltage regulation through reactive power support: remotely set point control for voltage stability | 1 |  | 1 |  |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  | 8.2 needs to ensure these questions are answered in the bids. |  |  |  | 1 |  | Pass
Tbea | MAW | Inverters | Inverters | Manufacturers confirmation | 1.18.9 | The Bidder shall deliver a manufacturer's confirmation in his Bid for the suitability of the inverter for the specific weather conditions applicable in Bahawalpur Pakistan. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Tbea | MAW | Inverters | Inverters | Quality Assurance | 1.18.11 | After commissioning, 1 of 10 inverters will be measured on site (power curve and efficiency) by an approved independent technical consultant on behalf of the Employer. The on-site measurements shall be accepted by the Bidder as average values for all inverters | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  | Cannot be evaluated at this stage | compliance! | C |  | 1 |  | Open
Tbea | MAW | Inverters | Inverters | Quality Assurance | 1.18.11 | Check of protection against overload, short-circuit, grid-failure, internal failure, over-temperature (de-rating), surge protection, detection of insulation faults of AC Cables. Bidder shall firmly specify the manufacturer, types and length of cables to be installed | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | shall? | 8.2 needs to ensure these questions are answered in the bids. |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Tbea | MAW | Inverters | Inverters | Quality Assurance | 1.18.11 | Test run and check of MPP tracking of all inverters | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | shall? | 8.2 needs to ensure these questions are answered in the bids. |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Tbea | MAW | Inverters | Inverters | Quality Assurance | 1.18.11 | Test run in the field for maximum and EU-efficiency of all Inverters | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | shall? | 8.2 needs to ensure these questions are answered in the bids. |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Tbea | MAW | Inverters | Inverters | Quality Assurance | 1.18.11 | The Bidder shall deliver detailed protocols of performance test run (warm power test) for every single inverter | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | shall? | Cannot be evaluated at this stage |  | C |  | 1 |  | Open
Tbea | MAW | Inverters | Inverters | Specific Requirements | 1.18.6 | Specifications of table in Schedule C shall be met | 1 |  | 1 |  |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  | Link to table |  |  |  | 1 |  | Pass
Tbea | MAW | Inverters | Inverters | Standards | 1.18.8 | IEEE 1547 | 1 |  | 1 |  |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? | no, just a statement of compliance Interconnecting Distributed Resources |  |  | 1 |  | Pass
Tbea | MAW | Inverters | Inverters | Standards | 1.18.8 | TUV, VDE, or equivalent certification of passing the relevant standards | 1 |  | 1 |  |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | [5 empty] | 1 |  | Pass
Tbea | MAW | Inverters | Inverters | Strategic Reason for Inverter Selection | 1.18.2 | Available uptime | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us | [5 empty] | 1 |  | Open
Tbea | MAW | Inverters | Inverters | Strategic Reason for Inverter Selection | 1.18.2 | Balance of System (BOS) costs of inverter and labour | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  | financial bid | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Tbea | MAW | Inverters | Inverters | Strategic Reason for Inverter Selection | 1.18.2 | Concept of protection against overload, short-circuit, grid-failure, internal failure, over-temperature (de-rating), surge protection | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Its too general, needs to be reviewed. | failure codes and consquences (automatic/manual restart, throw away safety devices) | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Tbea | MAW | Inverters | Inverters | Strategic Reason for Inverter Selection | 1.18.2 | Dust and heat protection | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  | derating? | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Tbea | MAW | Inverters | Inverters | Strategic Reason for Inverter Selection | 1.18.2 | Timely and effective monitoring at a granular/zoomed-in level | 1 |  |  |  | 1 |  |  |  |  | C | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | 1 |  | Open
Tbea | GD | Scope of the Bid | Layout | Guarantees | 1.1.6 | The bidder confirms that the system complies with all applicable requirements of the NEPRA Grid Code of Pakistan and its Draft Amendment no. 2 for Solar Power Projects. | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  | Only to be checked in list of deviations. |  |  |  | 1 |  | Open
Tbea | JBS | Physical layout | Layout | Specific Requirements | 1.7.2 | Provide a schematic electrical Single Line Diagram (SLD) of the entire System layout from the modules to the grid-connection, identifying and listing all of the following DC and AC components. | 1 | page 85 | 1 | [8 empty] | 1 |  | Pass
Tbea | JBS | Physical layout | Layout | Specific Requirements | 1.7.2 | The system design shall be such as to ensure ease of maintenance and a multiple ring main unit (RMU) philosophy (on MV level) must be followed for circuit breaker configuration. | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  |  |  | U |  | 1 |  | Open
Tbea | MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Bills of Materials, BoMs: (glass, encapsulant, backsheet, ribbon, adhesives, cable, junction box, connector) | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Tbea | MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Current at the maximum current point | 1 | page 840 | 1 | [8 empty] | 1 |  | Pass
Tbea | MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Degradation Curve from Manufacturer | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Tbea | MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Manufacturers confirmation for the suitability of module for specific weather conditions and the high UV-radiation | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  | especially reliability at high UV irridiance / Product warranty | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Tbea | MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Manufacturers installation guidelines | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Tbea | MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Materials and workmanship warranty of a minimum of 10 years | 1 | page 840 | 1 | [8 empty] | 1 |  | Pass
Tbea | MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Maximum rated power | 1 | page 840 | 1 | [8 empty] | 1 |  | Pass
Tbea | MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Maximum system voltage | 1 | page 840 | 1 | [5 empty] | … at SK-II safety class |  |  | 1 |  | Pass
Tbea | MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Minimum efficiency at 200 W/m² (25°, AM 1.5) | 1 | page 840 | 1 | [8 empty] | 1 |  | Pass
Tbea | MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Open-circuit voltage | 1 | page 840 | 1 | [8 empty] | 1 |  | Pass
Tbea | MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Operating temperature range and nominal operating cell temperature NOCT | 1 | page 840 | 1 |  |  |  |  | What range is acceptable | There is as small range anyway Will result in the PR losses |  |  | 1 |  | Pass
Tbea | MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Power warranty/performance guarantee of a minimum of 25 years: the power output should not fall below 90% within 10 years, and below 80% within 25 years; linear warranty mandatory | 1 | page 840 | 1 | [8 empty] | 1 |  | Pass
Tbea | MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Provide guarantees and data sheets (to be transferred to Employer upon COD) | 1 | page 840 | 1 | [8 empty] | 1 |  | Pass
Tbea | MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Rated power tolerance | 1 | page 840 | 1 | [8 empty] | 1 |  | Pass
Tbea | MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Short-circuit current | 1 | page 840 | 1 | [8 empty] | 1 |  | Pass
Tbea | MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Specify number of modules and total MWp to be provided | 1 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Tolerance to wind (maximum load) impact (mechanical load) | 1 | page 840 | 1 | [5 empty] | minimum 2400 Pa |  |  | 1 |  | Pass
Tbea | MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Type of cells comprising the module, and number of cells in series | 1 | page 840 | 1 | [5 empty] | manufacturer |  |  | 1 |  | Pass
Tbea | MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Voltage at the maximum power point | 1 | page 840 | 1 | [8 empty] | 1 |  | Pass
Tbea | JBS | Equipment guarantees | Modules | Guarantees | 1.28.1 | The Successful bidder shall provide a Module warranty of at least 10 years. The performance warranty of the module shall be linear with a fixed factor over 25 years. | 1 |  |  |  | 1 | General understanding: expressions like "shall", "shall be supplied with", "has to be", "must be" have the meaning of "will be delivered"? Please confirm. |  | To be discussed |  | G | General understanding: expressions like "shall", "shall be supplied with", "has to be", "must be" have the meaning of "will be delivered"? Please confirm. | 1 |  | Open
Tbea | MAW | Modules | Modules | Pre-shipment quality assurance | 1.14.4 | All modules must undergo Electroluminiscense (EL) inspection with a resolution of minimum 4 MPixel prior to shipment. | 1 | page 93 |  |  | 1 |  |  | Cannot be evaluated at this stage. | compliance necessary | C |  | 1 |  | Open
Tbea | MAW | Modules | Modules | Pre-shipment quality assurance | 1.14.7 | Warranties and evidence shall be given by the bidder that their selected modules have been tested for susceptibility to Potential Induced Degradation (PID). | 1 | page 93 |  |  | 1 | Unclear: We do not understand your proposal, please detail your proposal. Especially confirm that you are compliant with our requested criteria. |  |  |  | C |  | 1 |  | Open
Tbea | MAW | Modules | Modules | Pre-shipment quality assurance | 1.14.4 | A sufficient EVA cross linking has to be verified per production line through a gel content test supervised by an accredited (IEC 17025 or national pendant) independent certified module testing agency. | 1 | page 93 |  |  | 1 |  |  | Cannot be evaluated at this stage. | compliance necessary | C |  | 1 |  | Open
Tbea | MAW | Modules | Modules | Pre-shipment quality assurance | 1.14.4 | Pre-shipment flash tested data Quality assurance for PV modules on-site and in laboratory simulator must meet the class AAA requirements of IEC 60904-9. The sun simulator must be calibrated with a reference cell, which itself was calibrated by a member of the WPVS scheme, with a maximum uncertainty of Isc of 1%. unique barcode (SNr) and labelled performance headlines (P(mpp), I(sc), U(oc), I(mpp), U(mpp) maximum current, maximum voltage Positive power sorting | 1 | page 93 |  |  | 1 |  |  | Cannot be evaluated at this stage. | compliance necessary | C |  | 1 |  | Open
Tbea | MAW | Modules | Modules | Quality assurance on site | 1.14.5 | The modules shall undergo an incoming inspection at arrival on construction site. | 1 | page 93 |  |  | 1 |  |  | Cannot be evaluated at this stage. | stated and accepted | C |  | 1 |  | Open
Tbea | MAW | Modules | Modules | Standards (as applicable to crystalline silicion or thin-film) | 1.14.3 | IEC 60364-4-41 | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? | no, just a statement of compliance 'protection against electric shock | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Tbea | MAW | Modules | Modules | Standards (as applicable to crystalline silicion or thin-film) | 1.14.3 | IEC 60904-1, IEC 60904-3 | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? | no, just a statement of compliance | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Tbea | MAW | Modules | Modules | Standards (as applicable to crystalline silicion or thin-film) | 1.14.3 | IEC 61215 | 1 |  | 1 |  |  |  |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? | no, just a statement of compliance |  |  | 1 |  | Pass
Tbea | MAW | Modules | Modules | Standards (as applicable to crystalline silicion or thin-film) | 1.14.3 | IEC 61416 | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? | not existing | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Tbea | MAW | Modules | Modules | Standards (as applicable to crystalline silicion or thin-film) | 1.14.3 | IEC 61646 | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? | no, just a statement of compliance | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Tbea | MAW | Modules | Modules | Standards (as applicable to crystalline silicion or thin-film) | 1.14.3 | IEC 61701 | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? | no, just a statement of compliance | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Tbea | MAW | Modules | Modules | Standards (as applicable to crystalline silicion or thin-film) | 1.14.3 | IEC 61730 | 1 |  | 1 |  |  |  |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? | no, just a statement of compliance |  |  | 1 |  | Pass
Tbea | MAW | Inverters | Monitoring | Functionalities | 1.18.3 | Advanced communication, with intelligent alerts/warnings, to the SCADA server | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Tbea | JBS | Equipment guarantees | Mounting | Guarantees | 1.28.3 | The Successful Bidder shall provide a product warranty for the structure of at least 10 years. | 1 |  |  |  | 1 | General understanding: expressions like "shall", "shall be supplied with", "has to be", "must be" have the meaning of "will be delivered"? Please confirm. |  |  |  | G | General understanding: expressions like "shall", "shall be supplied with", "has to be", "must be" have the meaning of "will be delivered"? Please confirm. | 1 |  | Open
Tbea | RM | Mounting | Mounting | Specific Requirements | 1.13.8 | The mounting structures must be earthed | 1 |  |  |  | 1 | We cant find the information in the Bid. Please provide Location TBEA-12/11 is only catodic protection | [5 empty] | 1 |  | Open
Tbea | RM | Mounting | Mounting | Specific Requirements | 1.13.1 | The system is fixed-tilted. Tilt angle is specified. | 1 |  | 1 |  |  |  | S.89 29° - 30° south |  |  |  |  | 1 |  | Pass
Tbea | RM | Mounting | Mounting | Specific Requirements | 1.13.5 | All fastening structures must be verified for durability and resistance to environmental degradation for 25 years | 1 |  | 1 |  |  | "Applicable construction codes" not mentioned in TBEA-12 / 8… Please add. |  | What sort of mechanism is required for verification? | Sub structure description / materials double to line 172 - 175 |  |  | 1 |  | Pass
Tbea | RM | Mounting | Mounting | Specific Requirements | 1.13.3 | Mounting structure is made of durable material, resistant to sandstorms and compatible with the module frame material so as to avoid any adverse electrolytic/galvanic effects. | 1 |  | 1 |  |  |  |  | Information about materials to be known before evaluation. | right |  |  | 1 |  | Pass
Tbea | RM | Mounting | Mounting | Specific Requirements | 1.13.3 | Mounting system resists corrosion (passing the salt spray test IEC 61701, among other verification), | 1 |  | 1 |  |  |  |  | Information about materials to be known before evaluation. | right |  |  | 1 |  | Pass
Tbea | RM | Mounting | Mounting | Specific Requirements | 1.13.3 | Mounting system resists high wind speeds (up to 40 m/s) | 1 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | RM | Mounting | Mounting | Specific Requirements | 1.13.3 | Mounting system resists UV induced degradation | 1 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | RM | Mounting | Mounting | Specific Requirements | 1.13.9 | Specific site conditions have been considered. | 1 |  |  |  | 1 | Please confirm that at minimum IEC stadards are fullfilled |  | Needs to be discussed. | … specific requirements of the soil conditions Static |  |  | 1 |  | Open
Tbea | JBU | Step-up Transformers/MV Switchgear | MV Switchgear | Design factors to be provided | 1.21.4 | Rated lightning impulse voltage | 1 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | JBU | Step-up Transformers/MV Switchgear | MV Switchgear | Design factors to be provided | 1.21.4 | Rated power frequency withstand voltage | 1 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | JBU | Step-up Transformers/MV Switchgear | MV Switchgear | Design factors to be provided | 1.21.4 | Rated short circuit current | 1 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | JBU | Step-up Transformers/MV Switchgear | MV Switchgear | Design factors to be provided | 1.21.4 | System maximum voltage | 1 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | JBU | Step-up Transformers/MV Switchgear | MV Switchgear | Design factors to be provided | 1.21.4 | System nominal voltage | 1 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | JBU | Step-up Transformers/MV Switchgear | MV Switchgear | Specific Requirements | 1.21.4 | Interlocks will also be mechanically interlocked between line MV switchgears. | 1 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | JBU | Step-up Transformers/MV Switchgear | MV Switchgear | Specific Requirements | 1.21.4 | MV Switchgears shall be SF6 gas insulated or VCB (Vacuum circuit breaker). | 1 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | JBU | Step-up Transformers/MV Switchgear | MV Switchgear | Specific Requirements | 1.21.4 | The separating equipment shall be installed with visible disconnection (pivotable disconnectors). | 1 |  | 1 |  |  |  |  | Cannot be evaluated at this stage |  |  |  | 1 |  | Pass
Tbea | JBU | Step-up Transformers/MV Switchgear | MV Switchgear | Standards | 1.21.5 | IEC 60529 | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  | C |  | 1 |  | Open
Tbea | JBU | Step-up Transformers/MV Switchgear | MV Switchgear | Standards | 1.21.5 | IEC 62271-200 | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  | C |  | 1 |  | Open
Tbea | JBU | Step-up Transformers/MV Switchgear | MV Switchgear | Standards | 1.21.5 | IEC 62446 | 1 |  | 1 |  |  |  |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  |  |  | 1 |  | Pass
Tbea | JUE | Deactivation | O&M | Allowed deactivation periods | 2.6.1 | Approved by The Employer to ensure consideration of Employer's obligations | 2 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | JUE | Deactivation | O&M | Allowed deactivation periods | 2.6.1 | Approved from grid operator | 2 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | JUE | Deactivation | O&M | Allowed deactivation periods | 2.6.1 | Times with irradiation level < 300 W/m² | 2 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | JUE | Main Annual Inspection | O&M | Auxiliary system | 2.4.5 | If existing: inspection of requirements out of the building permit | 2 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | JUE | Main Annual Inspection | O&M | Auxiliary system | 2.4.5 | Inspection of security system inclusive fence, all gates, all cameras etc. Random test of the fence fastening, if necessary retightening of the screws | 2 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | JUE | Main Annual Inspection | O&M | Auxiliary system | 2.4.5 | Maintenance of all components according to manufacturer instruction | 1 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | JUE | Initial Inspection | O&M | General Requirements | 2.2.2 | Maintenance routines, inspection check-lists, working files, | 1 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | JUE | Scope of the Bid | O&M | General Requirements | 2.1.2 | Cleaning of Modules and irradiation sensors to prevent dust accumulation to undesirable level. | 1 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | JUE | Scope of the Bid | O&M | General Requirements | 2.1.2 | Cleaning of the Plant, preventive and corrective maintenance of the civil works and the fences. | 1 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | JUE | Initial Inspection | O&M | General Requirements | 2.2.3 | coordinate with the Employer and keep him updated regarding his progress of preparation, status of construction, pending issues of Construction, Commissioning and testing. | 2 |  | 1 |  |  |  | Cannot be evaluated at this stage |  |  |  |  | 1 |  | Pass
Tbea | JUE | Scope of the Bid | O&M | General Requirements | 2.1.2 | Coordination and compliance with NTDC requirements | 1 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | JUE | Scope of the Bid | O&M | General Requirements | 2.1.2 | Corrective maintenance with guaranteed response times | 1 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | JUE | Scope of the Bid | O&M | General Requirements | 2.1.2 | Daily, monthly and yearly performance and production reporting | 1 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | JUE | Initial Inspection | O&M | General Requirements | 2.2.1 | familiarize himself with the specific plant equipment and specific maintenance requirements / training of staff | 1 |  |  |  | 1 | first criteria / sentence is missing. | [5 empty] | 1 |  | Open
Tbea | JUE | Scope of the Bid | O&M | General Requirements | 2.1.2 | Insuring products at different levels but for sensible costs; the insurance policy shall not become expensive compared to the replacement cost of the item | 3 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | JUE | Scope of the Bid | O&M | General Requirements | 2.1.2 | Maintaining a customer support hotline for the Employer/NTDC | 3 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | JUE | Scope of the Bid | O&M | General Requirements | 2.1.2 | Maintaining adequate reserves for timely replacement | 2 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | JUE | Scope of the Bid | O&M | General Requirements | 2.1.2 | Negotiating a warranty reserve for replacements with the suppliers | 3 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | JUE | Scope of the Bid | O&M | General Requirements | 2.1.2 | On site Security services. | 3 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | JUE | Scope of the Bid | O&M | General Requirements | 2.1.2 | Operation of the Plant (including 24/7 presence of O&M and security staff on the project site). | 1 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | JUE | Scope of the Bid | O&M | General Requirements | 2.1.2 | Optimal level of SCADA monitoring | 1 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | JUE | Scope of the Bid | O&M | General Requirements | 2.1.2 | Ordinary road and land maintenance to the extent required for proper maintenance of the Plant. | 3 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | JUE | Scope of the Bid | O&M | General Requirements | 2.1.2 | Performance variance analysis of the module strings and inverters | 1 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | JUE | Scope of the Bid | O&M | General Requirements | 2.1.2 | Periodic maintenance of inverter, transformer, combiner boxes etc., according manufacturer's requirements | 1 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | JUE | Scope of the Bid | O&M | General Requirements | 2.1.2 | Preventive maintenance | 2 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | JUE | Scope of the Bid | O&M | General Requirements | 2.1.2 | Provide all O&M Staff, trained and certified as far as applicable. For security reasons, a 24 h/ 7 days a week staffing of security and maintenance shall be provided. The staffing concept and selected key employees shall be presented to the Employer for approval. | 1 |  |  |  | 1 | Second criteria / sentence is missing. | [5 empty] | 1 |  | Open
Tbea | JUE | Scope of the Bid | O&M | General Requirements | 2.1.2 | Providing regular reports of repairs, maintenance, and tests | 3 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | JUE | Scope of the Bid | O&M | General Requirements | 2.1.2 | Provision and Installation of spare parts, keeping of spare parts stock (refill of used spares). Reporting of status and consumption to be continuously updated | 2 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | JUE | Scope of the Bid | O&M | General Requirements | 2.1.2 | Reporting the monitoring and surveillance system. | 3 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | JUE | Scope of the Bid | O&M | General Requirements | 2.1.2 | Responsibility to keep Performance Ratio and Availability at highest levels | 1 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | JUE | Scope of the Bid | O&M | General Requirements | 2.1.2 | Scheduled maintenance routines: e.g., inspections of modules with polarized sunglasses to check for discolouration, the first signs of de-lamination, loose wires in the electronics, corrosion of mounting structures, erosion | 1 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | JUE | Scope of the Bid | O&M | General Requirements | 2.1.2 | Smooth functioning of all interconnections and data communications of the system performance | 2 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | JUE | Scope of the Bid | O&M | General Requirements | 2.1.2 | Technical report elaboration. | 3 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | JUE | Scope of the Bid | O&M | General Requirements | 2.1.2 | Track chronic negative deviations in the module string output, i.e., power tolerances consistently in the negative | 3 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | JUE | Scope of the Bid | O&M | General Requirements | 2.1.2 | Warranties and insurance policies should be assignable/transferrable to the Employer in case it decides to take over the O&M | 1 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | MAW | Inverters | O&M | Guarantees | 1.18.2 | For central inverters concept: the bidder shall ensure with an undertaking from the manufacturer that the concerned skilled staff will be made available at the site within 24 hours of reporting the defect to the manufacturer. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | Klaus? |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Tbea | JUE | Main Annual Inspection | O&M | Inverter (100%) | 2.4.2 | Check of control and auxiliary voltages | 2 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | JUE | Main Annual Inspection | O&M | Inverter (100%) | 2.4.2 | Check of the safety circuit for the interruption of the AC-grid protection in the case of failure (emergency shut-off, over-/ under-voltage, over temperature, etc.) based on the local conditions | 1 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | JUE | Bi-annual inspection | O&M | Inverter (100%) | 2.3.2 | Cleaning of the filter mats in the air leaks | 2 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | JUE | Main Annual Inspection | O&M | Inverter (100%) | 2.4.2 | Functional check of internal and external over- and under-voltage monitoring through operation of test terminal | 1 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | JUE | Main Annual Inspection | O&M | Inverter (100%) | 2.4.2 | Functional check of insulation monitoring | 1 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | JUE | Bi-annual inspection | O&M | Inverter (100%) | 2.3.2 | Functional check of ventilator system of inverter station | 1 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | JUE | Main Annual Inspection | O&M | Inverter (100%) | 2.4.2 | Inspection of over-voltage protection and upstream fuses regarding external damage | 1 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | JUE | Bi-annual inspection | O&M | Inverter (100%) | 2.3.2 | Inspection of the interior of the electrical cabinet regarding dust deposit, dirtiness, humidity, water penetration from outside. If necessary the cabinet has to be cleaned. | 1 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | JUE | Main Annual Inspection | O&M | Inverter (100%) | 2.4.2 | Maintenance of inverters according to manufacturer instruction | 1 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | JUE | Bi-annual inspection | O&M | Inverter (100%) | 2.3.2 | Maintenance of inverters according to manufacturer's instruction. | 1 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | JUE | Bi-annual inspection | O&M | Inverter (100%) | 2.3.2 | Replacement of dirty filter mats | 2 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | JUE | Main Annual Inspection | O&M | Inverter (100%) | 2.4.2 | Test of the internal miniature circuit breakers and power switch, test of emergency shut-off | 1 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | JUE | Bi-annual inspection | O&M | Inverter (100%) | 2.3.2 | Testing of inverter features according to maintenance schedule of manufacturer. | 1 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | JUE | Main Annual Inspection | O&M | Inverter (100%) | 2.4.2 | Visual inspection of AC and DC clamps regarding tightness and colouring, tightening of clamps | 1 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | JUE | Main Annual Inspection | O&M | Inverter (100%) | 2.4.2 | Visual inspection of all fuses | 1 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | JUE | Bi-annual inspection | O&M | Maintenance | 2.3.3 | Maintenance of all Power plant components according to manufacturer's instructions | 1 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | JUE | Bi-annual inspection | O&M | Monitoring | 2.3.3 | Functionality testing of the monitoring system | 3 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | JUE | Bi-annual inspection | O&M | PV Generator | 2.3.1 | 100% visual inspection of modules regarding damage in spring | 1 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | JUE | Bi-annual inspection | O&M | PV Generator | 2.3.1 | Cleaning of all modules | 1 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | JUE | Bi-annual inspection | O&M | PV Generator | 2.3.1 | Cleaning of sensors and switches | 1 |  | 1 |  |  |  | sensors shall be done by independent Meteo Station Operator |  |  |  |  | 1 |  | Pass
Tbea | JUE | Bi-annual inspection | O&M | PV Generator | 2.3.1 | Documentation of wear and tear of moving components, monitoring of dust intrusion and corrosion. | 2 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | JUE | Main Annual Inspection | O&M | PV Generator | 2.4.1 | Inspection of DC distribution box: Visual inspection of all clamps and degree of pollution. Testing of over-voltage protection | 1 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | JUE | Main Annual Inspection | O&M | PV Generator | 2.4.1 | Maintenance of sensors based on manufacturer’s instructions | 1 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | JUE | Bi-annual inspection | O&M | PV Generator | 2.3.1 | Random check of module clip with respect to loosening; if necessary replacement of clips (min. 10%, documentation of location, during 5 years inspection of whole PV plant) | 2 |  | 1 |  |  |  | Cannot be evaluated at this stage |  |  |  |  | 1 |  | Pass
Tbea | JUE | Bi-annual inspection | O&M | PV Generator | 2.3.1 | Random testing of the steadiness of the mounting foundation/system and random inspection regarding corrosion at substructure (min. 10%, documentation of location, during 10 years inspection of whole PV plant) | 1 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | JUE | Bi-annual inspection | O&M | PV Generator | 2.3.1 | Random visual inspection of modules regarding damage in autumn | 2 |  | 1 |  |  |  | Cannot be evaluated at this stage |  |  |  |  | 1 |  | Pass
Tbea | JUE | Main Annual Inspection | O&M | PV Generator | 2.4.1 | Visual inspection of all accessible cable trenches and cable trays regarding damage | 1 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | JUE | Main Annual Inspection | O&M | PV Generator | 2.4.1 | Visual inspection and random testing of string connector (min. 10% with Documentation of location , during 10 years testing of whole PV plant) | 1 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | JUE | Main Annual Inspection | O&M | Roads | 2.4.3 | Visual inspection of roads within the PV plant shall be carried out to ascertain that these are maintained in good condition for the intended purpose. | 2 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | JUE | On-site monitoring | O&M | Specific Requirements | 2.9.2 | Bidder shall arrange service contracts with specialized sub-contractors | 2 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | JUE | Reaction to Fault Messages / Response Times | O&M | Specific Requirements | 2.11.1 | Every fault message has to be registered in the monitoring software. According to the fault message, the Bidder shall issue a fault diagnosis within a response time of 2 hours (24/7) | 1 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | JUE | Fault Management / Warranty defects | O&M | Specific Requirements | 2.12.5 | Operational defects, which are not considered as warranty defects - see repair works section below | 1 |  |  |  | 1 | rectified at the soonest occasion by TBEA? | Failure Response Time Model not not accepted |  |  |  |  | 1 |  | Open
Tbea | JUE | Fault Calls | O&M | Specific Requirements | 2.13.2 | The minimum response time in case of failure must meet the EPA requirements | 1 |  | 1 |  |  |  | EPA has to accept |  |  |  |  | 1 |  | Pass
Tbea | JUE | Remote Supervision | O&M | Specific Requirements | 2.10.6 | The remote supervision shall also include the taking of measures for removal of faults. | 2 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | JUE | Spare Parts and Tools | O&M | Specific Requirements | 2.14 | provide the necessary set of spare parts and maintenance tools as required to perform the services | 1 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | JUE | Fault Calls | O&M | Specific Requirements | 2.13.2 | --> Time Model: Response Times for Priorities 1-3 (12h / 24h / 1 week) | 1 |  |  |  | 1 | Please clarify compliance with rfp: rectified at the soonest occasion by TBEA? look at 2.12.5 | look at 2.12.5 |  |  |  |  | 1 |  | Open
Tbea | JUE | Fault Management / Warranty defects | O&M | Specific Requirements | 2.12.6 | All defects shall be documented within the same day of detection, | 2 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | JUE | Working Time | O&M | Specific Requirements | 2.17 | All working times of Bidders personnel shall be included in the Bidders annual remuneration. | 1 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | JUE | Deactivation | O&M | Specific Requirements | 2.6.2 | All deactivations during maintenance works shall be completely documented. | 2 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | JUE | On-site monitoring | O&M | Specific Requirements | 2.9.3 | All operational data shall be logged on-site in parallel to the remote data storage | 2 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | JUE | Documentation | O&M | Specific Requirements | 2.19 | All repair works and compensations shall have to be documented and to be submitted to the Employer within two weeks. | 2 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | JUE | Remote Supervision | O&M | Specific Requirements | 2.10.2 | Any reductions in performance shall have to be logged. | 1 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | JUE | Special inspection (every 4 years) | O&M | Specific Requirements | 2.5.1 | Control of station equipment | 2 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | JUE | Performance of maintenance and repair works | O&M | Specific Requirements | 2.8.1 | Corresponding regulations of the respective component manufacturer shall have to be followed during maintenance works | 1 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | JUE | Spare Parts and Tools | O&M | Specific Requirements | 2.14.1 | cover all cost for supply and re-stocking of spare parts from his annual remuneration. | 1 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | JUE | Deactivation | O&M | Specific Requirements | 2.6.3 | Deactivation shall not be considered as permitted downtime. | 2 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | JUE | Performance of maintenance and repair works | O&M | Specific Requirements | 2.8.5 | During his work the Bidder shall be held responsible for the public safety of the PV plant | 2 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | JUE | Approval | O&M | Specific Requirements | 2.18 | Extensive repairs have to be approved by the Employer. | 2 |  |  |  | 1 | please confirm: No exemptions are allowed | [5 empty] | 1 |  | Open
Tbea | JUE | Fault Calls | O&M | Specific Requirements | 2.13.3 | failure time response does not match the response time of EPA >> failure time response does not match the response time of EPA | 3 |  | 1 |  |  |  | EPA has to accept |  |  |  |  | 1 |  | Pass
Tbea | JUE | Fault Calls | O&M | Specific Requirements | 2.13.5 | Fault calls can be performed without prior consent of the Employer. | 3 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | JUE | Fault Management / Warranty defects | O&M | Specific Requirements | 2.12.3 | Fault Management = without repair works | 3 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | JUE | Fault Management / Warranty defects | O&M | Specific Requirements | 2.12.1 | Fault Management: all handling and communication | 2 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | JUE | Fault Management / Warranty defects | O&M | Specific Requirements | 2.12.2 | Fault Management: Handling / correspondence with third parties | 2 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | JUE | Ground Maintenance | O&M | Specific Requirements | 2.21 | Ground maintenance shall include all procedures that are necessary to avoid module shading and an incorrect operation of the trackers. This shall include the levelling of sand drifts. Necessary switching operations shall be coordinated by the Bidder with responsible authorities | 2 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | JUE | Reduced Output of the Plant | O&M | Specific Requirements | 2.15.1 | Identified reduced output shall be justified. Reduced output shall be recovered and liquidated damages determined. | 1 |  | 1 |  |  |  | liquidated --> means --> performance |  |  |  |  | 1 |  | Pass
Tbea | JUE | Fault Calls | O&M | Specific Requirements | 2.13.6 | If the elimination of faults is not possible within the response time / and additional travelling, this is Repair Work | 3 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | JUE | Special inspection (every 4 years) | O&M | Specific Requirements | 2.5.1 | Measurement of inverters and generators according to recognized international standards and according to results from commissioning certificates (insulation, loop resistance, earthing, DC-open circuit voltage) | 2 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | JUE | Remote Supervision | O&M | Specific Requirements | 2.10.8 | Monthly / quarterly and annual reports based on the data of the remote supervision provided to the Employer 4 weeks after the last period of reporting at the latest. | 1 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | JUE | Reduced Output of the Plant | O&M | Specific Requirements | 2.15 | Monthly comparison of the specific performance of all measuring channels among each other. 5% reduced output results in general check of all the channels and shall be documented. | 1 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | JUE | Performance of maintenance and repair works | O&M | Specific Requirements | 2.8.4 | Observe and respect the local law, regulations and international PV standards. | 3 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | JUE | Performance of maintenance and repair works | O&M | Specific Requirements | 2.8.3 | Observe and respect the maintenance and operation specifications of the manufacturer of the components | 3 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | JUE | Special inspection (every 4 years) | O&M | Specific Requirements | 2.5.1 | Oil check of transformers | 1 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | JUE | Remote Supervision | O&M | Specific Requirements | 2.10.1 | On-call service provided for the Employer for availability outside business hours and during weekends (24/7). | 1 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | JUE | On-site monitoring | O&M | Specific Requirements | 2.9.1 | Permanent (24/7) staffing of the Power Plant, consisting of security and O&M personnel. | 1 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | JUE | Fault Management / Warranty defects | O&M | Specific Requirements | 2.12.4 | Product warranties in favour of contractor / Bidder (responsible) to claim all warranties for at least 5 years | 1 |  |  |  | 1 | we cant find the first criteria. please explaine. | the first criteria is missing, please explaine. |  |  |  |  | 1 |  | Open
Tbea | JUE | Reaction to Fault Messages / Response Times | O&M | Specific Requirements | 2.11.2 | profit relevant Fault Events: Downtime registration/ reasons/ repair/ in monthly report (blanc of monthly report?) | 1 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | JUE | Special inspection (every 4 years) | O&M | Specific Requirements | 2.5.1 | Protection systems of medium voltage switching panels of the stations | 1 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | JUE | Spare Parts and Tools | O&M | Specific Requirements | 2.14.2 | refill spare parts immediately after consumption | 2 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | JUE | Repair time and cost | O&M | Specific Requirements | 2.16 | Repair times are considered as part of the availability guaranty of the Bidder. All cost of repair shall be part of the Bidders annual remuneration. For the avoidance of doubt that includes any repairs due to lightening, theft and vandalism. | 1 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | JUE | Performance of maintenance and repair works | O&M | Specific Requirements | 2.8.2 | Report document for maintenance works (blanc sample requiered for bid) | 1 |  |  |  | 1 | blanc sample is missing | [5 empty] | 1 |  | Open
Tbea | JUE | Person in Control of PV plant | O&M | Specific Requirements | 2.22 | The Bidder shall propose an organigram for the O& M personnel with one main responsible | 2 |  |  |  | 1 | "and shall be approved by the Employer. Any replacement or substitute of this person shall be subject to approval by the Employer." we can not find. Please confirm. | [5 empty] | 1 |  | Open
Tbea | JUE | Remote Supervision | O&M | Specific Requirements | 2.10.7 | The Bidder shall provide to the Employer permanent online access to the power plant control system for parallel monitoring | 1 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | JUE | On-site monitoring | O&M | Specific Requirements | 2.9.4 | The data of irradiation sensors shall be monitored by an independent expert on a continuous basis | 2 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | JUE | Remote Supervision | O&M | Specific Requirements | 2.10.4 | The data shall present the status of the plant such as the performance ratio annual overview and the current feed-in power | 2 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | JUE | Fault Calls | O&M | Specific Requirements | 2.13.1 | The scope of service shall include any working times for all fault calls including travelling times and costs. | 1 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | JUE | Reporting | O&M | Specific Requirements | 2.23 | The Bidder shall deliver to the Employer regular reports on monthly, quarterly and annual basis. | 1 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | JUE | Remote Supervision | O&M | Specific Requirements | 2.10.3 | The data will comprise, apart from electrical parameters of the PV plant: currents, voltages, irradiation values, kind and period of reductions in performance such as curtailment by the grid operator | 2 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | JUE | Inspection of Repair Works | O&M | Specific Requirements | 2.20 | The Employer can inspect the repair works within one month (30 days) after receiving the documentation | 2 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | JUE | Fault Calls | O&M | Specific Requirements | 2.13.4 | The fault call shall include the fault diagnosis on site as well as an immediate error correction if possible. The fault shall have to be corrected within the response time and, failing this, a diagnosis of the fault has to be effect indicating further measures. | 2 |  | 1 |  |  | General understanding: expressions like "shall", "shall be supplied with", "has to be", "must be" have the meaning of "will be delivered"? Please confirm. | (shall) have to --> or --> will be corrected? |  |  |  |  | 1 |  | Pass
Tbea | JUE | Remote Supervision | O&M | Specific Requirements | 2.10.9 | The fees for telephone connection and/or data transfer services are included in the annual remuneration. | 2 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | JUE | Remote Supervision | O&M | Specific Requirements | 2.10.5 | The remote supervision shall also control the operation of the PV plant. | 2 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | JUE | Change of Inspection and Maintenance Work procedures | O&M | Specific Requirements | 2.7 | work in accordance with all applicable laws | 2 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | JUE | Main Annual Inspection | O&M | Substation and Transmission Line | 2.4.4 | Maintenance of substation and transmission line according to manufacturer instruction | 1 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | JUE | Main Annual Inspection | O&M | Substation and Transmission Line | 2.4.4 | Visual inspection of transformer and switchboard rooms and cleaning if necessary | 1 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | JUE | Main Annual Inspection | O&M | Substation and Transmission Line | 2.4.4 | Visual inspection of Transmission Line and report of damage to the grid operator | 2 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | JBS | Physical layout | Physical layout plan | Specific Requirements | 1.7.7 | Detailed top view of the PV mounting structure, including module sizes and spacing between the module rows | 1 | page 145/146 | 1 | [8 empty] | 1 |  | Pass
Tbea | JBS | Physical layout | Physical layout plan | Specific Requirements | 1.7.7 | Detailed view of the distribution of inverters and connections to the PV string/array | 1 | page 84 | 1 | [8 empty] | 1 |  | Pass
Tbea | JBS | Physical layout | Physical layout plan | Specific Requirements | 1.7.7 | Detailed side and front view of the PV mounting structure | 1 | page 145/146 | 1 |  |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | [5 empty] | 1 |  | Pass
Tbea | JBS | Physical layout | Physical layout plan | Specific Requirements | 1.7.7 | Detailed top view of electrical cabling interconnections | 1 | page 134 | 1 | [8 empty] | 1 |  | Pass
Tbea | JBS | Physical layout | Physical layout plan | Specific Requirements | 1.7.7 | Floor plans and elevations for all buildings, housing units, containers on site: e.g. , substations, the SCADA operational room, inverters, O&M, storage facilities | 1 | page 1124 | 1 | [8 empty] | 1 |  | Pass
Tbea | JBS | Physical layout | Physical layout plan | Specific Requirements | 1.7.7 | Location of the system metering and grid connection point | 1 | page 85 | 1 |  |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | [5 empty] | 1 |  | Pass
Tbea | JBS | Power plant documentation | Power plant documentation | Quality Assurance | 1.27.1 | Flash report list of all modules shall be provided in digital form. | 1 |  |  |  | 1 | General understanding: expressions like "shall", "shall be supplied with", "has to be", "must be" have the meaning of "will be delivered"? Please confirm. |  |  |  | G | General understanding: expressions like "shall", "shall be supplied with", "has to be", "must be" have the meaning of "will be delivered"? Please confirm. | 1 |  | Open
Tbea | JBS | Power plant documentation | Power plant documentation | Quality Assurance | 1.27.1 | The Bidder shall confirm that the complete as-built documentation of the plant will be provided in compliance with IEC 62446. Additionally all module serial numbers shall be listed with their individual location. | 1 |  |  |  | 1 | General understanding: expressions like "shall", "shall be supplied with", "has to be", "must be" have the meaning of "will be delivered"? Please confirm. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  | G | General understanding: expressions like "shall", "shall be supplied with", "has to be", "must be" have the meaning of "will be delivered"? Please confirm. | 1 |  | Open
Tbea | JBS | Workflow, Project Management Plan and Timelines | Project schedule / Project management | Project schedule | 1.8.1 | Interdependencies between the tasks | 1 | page 44-45 | 1 | [8 empty] | 1 |  | Pass
Tbea | JBS | Workflow, Project Management Plan and Timelines | Project schedule / Project management | Project schedule | 1.8.1 | Interdependencies of tasks with equipment order and delivery times | 1 | page 44-45 | 1 | [8 empty] | 1 |  | Pass
Tbea | JBS | Workflow, Project Management Plan and Timelines | Project schedule / Project management | Project schedule | 1.8.1 | Key milestones to indicate that the progress in on schedule | 1 | page 44-45 | 1 | [8 empty] | 1 |  | Pass
Tbea | JBS | Workflow, Project Management Plan and Timelines | Project schedule / Project management | Project schedule | 1.8.1 | Provide installation schedule in compliance with sub-clause 8.2 of Particular Conditions (Time for Completion is 225 days after Commencement Date). | 1 | page 44-45 | 1 |  |  |  |  | Find sub-clause 8.2 of Particular Conditions |  |  |  | 1 |  | Pass
Tbea | JBS | Workflow, Project Management Plan and Timelines | Project schedule / Project management | Project schedule | 1.8.1 | Provide work breakdown structures, activity decomposition and sequencing and dependability with the baseline schedule clearly showing the critical path | 1 | page 44-45 | 1 | [8 empty] | 1 |  | Pass
Tbea | JBS | Workflow, Project Management Plan and Timelines | Project schedule / Project management | Project schedule | 1.8.1 | Schedule of tasks | 1 | page 44-45 | 1 | [8 empty] | 1 |  | Pass
Tbea | JBS | Workflow, Project Management Plan and Timelines | Project schedule / Project management | Project schedule | 1.8.1 | Teams, the number and skills of personnel to be deployed for each task | 1 | Page 13-41 | 1 | [8 empty] | 1 |  | Pass
Tbea | JBS | Workflow, Project Management Plan and Timelines | Project schedule / Project management | Quality Assurance | 1.8.3 | Inspection of equipment delivery | 1 | Page 1018 | 1 | [8 empty] | 1 |  | Pass
Tbea | JBS | Workflow, Project Management Plan and Timelines | Project schedule / Project management | Quality Assurance | 1.8.3 | Milestones for the completion of civil, mechanical, and electrical works | 1 | page 1025 | 1 | [5 empty] | dobble to 105 and 111 |  |  | 1 |  | Pass
Tbea | JBS | Workflow, Project Management Plan and Timelines | Project schedule / Project management | Quality Assurance | 1.8.3 | Quality control of delivered modules | 1 | Page 93, 1018 | 1 | [8 empty] | 1 |  | Pass
Tbea | JBS | Workflow, Project Management Plan and Timelines | Project schedule / Project management | Quality Assurance | 1.8.3 | Risk analysis and mitigation plan | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Tbea | JBS | Workflow, Project Management Plan and Timelines | Project schedule / Project management | Quality Assurance | 1.8.3 | System acceptance QA procedure by the Employer | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Tbea | JBS | Miscellaneous | Project schedule / Project management | Specific Requirements | 1.29.9 | The Bidder shall submit an organizational chart illustrating management and functional relationships among all project team members including consultants, sub-contractors and vendors at each significant stage of the work, such as permitting, design, construction, testing and commissioning and O&M. | 1 | page 14 | 1 | [8 empty] | 1 |  | Pass
Tbea | RM | Supervisory Control and Data Acquisition (SCADA) | SCADA | Specific Requirements | 1.9.2 | Alarms/alerts and timely notification of key performance indicators | 1 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | RM | Supervisory Control and Data Acquisition (SCADA) | SCADA | Specific Requirements | 1.9.2 | All communication/data cables outside of buildings must be fiber-optic cables | 1 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | RM | Supervisory Control and Data Acquisition (SCADA) | SCADA | Specific Requirements | 1.9.2 | Back-up power for a minimum of twelve hours | 1 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | RM | Supervisory Control and Data Acquisition (SCADA) | SCADA | Specific Requirements | 1.9.2 | Control room to remotely monitor and manage the whole system, on a 24 x 7 basis, with the capability of Web-based information sharing | 1 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | RM | Supervisory Control and Data Acquisition (SCADA) | SCADA | Specific Requirements | 1.9.2 | Data must be readily available for the fulfilment of all warranties and performance guarantees | 1 |  | 1 |  |  |  |  | Cannot be evaluated at this stage. | statement |  |  | 1 |  | Pass
Tbea | RM | Supervisory Control and Data Acquisition (SCADA) | SCADA | Specific Requirements | 1.9.2 | Data logging at intervals of not less than one minute, processing, transmission, and back-up | 1 |  |  |  | 1 | Correct meaning was: maximum interval length of 1 minute. Please confirm. |  |  | not more (!) |  |  | 1 |  | Open
Tbea | RM | Supervisory Control and Data Acquisition (SCADA) | SCADA | Specific Requirements | 1.9.2 | Data shall be provided via FTP (Push/Pull) to the Employer | 1 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | RM | Supervisory Control and Data Acquisition (SCADA) | SCADA | Specific Requirements | 1.9.1 | Remote access to all operational data for independent monitoring purposes shall be possible (NTDC requirements) | 1 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | RM | Supervisory Control and Data Acquisition (SCADA) | SCADA | Specific Requirements | 1.9.1 | Safe and redundant archive for operational data. | 1 |  | 1 |  |  | General understanding: expressions like "shall", "has to be", "must be" have the meaning of "will be delivered"? | [5 empty] | 1 |  | Pass
Tbea | RM | Supervisory Control and Data Acquisition (SCADA) | SCADA | Specific Requirements | 1.9.2 | Separate inverter, zone, and string level (current and voltage) monitoring | 1 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | RM | Supervisory Control and Data Acquisition (SCADA) | SCADA | Specific Requirements | 1.9.1 | The system has to provide different access-levels with different access rights allocated. | 1 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | RM | Earthworks | Site Preparation and site access | Design factors to be provided | 1.12 | All earth works required have to be specified and included in the offer | 1 |  |  |  | 1 | How about access accross those trenches into rows / where located? What is the idea of the paved station suare? Please describe cross section of internal access roads (line 163) | TBEA-12 Appendices Structure foundaton+earthing Inverter Station foundation MV box foundation Station square Cabel trench (solid box), top cover is 150mm above (!) ground |  |  |  |  | 1 |  | Open
Tbea | RM | Earthworks | Site Preparation and site access | Specific Requirements | 1.12, 1.13.4, 1.7.7 | Cross-sections of foundations for stations shall be provided, including explanation of the foundations laying down, height, penetration, and method of installing foundation posts, mounting fixtures | 1 |  | 1 |  |  | Stated | TBEA-12 Appedices Structure solution not finalized. Site testings will be executed in advance. Check in detail. |  |  |  |  | 1 |  | Pass
Tbea | RM | Earthworks | Site Preparation and site access | Specific Requirements | 1.12 | Position and specification of underground cable connections must be documented during installation | 1 |  | 1 |  |  |  |  | Cannot be avaluated at this stage. |  |  |  | 1 |  | Pass
Tbea | RM | Site Preparation and site access | Site Preparation and site access | Specific Requirements | 1.11.1 | The Bidder shall provide foundations and structures in accordance with the actual soil conditions. | 1 |  |  |  | 1 | I please describe so far calculations / plannings / uncertainties. Soil study is for information even if professionally executed. |  |  | refer to Soil study |  |  | 1 |  | Open
Tbea | RM | Earthworks | Site Preparation and site access | Specific Requirements | 1.12 | After completion of construction and all earthworks ground shall be levelled and stabilized. | 1 |  | 1 | [5 empty] | (maintanance, dust) |  |  | 1 |  | Pass
Tbea | RM | Earthworks | Site Preparation and site access | Specific Requirements | 1.12 | Within the plant boundary limits, access roads to all stations shall be suitable for heavy load trucks (axle load: min. 12 tonn). | 1 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | JBS | Power plant documentation | Spare parts | Warranty | 1.27.2 | The successful bidder shall provide all warranty spares for a warranty period of 5 years. | 1 |  |  |  | 1 | General understanding: expressions like "shall", "shall be supplied with", "has to be", "must be" have the meaning of "will be delivered"? Please confirm. |  |  |  | G | General understanding: expressions like "shall", "shall be supplied with", "has to be", "must be" have the meaning of "will be delivered"? Please confirm. | 1 |  | Open
Tbea | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Design factors to be provided | 1.21.2 | 3-phase, double wound, continuously rated, oil-cooled, enclosed transformers, use of low loss core steel and close coupled copper windings | 1 | page 902 |  | 1 |  | Unclear: We do not understand your proposal, please detail your proposal. Especially confirm that you are compliant with our requested criteria. | dry type transformer according to datasheet |  |  | U |  | 1 | 1 | Fail
Tbea | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Design factors to be provided | 1.21.2 | Cooling method | 1 | page 902 |  |  | 1 | Unclear: We do not understand your proposal, please detail your proposal. Especially confirm that you are compliant with our requested criteria. | dry type transformer according to datasheet |  |  | U |  | 1 |  | Open
Tbea | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Design factors to be provided | 1.21.2 | Efficiency | 1 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Design factors to be provided | 1.21.2 | Humidity tolerance | 1 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Design factors to be provided | 1.21.2 | Incoming terminals | 1 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Design factors to be provided | 1.21.2 | Insulation type | 1 |  |  |  | 1 | Unclear: We do not understand your proposal, please detail your proposal. Especially confirm that you are compliant with our requested criteria. | dry type transformer according to datasheet |  |  | U |  | 1 |  | Open
Tbea | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Design factors to be provided | 1.21.2 | kVA rating | 1 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Design factors to be provided | 1.21.2 | Maximum ambient temperature and altitude | 1 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Design factors to be provided | 1.21.2 | No-load losses | 1 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Design factors to be provided | 1.21.2 | Operating temperature range | 1 | page 902 |  |  | 1 | Unclear: We do not understand your proposal, please detail your proposal. Especially confirm that you are compliant with our requested criteria. | -35°C up to +45°C |  |  | U |  | 1 |  | Open
Tbea | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Design factors to be provided | 1.21.2 | Operational data shall be logged in central operating system (e.g. oil temperature, oil level, pressure, Temperature probes (one per phase): Alarm and trip of cell etc.) | 1 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Design factors to be provided | 1.21.2 | Outgoing terminals | 1 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Design factors to be provided | 1.21.2 | Primary side voltage | 1 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Design factors to be provided | 1.21.2 | Protection system | 1 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Design factors to be provided | 1.21.2 | Secondary side voltage | 1 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Design factors to be provided | 1.21.2 | Short-circuit impedance | 1 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Standards | 1.21.3 | IEC 60076 | 1 |  | 1 |  |  |  |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  |  |  | 1 |  | Pass
Tbea | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Standards | 1.21.3 | IEC 60085 | 1 |  | 1 |  |  |  |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  |  |  | 1 |  | Pass
Tbea | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Standards | 1.21.3 | IEC 60137 | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  | C |  | 1 |  | Open
Tbea | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Standards | 1.21.3 | IEC 60214 | 1 |  | 1 |  |  |  |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  |  |  | 1 |  | Pass
Tbea | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Standards | 1.21.3 | IEC 62446 | 1 |  | 1 |  |  |  |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  |  |  | 1 |  | Pass
Tbea | JBU | Step-up Transformers/MV Switchgear | Step-up Transformers/MV Switchgear | Guarantees | 1.21.1 | Compatibility with NTDC grid connection code must be ensured | 1 |  |  |  | 1 | General understanding: expressions like "shall", "shall be supplied with", "has to be", "must be" have the meaning of "will be delivered"? Please confirm. |  |  |  | G | General understanding: expressions like "shall", "shall be supplied with", "has to be", "must be" have the meaning of "will be delivered"? Please confirm. | 1 |  | Open
Tbea | GD | PR and System Performance Guarantee | System PR | Guarantees | 1.4.1 | A 25 years commitment, in the form of a whole System performance guarantee, is required. The performance guarantee is based on measuring the PR with the actual kWh-AC delivery per year adjusted for the actual POA irradiation for the same period | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  | Only to be checked in list of deviations. |  |  |  | 1 | 1 | Open
Tbea | JBS | System PR Specification | System PR | Losses included in PR calculation | 1.5.4 | Auxiliary loads | 1 | page 77 -78 |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | Fail Nicht berücksichtigt | We don’t understand the question. Kindly clarify. | see relevant chapter 1.5.4 List of "losses" = auxilary loads from PV Energy that make the PR | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Tbea | JBS | System PR Specification | System PR | Losses included in PR calculation | 1.5.4 | Inverter (operating efficiency, operating voltage variations, power/voltage levels) | 1 | page 77 -78 | 1 |  |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  | We don’t understand the question. Kindly clarify. | see relevant chapter 1.5.4 List of technical losses that make the PR |  |  | 1 |  | Pass
Tbea | JBS | System PR Specification | System PR | Losses included in PR calculation | 1.5.4 | Module Array (temperature dependence, soiling, low light inefficiency, shading, mismatches in array) | 1 | page 77 -78 |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | Fail. Shading and IAM losses missing | We don’t understand the question. Kindly clarify. | we want to see these losses specified. Thos need to be aligned with O+M Startegy and System composition | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Tbea | JBS | System PR Specification | System PR | Losses included in PR calculation | 1.5.4 | Ohmic losses in cables | 1 | page 77 -78 | 1 |  |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  | We don’t understand the question. Kindly clarify. | see relevant chapter 1.5.4 List of technical losses that make the PR |  |  | 1 |  | Pass
Tbea | JBS | System PR Specification | System PR | Losses included in PR calculation | 1.5.4 | Transformer losses | 1 | page 77 -78 | 1 |  |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  | We don’t understand the question. Kindly clarify. | see relevant chapter 1.5.4 List of technical losses that make the PR |  |  | 1 |  | Pass
Tbea | JBS | System PR Specification | System PR | O&M | 1.5.2 | The target PR specification at the time of commissioning the System is equal to or greater than 0.75 (75%). | 1 | page 77 -78 |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | [5 empty] | 1 |  | Open
Tbea | JBS | Physical layout | System PR | Specific Requirements | 1.7.1 | Provide a report using Solar GIS data provided by the Employer | 1 | page 75 | 1 |  |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  | Replace 'Report' with ' PV-Syst report'. | 'Report' is original wording in ER in 1.7.1 |  |  | 1 |  | Pass
Tbea | JBS | Physical layout | System PR | Specific Requirements | 1.7.1, 1.1.8 | Layout calculations of predicted kWh over the system lifetime and PR using the tool PVSyst V5.62 or higher | 1 | page 76 | 1 |  |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | [5 empty] | 1 |  | Pass
Tbea | GD | PR and System Performance Guarantee | System PR | System PR | 1.4.2 | Guaranteed PR values in the form of the Table in 1.4.1 for the acceptance phase and annual output of the PV system shall be specified. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Link to table in Documents sheet |  |  |  | 1 | 1 | Open
Tbea | GD | PR and System Performance Guarantee | System PR | System PR | 1.4.1 | The billing system/metering system will be installed at interconnection point of 132 kV bus bar of HV substation to be installed by the EPC Contractor and the 132 kV Transmission line of NTDC existing at site. | 2 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  | Only to be checked in list of deviations. |  |  |  | 1 |  | Open
Tbea | GD | PR and System Performance Guarantee | System PR | System PR | 1.4.4 | The initial PR will be first measured after the time of commissioning of the completed PV System during the acceptance phase of 30 days. | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  | Cannot be evaluated at this stage. Only to be checked in list of deviations. |  |  |  | 1 | 1 | Open
Tbea | JBS | Equipment guarantees | Warranty | Guarantees | 1.28.4, 1.6 | A detailed list of all guarantee conditions for the main equipments (beside modules and inverters) shall be provided by the Successful Bidder with the technical offer. The product warranty shall be at least 5 years. | 1 |  |  |  | 1 | General understanding: expressions like "shall", "shall be supplied with", "has to be", "must be" have the meaning of "will be delivered"? Please confirm. |  |  |  | G | General understanding: expressions like "shall", "shall be supplied with", "has to be", "must be" have the meaning of "will be delivered"? Please confirm. | 1 |  | Open
Tbea | JBS | Equipment guarantees | Warranty | Guarantees | 1.28 | The overall Guarantee and Power Plant Acceptance Procedures required for the Project are described in Sections 1.3, 1.4, 1.14, 1.18 and Schedule D and shall be met. | 1 |  |  |  | 1 | General understanding: expressions like "shall", "shall be supplied with", "has to be", "must be" have the meaning of "will be delivered"? Please confirm. |  | Link |  | G | General understanding: expressions like "shall", "shall be supplied with", "has to be", "must be" have the meaning of "will be delivered"? Please confirm. | 1 |  | Open
Tbea | JBS | Basic Scope of Supply | Warranty | Quality Assurance | 1.6 | The Product Warranties shall be given for a duration of at least 5 years | 1 | page 83 | 1 |  |  | General understanding: expressions like "shall", "shall be supplied with", "has to be", "must be" have the meaning of "will be delivered"? |  | Cannot be evaluated at this stage. Only to be checked in list of deviations. |  |  |  | 1 |  | Pass
Tbea | MAW | Inverters | Warranty | Warranty option | 1.18.1 | The Bidder shall arrange a full-service package for the selected inverters for a product warranty period of 5 years, with an option to cover additional 20 years including provisions for any necessary replacements including O&M service plan guaranteeing 99% availability. | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | Klaus? |  |  |  | Unclear: We do not understand your proposal, please detail your proposal. Especially confirm that you are compliant with our requested criteria. | 1 |  | Open
Zte | JBU | AC Cabling | AC Cabling | Design factors to be provided | 1.19.1 | AC cable shall be of Copper. Rated voltage, nominal voltage between phase and neutral and nominal voltage between phases to be specified by the Bidder | 1 | Technical Proposal of 100MW Solar Power Plant, page 85 |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | material is copper |  |  | C |  | 1 |  | Open
Zte | JBU | AC Cabling | AC Cabling | Design factors to be provided | 1.19.1 | Appropriate sizing to minimise voltage drop and losses | 1 | Technical Proposal of 100MW Solar Power Plant, page 114 | 1 |  |  |  | AC ohmic loss 0,1% | What is the appropriate size? | leeway to allow MPP tracking when module voltage drops. At least 10%. Ralf, ist Vital kriterium. |  |  | 1 |  | Pass
Zte | JBU | AC Cabling | AC Cabling | Design factors to be provided | 1.19.1 | Bending radius | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | no datasheet |  |  | C |  | 1 |  | Open
Zte | JBU | AC Cabling | AC Cabling | Design factors to be provided | 1.19.1 | Cable installation shall ensure grounding and short-circuit protection | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | no datasheet |  |  | C |  | 1 |  | Open
Zte | JBU | AC Cabling | AC Cabling | Design factors to be provided | 1.19.1 | Cables shall be suitable for the environmental conditions at the project site, including UV protection (The Bidder shall provide certification from manufacturer) | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | no datasheet |  |  | C |  | 1 |  | Open
Zte | JBU | AC Cabling | AC Cabling | Design factors to be provided | 1.19.1 | Installation to be verified by measurement-protocols | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | no datasheet |  |  | C |  | 1 |  | Open
Zte | JBU | AC Cabling | AC Cabling | Design factors to be provided | 1.19.1 | Lifetime longer than 25 years | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | no datasheet |  |  | C |  | 1 |  | Open
Zte | JBU | AC Cabling | AC Cabling | Design factors to be provided | 1.19.1 | Rated voltage | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | no datasheet |  |  | C |  | 1 |  | Open
Zte | JBU | AC Cabling | AC Cabling | Design factors to be provided | 1.19.1 | Sufficient and effective cable protection against attacks of rodents for any cabling underground or above is required | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | no datasheet |  |  | C |  | 1 |  | Open
Zte | JBU | AC Cabling | AC Cabling | Specific Requirements | 1.19.3 | The runs of both the main DC and AC cables, in the System layout, should be adjusted to keep power losses below <1% at STC (Design calculations through cable loss simulation to be provided for review & comment). | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  | Part of system design | Kategorie ? | C |  | 1 |  | Open
Zte | JBU | AC Cabling | AC Cabling | Standards | 1.19.2 | DIN-VDE-0276 | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | no datasheet | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  | C |  | 1 |  | Open
Zte | JBU | AC Cabling | AC Cabling | Standards | 1.19.2 | EN 60332-1-1 and EN 60332-2-1 | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | no datasheet | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  | C |  | 1 |  | Open
Zte | JBU | AC Cabling | AC Cabling | Standards | 1.19.2 | IEC 60364 | 1 |  | 1 |  |  |  | no datasheet | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  |  |  | 1 |  | Pass
Zte | JBU | AC Cabling | AC Cabling | Standards | 1.19.2 | IEC 60502 | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | no datasheet | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  | C |  | 1 |  | Open
Zte | JBU | AC Combiner Box | AC Combiner Box | Design factors to be provided | 1.20.1 | Class 2 AC surge arrestor | 1 |  | 1 |  |  |  | not applicable |  |  |  |  | 1 |  | Pass
Zte | JBU | AC Combiner Box | AC Combiner Box | Design factors to be provided | 1.20.1 | Flame test | 1 |  | 1 |  |  |  | not applicable |  |  |  |  | 1 |  | Pass
Zte | JBU | AC Combiner Box | AC Combiner Box | Design factors to be provided | 1.20.1 | Load breaker switch of adequate size | 1 |  | 1 |  |  |  | not applicable |  |  |  |  | 1 |  | Pass
Zte | JBU | AC Combiner Box | AC Combiner Box | Design factors to be provided | 1.20.1 | Operating temperature range | 1 |  | 1 |  |  |  | not applicable |  |  |  |  | 1 |  | Pass
Zte | JBU | AC Combiner Box | AC Combiner Box | Design factors to be provided | 1.20.1 | Rated current | 1 |  | 1 |  |  |  | not applicable |  |  |  |  | 1 |  | Pass
Zte | JBU | AC Combiner Box | AC Combiner Box | Design factors to be provided | 1.20.1 | Rated voltage | 1 |  | 1 |  |  |  | not applicable |  |  |  |  | 1 |  | Pass
Zte | JBU | AC Combiner Box | AC Combiner Box | Design factors to be provided | 1.20.1 | Stripping length of the individual wire | 1 |  | 1 |  |  |  | not applicable |  |  |  |  | 1 |  | Pass
Zte | JBU | AC Combiner Box | AC Combiner Box | Design factors to be provided | 1.20.1 | Waterproof test | 1 |  | 1 |  |  |  | not applicable |  |  |  |  | 1 |  | Pass
Zte | JBU | AC Combiner Box | AC Combiner Box | Standards | 1.20.2 | EN 60529, DIN-VDE-0472 | 1 |  | 1 |  |  |  | not applicable | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  |  |  | 1 |  | Pass
Zte | JBU | AC Combiner Box | AC Combiner Box | Standards | 1.20.2 | IP 67 | 1 |  | 1 |  |  |  | not applicable |  |  |  |  | 1 |  | Pass
Zte | JBS | Physical layout | Auxiliary equipment | Specific Requirements | 1.7.8 | All parts of the installation are covered by two high speed protection schemes, which shall be independent to avoid common mode failures | 1 | Technical Proposal of 100MW Solar Power Plant.pdfPate 17 | 1 |  |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | [5 empty] | 1 |  | Pass
Zte | JBS | Physical layout | Auxiliary equipment | Specific Requirements | 1.7.8 | The outline of protection schemes shall be shown on the single line diagram (SLD) | 1 |  | 1 | [8 empty] | 1 |  | Pass
Zte | JBS | Physical layout | Auxiliary equipment | Specific Requirements | 1.7.8 | Provide complete indicating, regulating, controlling, protecting and interlocking equipment necessary for safe and efficient operation of the plant and substation, including complete protection scheme. | 1 | P004 Single line diagram.pdf | 1 | [8 empty] | 1 |  | Pass
Zte | JBS | Physical layout | Auxiliary equipment | Specific Requirements | 1.7.9 | The scope of the documentation shall cover at least the requirements of IEC 62446. | 1 | 1. SoC to Bidding Document 30-01-14.pdf | 1 | [8 empty] | 1 |  | Pass
Zte | JBS | Physical layout | Auxiliary equipment | Specific Requirements | 1.7.8 | The Bidder shall include a fire prevention and response plan | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Zte | JBS | Physical layout | Auxiliary equipment | Specific Requirements | 1.7.9 | The documentation includes clearly labelled objects and figures annotated in English language. | 1 | 1. SoC to Bidding Document 30-01-14.pdf | 1 | [8 empty] | 1 |  | Pass
Zte | JBS | Physical layout | Auxiliary equipment | Specific Requirements | 1.7.8 | The fire prevention and response plan shall include a fire alarm und detection system with a main panel in the control room | 1 | 1. SoC to Bidding Document 30-01-14.pdf Page 97 | 1 | [8 empty] | 1 |  | Pass
Zte | RM | Other infrastructure | Auxiliary systems | DC Backup System / uninterrupted power supply (UPS) | 1.25.6 | IEC-60051 and IEC-60439 standards apply | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  |  |  | 1 |  | Open
Zte | RM | Other infrastructure | Auxiliary systems | Design factors to be provided | 1.25.1 | One administration and office building with car port for 10 vehicles shall be provided, with sufficient space for operating personal, control room, security office, regular office rooms for permanent and visiting staff, meeting room, kitchen sanitary systems (toilet, showers separate for male and female), first aid, control room, electrical rooms, etc. The building shall have windows for office rooms and air conditioning system (split units) for all office rooms. | 1 |  | 1 |  |  |  |  | Priority to be discussed |  |  |  | 1 |  | Pass
Zte | RM | Other infrastructure | Auxiliary systems | Design factors to be provided | 1.25.1 | Service water system sufficiently sized for cleaning cycle of modules | 1 |  | 1 | [8 empty] | 1 |  | Pass
Zte | RM | Other infrastructure | Auxiliary systems | Design factors to be provided | 1.25.1 | Sewage system including sewage disposal for Construction and O&M phase | 1 |  | 1 | [8 empty] | 1 |  | Pass
Zte | RM | Other infrastructure | Auxiliary systems | Design factors to be provided | 1.25.1 | Warehouse for spare parts and workshop for minor mechanical/electrical works. | 1 |  | 1 | [8 empty] | 1 |  | Pass
Zte | RM | Other infrastructure | Auxiliary systems | Design factors to be provided | 1.25.1 | Water storage facility for drinking water, sanitary water (sufficient for 1 week) | 1 |  |  |  | 1 | description is exhaustive, but please confirm cormity with RFP | [5 empty] | 1 |  | Open
Zte | RM | Other infrastructure | Auxiliary systems | Guarantees | 1.25.4 | All buildings should be designed in accordance with the requirements of the Pakistan Building Code (available at www.pec.org.pk/buildingcode.aspx) and latest Seismic Provisions 2007. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Link to code |  |  |  | 1 |  | Open
Zte | JBS | Miscellaneous | Auxiliary systems | Power supply | 1.29.1 | An off-grid power station may need to be provided by the Bidder for commencing the work. Diesel generators shall be arranged by the bidder on its own. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Zte | RM | Other infrastructure | Auxiliary systems | Security Surveillance System | 1.25.5 | The Bidder shall provide security personnel for 24 h / 7 days a week for the whole year | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | [5 empty] | 1 |  | Open
Zte | RM | Other infrastructure | Auxiliary systems | Security Surveillance System | 1.25.5 | The system shall comply with insurance requirements | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | [5 empty] | 1 |  | Open
Zte | RM | Meteorological Sensors | Auxiliary Systems | Specific Requirements | 1.10.1 | Irradiation and temperature measurements are to be recorded at intervals of 15 min or less. | 1 |  |  |  | 1 | "Technical Proposal of 100MW Solar Power Plant.pdf" 5.2.10: more details requiered | [5 empty] | 1 |  | Open
Zte | RM | Meteorological Sensors | Auxiliary Systems | Specific Requirements | 1.10.2 | Seven pyranometers shall be placed : three for measuring the horizontal plane irradiation and the others for the in-plane irradiation. | 1 |  |  |  | 1 | please confirm Secondary Standard and 7 Py's as required |  | As in 1.10.2, it is seven pyranometer per system, please clarify the word "per system" | 1.1.1: "100 MWp (DC capacity at Standard Testing Conditions, abbreviated STC … hereinafter called 'the System') " |  |  | 1 |  | Open
Zte | RM | Meteorological Sensors | Auxiliary Systems | Specific Requirements | 1.10.2 | The irradiation measurement equipment should be calibrated by an independent certified third party at least every two years. The calibration must be traceable to international standards. | 1 |  |  |  | 1 | please confirm |  | Should be checked in list of deviations |  |  |  | 1 |  | Open
Zte | RM | Meteorological Sensors | Auxiliary Systems | Specific Requirements | 1.10.3 | Ambient air and the module temperature shall be measured at every 5 installed MWp in conformity with IEC 60751 AA | 1 |  |  |  | 1 | please confirm | [5 empty] | 1 |  | Open
Zte | RM | Meteorological Sensors | Auxiliary Systems | Specific Requirements | 1.10.1 | The equipment should have the capability of recording and storing data for 24 hours using auxiliary DC power. | 1 |  |  |  | 1 | DC control power system back-up 100Ah: pease confirm back-up time |  | Should be priority 1 question |  |  |  | 1 |  | Open
Zte | RM | Meteorological Sensors | Auxiliary Systems | Specific Requirements | 1.10.2 | The pyranometers should conform to the standards of ISO 9060 (SR5: secondary standard) or the WMO classification, and IEC 60904. | 1 |  |  |  | 1 | please confirm |  | Do we need to know some parameter values according to standards mentioned or just a statement of comlience with the standard would be sufficient? | compliance will be necessary, no data due diligence right now. |  |  | 1 |  | Open
Zte | GD | PR and System Performance Guarantee | Compensations | O&M | 1.4.6 | If the successful Bidder defaults in being able to provide the O&M services required for the Systems performance guarantee, then it will be liable to cover all costs – but at least in the amount of Liquidated Damages imposed to the Employer by its PPA agreements - incurred by the Employer, including the loss of the guaranteed electricity export to the grid (but at a minimum rate of USD 0.20-per-kWh) for the disrupted period, in finding and hiring a replacement for the purpose. | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  | Cannot be evaluated at this stage. Only to be checked in list of deviations. |  |  |  | 1 | 1 | Open
Zte | GD | PR and System Performance Guarantee | Compensations | O&M | 1.4.5 | For timely compensation the PR Calculation will be carried out provisionally for each quarter whereby the contractor and employer might jointly agree on different PR values for each quarter. In the last quarter of each calendar year the annual PR compensation of the full year will be carried out and any provisions will be offset by the annual compensation. | 3 |  |  |  | 1 |  |  | Cannot be evaluated at this stage. Only to be checked in list of deviations. |  |  |  | 1 |  | Open
Zte | GD | PR and System Performance Guarantee | Compensations | O&M | 1.4.5 | If the annual measured PR falls below the guaranteed PR value according to Table 1.4.1, the liquidated damages will be levied on the successful Bidder at the rate of USD 0.20-per-kWh or the kWh Value the Employer receives for each kWh of shortfall – whichever is higher. Adjustments shall be made for any events outside the control of the O&M operator as grid outages, from grid operator ordered shutdowns, or force majeure events during the year. | 2 |  |  |  | 1 |  |  | Cannot be evaluated at this stage. Only to be checked in list of deviations. | Only to be checked in list of deviations. |  |  | 1 |  | Open
Zte | GD | PR and System Performance Guarantee | Compensations | O&M | 1.4.5 | In case the PR is higher than the guaranteed PR value, the net value of this excess energy will be shared as follows: 50% towards the asset replacement fund, 25% towards the Employer, 25% towards the O&M contractor | 3 |  |  |  | 1 |  |  | Cannot be evaluated at this stage. Only to be checked in list of deviations. |  |  |  | 1 |  | Open
Zte | GD | PR and System Performance Guarantee | Compensations | System PR | 1.4.4 | If the measured PR within further 30 days does not reach the guaranteed PR, the Employer can demand that the price of the system will be reduced by the percentage of shortfall times 1.2 for liquidated damages or the contractor will have to install more power at its own cost or combination of both. | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  | Cannot be evaluated at this stage. Only to be checked in list of deviations. |  |  |  | 1 | 1 | Open
Zte | GD | PR and System Performance Guarantee | Compensations | System PR | 1.4.4 | The successful Bidder shall conduct the initial PR test for the daylight hours of at least 30 consecutive days, recording data at a frequency of fifteen minute intervals or less, to validate the guaranteed PR value for acceptance. Any excused downtime (e.g., from Grid Operator ordered shutdowns, grid failure, theft, force majeure) will be excluded from that calculation by an independent consultant (Auditing Body). That day will be taken out and another day added, if the initial PR falls short of the guaranteed PR value, the successful Bidder shall be obliged to identify and rectify the causes for the performance shortfall at their own cost. | 2 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  | Cannot be evaluated at this stage. Only to be checked in list of deviations. |  |  |  | 1 |  | Open
Zte | GD | Conditions for Disqualification and Additional Information Required | Credentials | EPC | 1.2.6 | Approval from bidder to owners or owner representatives to answer questions freely regarding the past performance of the bidder and performance of the system against contractual obligations. | 2 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | [5 empty] | 1 |  | Open
Zte | GD | Conditions for Disqualification and Additional Information Required | Credentials | EPC | 1.2.6 | Cumulative MWp of ground mounted PV turnkey installations >5 MWp with stating of actual MWp per project, project location, date of commissioning, module type and Inverter type. | 1 |  | 1 | [5 empty] | experience of Bidder / EPC |  |  | 1 | 1 | Pass
Zte | GD | Conditions for Disqualification and Additional Information Required | Credentials | EPC | 1.2.6 | Detailed list of all the sites with the affirmation that the bidder played the leading EPC role in the turnkey installation of these systems. | 3 |  | 1 | [8 empty] | 1 |  | Pass
Zte | GD | Conditions for Disqualification and Additional Information Required | Credentials | EPC | 1.2.6 | References and contact data (mail and phone) from owners of all installations > 5 MW with quotes of the corresponding system Performance Ratios, as well as system performance vs. initial yield assessment per year since the installation. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  | for selection of referenz objects |  |  | 1 | 1 | Open
Zte | GD | Technical Bid Evaluation Criteria | Credentials | EPC | 1.3.1 | the systems have been completed on time and within budget, | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | [5 empty] | 1 | 1 | Open
Zte | GD | Scope of the Bid | Credentials | EPC | 1.1.9 | The bid includes professional experience of the Bidders in ground mounted utility-scale PV and financial information about their long-term stability | 3 |  | 1 | [8 empty] | 1 |  | Pass
Zte | GD | Scope of the Bid | Credentials | EPC | 1.1.10 | The Bidder, or the Lead company in case of JV is a EPC contractor | 1 |  | 1 |  |  |  |  | This is a non-technical question. We suggest such question should be separated from technical questions and placed in checklist for "General/Substantive Responsiveness of Bid" | a question of reliability and experience of solid understanding of the task/System Technology. See also 1.1.10 |  |  | 1 |  | Pass
Zte | GD | Technical Bid Evaluation Criteria | Credentials | Guarantees | 1.3.1 | To have met the contractual requirements of the EPC and O&M deliverables including certificate to the effect that the entire equipment is brand new as required vide notification number NEPRA/UTS-01/777-779 dated Jan 21 ,2014, | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Only to be checked in list of deviations. |  |  |  | 1 | 1 | Open
Zte | GD | Technical Bid Evaluation Criteria | Credentials | O&M | 1.3.1 | In case of a non-performance, comprehensible evidence has to be given why this case will not affect this project. | 3 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | [5 empty] | 1 |  | Open
Zte | GD | Technical Bid Evaluation Criteria | Credentials | O&M | 1.3.1 | that they have started supplying electricity to the grid and are still operating satisfactorily in 9 out of 10 MW for all the cases | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | [5 empty] | 1 | 1 | Open
Zte | GD | Conditions for Disqualification and Additional Information Required | Credentials | O&M | 1.2.6 | Cumulative MWp of ground mounted PV installations for which O&M services have been delivered by the bidder or his O&M subcontractor. | 2 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | [5 empty] | 1 |  | Open
Zte | GD | Technical Bid Evaluation Criteria | Credentials | O&M | 1.3.2 | Prove at least 100 MW of EPC experience and 50 MW of full O&M experience for a period longer than 24 months. | 1 |  | 1 | [8 empty] | 1 |  | Pass
Zte | GD | Conditions for Disqualification and Additional Information Required | Credentials | O&M | 1.2.6 | References, contact data and approval from owners or owner representatives of all installations > 5 MW from bidder or his O&M subcontractor to answer questions freely regarding the past performance of the bidder and performance of the system against contractual obligations. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | [5 empty] | 1 | 1 | Open
Zte | MAW | Modules | Credentials | Project references | 1.14.8 | To show the proven technology a minimum of 500MW of proposed product type series must be in operation and reference projects shall be named. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Related to project references |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Zte | MAW | Inverters | Credentials | Project references | 1.18.10 | A minimum of 100 MWp of similar product/type must be in operation and reference projects shall be named. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Zte | MAW | DC Cables | DC Cables | Design factors to be provided | 1.15.2 | String cable shall be of the following type: single conductor type, copper, 1000 V / Class II (according to protection class II / 1000V, IEC 61140, single core cable, tinned copper conductor, XLPE Insulation, double EVA jacket (resistant to heat and cold, resistant to ozone, UV, oil and chemicals), Temperature: 90 º C (Temperature Max. Allowable: 120 º C), Halogen free | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | It should be in accordance with the inverter values. | possibly 1500V for such system design | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Zte | MAW | DC Cables | DC Cables | Design factors to be provided | 1.15.2 | Balance of electrical potential | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Need to be disscussed | equipotential bonding earthing mesh | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Zte | MAW | DC Cables | DC Cables | Design factors to be provided | 1.15.2 | Clear and systematic labelling required | 1 |  |  |  | 1 |  |  |  |  | C |  | 1 |  | Open
Zte | MAW | DC Cables | DC Cables | Design factors to be provided | 1.15.2 | Connectors of Modules and string cables shall be connected of self-locking type, have IP65 rating and shall be from same manufacturer and type | 1 |  | 1 |  |  |  | MC4 |  |  |  |  | 1 |  | Pass
Zte | MAW | DC Cables | DC Cables | Design factors to be provided | 1.15.2 | Installation to be verified by measurement-protocols | 1 |  |  |  | 1 |  |  | Cannot be evaluated at this stage. | blanc protocol | C |  | 1 |  | Open
Zte | MAW | DC Cables | DC Cables | Design factors to be provided | 1.15.2 | Lifetime of 30 years is assured | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | What proof is required. | Life time test of nonmetal materials IEC 60811-408:2012 / (DIN EN 60811-408; VDE 0473-811-408:2012-12) 30 y assurance never seen until today | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Zte | MAW | DC Cables | DC Cables | Design factors to be provided | 1.15.2 | Sizing of cables shall be specified according to the number of modules and strings per array | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  | voltage drop calculation | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Zte | MAW | DC Cables | DC Cables | Design factors to be provided | 1.15.2 | The DC main (downstream of combiner box) wiring harness shall have the quality: Aluminum / Copper / 1000 V / Class II | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | It should be in accordance with the inverter values. | possibly 1500V for such system design | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Zte | MAW | DC Cables | DC Cables | Specific Requirements | 1.15.1 | Are Ohmic losses less than 1% at full power? | 1 |  | 1 | [5 empty] | DC+AC losses < 2% |  |  | 1 |  | Pass
Zte | MAW | DC Cables | DC Cables | Standards | 1.15.3 | IEC 60364-1 | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Zte | MAW | DC Connectors | DC Connectors | Standards | 1.16.2 | EN 50521 | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? | PV Connectors no, just a statement of compliance | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Zte | MAW | DC Connectors | DC Connectors | Standards | 1.16.2 | IEC 60512 | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? | Connectors E-Systems no, just a statement of compliance | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Zte | MAW | DC Junction Box | DC Junction Box | Design factors to be provided | 1.17.1 | At least IP54 | 1 | \3-Response to Section 2\2-Schedules to Bid\Schedule A - Specific Works Data\1. Technical Proposal | 1 |  |  |  | IP65 | DC Junction box is applicable in what conditions? | depending on DC Design |  |  | 1 |  | Pass
Zte | MAW | DC Junction Box | DC Junction Box | Design factors to be provided | 1.17.1 | Class 2 DC surge arrestor | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Zte | MAW | DC Junction Box | DC Junction Box | Design factors to be provided | 1.17.1 | DC fuses shall permit up to maximum 1000 V (or 1500V if designed). String box design, including all operating elements shall satisfy safety requirements | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | equipotential connection? | Will inverter voltage(1500V) effect the maximum voltage(1000V)? | depends on spec of inverter. | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Zte | MAW | DC Junction Box | DC Junction Box | Design factors to be provided | 1.17.1 | Dust and heat protection | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Zte | MAW | DC Junction Box | DC Junction Box | Design factors to be provided | 1.17.1 | Monitored input-couples | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Zte | MAW | DC Junction Box | DC Junction Box | Specifications | 1.17.2 | Current monitoring | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Zte | MAW | DC Junction Box | DC Junction Box | Specifications | 1.17.2, 1.17.1 | Monitoring interface for SCADA | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Zte | MAW | DC Junction Box | DC Junction Box | Specifications | 1.17.2 | Touch-safe protective cover | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | no cover, just small boxes |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Zte | MAW | DC Junction Box | DC Junction Box | Standards | 1.17.3 | EN 50178 | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? | High currat devices no, just a statement of compliance | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Zte | MAW | DC Junction Box | DC Junction Box | Standards | 1.17.3 | EN 60439-1 | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? | arcing fault / Störlichtbogen Verhalten no, just a statement of compliance | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Zte | MAW | DC Junction Box | DC Junction Box | Standards | 1.17.3 | EN 61000-6 | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? | EMV no, just a statement of compliance | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Zte | JBU | Step-up Transformers/MV Switchgear | Due Diligence | Quality Assurance | 1.21.3 | Factory witness testing will be required for MV transformer and switchgear to be installed at this project. The cost of the due diligence to be carried by the Employer through an independent technical consultant will be taken over by the successful bidder up to an amount of 30,000 USD. | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  |  |  | C |  | 1 |  | Open
Zte | MAW | Inverters | Due diligence | Quality Assurance | 1.18.12 | The Bidder accepts that the cost of the Quality assurance for Inverters to be carried by the Employer through an independent technical consultant shall be taken over by the successful bidder up to an amount of 100,000 USD. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Zte | MAW | Modules | Due Diligence | Quality Assurance | 1.14.6 | The bidder will bear the cost of the Quality assurance for PV modules on-site and in laboratory to be carried out by the Employer through an independent technical consultant up to 150,000 USD. | 1 |  |  |  | 1 |  |  |  |  | C |  | 1 |  | Open
Zte | GD | Technical Bid Evaluation Criteria | Due Diligence | Quality Assurance | 1.3.5 | The cost of the due diligence to be carried out by the Employer through an independent technical consultant before contract signature will be taken over by the successful bidder up to an amount of 50,000 USD independent of the result. The due diligence will cover a module factory visit, an inverter factory inspection and a due diligence on the provided financial, EPC and O&M credentials including up to three site visits. | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  | Only to be checked in list of deviations. |  |  |  | 1 |  | Open
Zte | GD | Scope of the Bid | General items | Guarantees | 1.1.5 | Energy Purchase Agreement (EPA) practices are followed | 1 |  |  |  | 1 | Important reasons: due to current uncertainty of the criteria we accept an open status. Please clarify that yo acknowledge the criteria and comply unless a reason of high importance will not allow you you to comply. In such a situation the parties will seek to agree a compromise. |  | This cannot be evaluated at this stage. | we need a sentence that it should and can only be disregarded for important reasons |  |  | 1 |  | Open
Zte | JBS | Labelling | General items | Labelling | 1.26 | the ID numbering / coding system shall allow unique identification of all components and be understandable | 1 | 1. SoC to Bidding Document 30-01-14.pdf | 1 |  |  |  |  | Cannot be evaluated at this stage |  |  |  | 1 |  | Pass
Zte | JBS | Labelling | General items | Labelling | 1.26 | Tags shall be weather and UV resistant. | 1 | 1. SoC to Bidding Document 30-01-14.pdf | 1 |  |  |  |  | Cannot be evaluated at this stage |  |  |  | 1 |  | Pass
Zte | JBS | Labelling | General items | Labelling | 1.26 | The ID’s shall correspond to all drawings, plant documentation and control system. | 1 | 1. SoC to Bidding Document 30-01-14.pdf | 1 |  |  |  |  | Cannot be evaluated at this stage |  |  |  | 1 |  | Pass
Zte | GD | Scope of the Bid | General items | Quality Assurance | 1.1.3 | Defect components consequences: If one tested sample fails in one criterion, all items of the same category will be regarded as failed and rejected. | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  | Only to be checked in list of deviations. | yes, we need to be sure that they comply as for most of the critera |  |  | 1 | 1 | Open
Zte | GD | Scope of the Bid | General items | Specific Requirements | 1.1.2 | The Offer shall include a list of all vendors and/or sub-contractors for major equipment. | 1 |  |  |  | 1 | [6 empty] | 1 |  | Open
Zte | GD | Scope of the Bid | General items | Specific Requirements | 1.1.9 | The bid covers the planning of the System design, the required functionality of the System in terms of its sub-systems and components, detailed feature-wise descriptions of the components to be used in the System, the planning of the System installation, its integration, testing, monitoring, commissioning and O&M of the System | 1 |  |  |  | 1 | We can not find all of the requested criteria in your documents. Please confirm that your bid is compliant with all expectations and requirements of Section 6 of the RFP and provide a list with ALL exeptions or alterations. This applies to both, the EOPC And the O&M part. |  | This question should be removed as detailed design of every component/sub-system will be checked and evaluated thoroughly in technical evaluation | no, its an overall critera an need to be met |  |  | 1 | 1 | Open
Zte | JBS | Basic Scope of Supply | General items | Specific Requirements | 1.6 | The maximum DC voltage shall not exceed 1500 V | 1 |  | 1 | [8 empty] | 1 |  | Pass
Zte | JBS | Basic Scope of Supply | General items | Specific Requirements | 1.6 | The required AC voltage / frequency at grid connection shall 132 kV/50 Hz | 1 |  | 1 | [8 empty] | 1 |  | Pass
Zte | JBS | Equipment guarantees | Inverter | Guarantees | 1.28.2 | The Successful Bidder shall provide an Inverter warranty of at least 5 years. A spare parts warranty shall be included for the 25 years operational period. | 1 | 1. SoC to Bidding Document 30-01-14.pdf | 1 | [8 empty] | 1 |  | Pass
Zte | JBU | Inverter/Transformer Station | Inverter/Transformer Station | Specific Requirements | 1.22 | All stations shall be equipped with fire and smoke detectors and alarm, connected to security and surveillance system | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | no datasheet |  |  | C |  | 1 |  | Open
Zte | JBU | Inverter/Transformer Station | Inverter/Transformer Station | Specific Requirements | 1.22 | Bidder shall firmly specify the number of stations, manufacturer, capacity and type of equipment. | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | no datasheet |  |  | C |  | 1 |  | Open
Zte | JBU | Inverter/Transformer Station | Inverter/Transformer Station | Specific Requirements | 1.22 | Every ten (10) or lesser number of stations shall be equipped with an earthing and short-circuiting equipment | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | no datasheet |  |  | C |  | 1 |  | Open
Zte | JBU | Inverter/Transformer Station | Inverter/Transformer Station | Specific Requirements | 1.22 | Fine sand filters shall be installed | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | no datasheet |  |  | C |  | 1 |  | Open
Zte | JBU | Inverter/Transformer Station | Inverter/Transformer Station | Specific Requirements | 1.22 | The station shall enable the grounding of hardware and neutral will be left ground isolated | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | no datasheet |  |  | C |  | 1 |  | Open
Zte | MAW | Inverters | Inverters | Design factors to be provided | 1.18.7 | Cooling method | 1 |  | 1 |  |  | Unclear: We do not understand your proposal, please detail your proposal. Especially confirm that you are compliant with our requested criteria. | [5 empty] | 1 |  | Pass
Zte | MAW | Inverters | Inverters | Design factors to be provided | 1.18.7 | Detection of insulation faults | 1 |  | 1 |  |  | Unclear: We do not understand your proposal, please detail your proposal. Especially confirm that you are compliant with our requested criteria. | [5 empty] | 1 |  | Pass
Zte | MAW | Inverters | Inverters | Design factors to be provided | 1.18.7 | Input voltage range (The voltage window for MPP tracking shall accommodate the expected degradation of the modules.) | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Zte | MAW | Inverters | Inverters | Design factors to be provided | 1.18.7 | Integrated transformer/transformerless / Outside Dry Type Transformer | 1 |  | 1 |  |  |  | no transformer |  |  |  |  | 1 |  | Pass
Zte | MAW | Inverters | Inverters | Design factors to be provided | 1.18.7 | Maximum output current | 1 |  | 1 | [8 empty] | 1 |  | Pass
Zte | MAW | Inverters | Inverters | Design factors to be provided | 1.18.7 | Nominal output frequency, 3-phase | 1 |  | 1 | [8 empty] | 1 |  | Pass
Zte | MAW | Inverters | Inverters | Design factors to be provided | 1.18.7 | Nominal output voltage | 1 |  | 1 | [8 empty] | 1 |  | Pass
Zte | MAW | Inverters | Inverters | Design factors to be provided | 1.18.7 | Nominal power | 1 |  | 1 | [8 empty] | 1 |  | Pass
Zte | MAW | Inverters | Inverters | Design factors to be provided | 1.18.7 | Operating temperature range | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | -25℃~+55℃(>45℃derating) | What is the acceptable range? | 60°C Derating? | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Zte | MAW | Inverters | Inverters | Design factors to be provided | 1.18.7 | Output voltage range | 1 |  | 1 | [8 empty] | 1 |  | Pass
Zte | MAW | Inverters | Inverters | Design factors to be provided | 1.18.7 | Peak efficiency/ Weighted efficiency | 1 |  | 1 | [8 empty] | 1 |  | Pass
Zte | MAW | Inverters | Inverters | Design factors to be provided | 1.18.7 | Protection rating: NEMA 3R, IP54/IP55/IP60 | 1 |  | 1 |  |  | Unclear: We do not understand your proposal, please detail your proposal. Especially confirm that you are compliant with our requested criteria. | IP54 |  |  |  |  | 1 |  | Pass
Zte | MAW | Inverters | Inverters | Design factors to be provided | 1.18.7 | PV array configuration options: positive ground, negative ground | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Zte | MAW | Inverters | Inverters | Functionalities | 1.18.3 | Active power control reduction: remotely set point of control in case of network congestions or risk of system collapse, if deemed necessary | 1 | \3-Response to Section 2\2-Schedules to Bid\Schedule F - Specific Operation Plant and Equipment Detail\3-Data Sheets, Instructions, Manuals\Inverter\Datasheet |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | 8.2 needs to ensure these questions are answered in the bids. |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Zte | MAW | Inverters | Inverters | Functionalities | 1.18.3 | Anti-islanding protection | 1 | \3-Response to Section 2\2-Schedules to Bid\Schedule F - Specific Operation Plant and Equipment Detail\3-Data Sheets, Instructions, Manuals\Inverter\Datasheet | 1 | [8 empty] | 1 |  | Pass
Zte | MAW | Inverters | Inverters | Functionalities | 1.18.3 | Frequency regulation | 1 | \3-Response to Section 2\2-Schedules to Bid\Schedule F - Specific Operation Plant and Equipment Detail\3-Data Sheets, Instructions, Manuals\Inverter\Datasheet |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | 8.2 needs to ensure these questions are answered in the bids. |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Zte | MAW | Inverters | Inverters | Functionalities | 1.18.3 | Limitation of voltage fluctuation due to switching operations and long-term flicker | 1 | \3-Response to Section 2\2-Schedules to Bid\Schedule F - Specific Operation Plant and Equipment Detail\3-Data Sheets, Instructions, Manuals\Inverter\Datasheet |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | 8.2 needs to ensure these questions are answered in the bids. |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Zte | MAW | Inverters | Inverters | Functionalities | 1.18.3 | Limitation of current harmonics and higher frequency components up to 9 kHz | 1 | \3-Response to Section 2\2-Schedules to Bid\Schedule F - Specific Operation Plant and Equipment Detail\3-Data Sheets, Instructions, Manuals\Inverter\Datasheet |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Zte | MAW | Inverters | Inverters | Functionalities | 1.18.3 | Limitation of short-circuit current | 1 | \3-Response to Section 2\2-Schedules to Bid\Schedule F - Specific Operation Plant and Equipment Detail\3-Data Sheets, Instructions, Manuals\Inverter\Datasheet |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | 8.2 needs to ensure these questions are answered in the bids. |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Zte | MAW | Inverters | Inverters | Functionalities | 1.18.3 | Limitation of steady-stage voltage changes to 2% of the nominal value | 1 | \3-Response to Section 2\2-Schedules to Bid\Schedule F - Specific Operation Plant and Equipment Detail\3-Data Sheets, Instructions, Manuals\Inverter\Datasheet |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Zte | MAW | Inverters | Inverters | Functionalities | 1.18.3 | Matching grid voltage and frequency at point-of-coupling | 1 | \3-Response to Section 2\2-Schedules to Bid\Schedule F - Specific Operation Plant and Equipment Detail\3-Data Sheets, Instructions, Manuals\Inverter\Datasheet |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Zte | MAW | Inverters | Inverters | Functionalities | 1.18.3 | Maximum Power Point Tracking (MPPT) and string/sub-array management | 1 | \3-Response to Section 2\2-Schedules to Bid\Schedule F - Specific Operation Plant and Equipment Detail\3-Data Sheets, Instructions, Manuals\Inverter\Datasheet |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Zte | MAW | Inverters | Inverters | Functionalities | 1.18.3 | Voltage and frequency fault ride-through: no disconnection of the connection through voltage dip and change of active power generation, feed-in of reactive power during the fault for voltage stabilisation | 1 | \3-Response to Section 2\2-Schedules to Bid\Schedule F - Specific Operation Plant and Equipment Detail\3-Data Sheets, Instructions, Manuals\Inverter\Datasheet | 1 |  |  |  |  | 8.2 needs to ensure these questions are answered in the bids. |  |  |  | 1 |  | Pass
Zte | MAW | Inverters | Inverters | Functionalities | 1.18.3 | Voltage regulation through reactive power support: remotely set point control for voltage stability | 1 | \3-Response to Section 2\2-Schedules to Bid\Schedule F - Specific Operation Plant and Equipment Detail\3-Data Sheets, Instructions, Manuals\Inverter\Datasheet | 1 |  |  |  |  | 8.2 needs to ensure these questions are answered in the bids. |  |  |  | 1 |  | Pass
Zte | MAW | Inverters | Inverters | Manufacturers confirmation | 1.18.9 | The Bidder shall deliver a manufacturer's confirmation in his Bid for the suitability of the inverter for the specific weather conditions applicable in Bahawalpur Pakistan. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Zte | MAW | Inverters | Inverters | Quality Assurance | 1.18.11 | After commissioning, 1 of 10 inverters will be measured on site (power curve and efficiency) by an approved independent technical consultant on behalf of the Employer. The on-site measurements shall be accepted by the Bidder as average values for all inverters | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Cannot be evaluated at this stage | compliance! | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Zte | MAW | Inverters | Inverters | Quality Assurance | 1.18.11 | Check of protection against overload, short-circuit, grid-failure, internal failure, over-temperature (de-rating), surge protection, detection of insulation faults of AC Cables. Bidder shall firmly specify the manufacturer, types and length of cables to be installed | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | 8.2 needs to ensure these questions are answered in the bids. |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Zte | MAW | Inverters | Inverters | Quality Assurance | 1.18.11 | Test run and check of MPP tracking of all inverters | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | 8.2 needs to ensure these questions are answered in the bids. |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Zte | MAW | Inverters | Inverters | Quality Assurance | 1.18.11 | Test run in the field for maximum and EU-efficiency of all Inverters | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | 8.2 needs to ensure these questions are answered in the bids. |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Zte | MAW | Inverters | Inverters | Quality Assurance | 1.18.11 | The Bidder shall deliver detailed protocols of performance test run (warm power test) for every single inverter | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Cannot be evaluated at this stage |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Zte | MAW | Inverters | Inverters | Specific Requirements | 1.18.6 | Specifications of table in Schedule C shall be met | 1 | \3-Response to Section 2\2-Schedules to Bid\Schedule F - Specific Operation Plant and Equipment Detail\3-Data Sheets, Instructions, Manuals\Inverter\Datasheet | 1 |  |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  | Link to table |  |  |  | 1 |  | Pass
Zte | MAW | Inverters | Inverters | Standards | 1.18.8 | IEEE 1547 | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? | no, just a statement of compliance Interconnecting Distributed Resources | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Zte | MAW | Inverters | Inverters | Standards | 1.18.8 | TUV, VDE, or equivalent certification of passing the relevant standards | 1 | \3-Response to Section 2\2-Schedules to Bid\Schedule F - Specific Operation Plant and Equipment Detail\3-Data Sheets, Instructions, Manuals\Inverter\Datasheet | 1 | [7 empty] | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | 1 |  | Pass
Zte | MAW | Inverters | Inverters | Strategic Reason for Inverter Selection | 1.18.2 | Available uptime | 1 | \3-Response to Section 2\2-Schedules to Bid\Schedule F - Specific Operation Plant and Equipment Detail\3-Data Sheets, Instructions, Manuals\Inverter\Datasheet |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Zte | MAW | Inverters | Inverters | Strategic Reason for Inverter Selection | 1.18.2 | Balance of System (BOS) costs of inverter and labour | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  | financial bid | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Zte | MAW | Inverters | Inverters | Strategic Reason for Inverter Selection | 1.18.2 | Concept of protection against overload, short-circuit, grid-failure, internal failure, over-temperature (de-rating), surge protection | 1 | \3-Response to Section 2\2-Schedules to Bid\Schedule F - Specific Operation Plant and Equipment Detail\3-Data Sheets, Instructions, Manuals\Inverter\Datasheet |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | partly confirmed | Its too general, needs to be reviewed. | failure codes and consquences (automatic/manual restart, throw away safety devices) | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Zte | MAW | Inverters | Inverters | Strategic Reason for Inverter Selection | 1.18.2 | Dust and heat protection | 1 | \3-Response to Section 2\2-Schedules to Bid\Schedule F - Specific Operation Plant and Equipment Detail\3-Data Sheets, Instructions, Manuals\Inverter\Datasheet |  |  | 1 |  |  |  | derating? |  |  | 1 |  | Open
Zte | MAW | Inverters | Inverters | Strategic Reason for Inverter Selection | 1.18.2 | Timely and effective monitoring at a granular/zoomed-in level | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Zte | GD | Scope of the Bid | Layout | Guarantees | 1.1.6 | The bidder confirms that the system complies with all applicable requirements of the NEPRA Grid Code of Pakistan and its Draft Amendment no. 2 for Solar Power Projects. | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  | Only to be checked in list of deviations. |  |  |  | 1 |  | Open
Zte | JBS | Physical layout | Layout | Specific Requirements | 1.7.2 | Provide a schematic electrical Single Line Diagram (SLD) of the entire System layout from the modules to the grid-connection, identifying and listing all of the following DC and AC components. | 1 | P004 Single line diagram.pdf | 1 | [8 empty] | 1 |  | Pass
Zte | JBS | Physical layout | Layout | Specific Requirements | 1.7.2 | The system design shall be such as to ensure ease of maintenance and a multiple ring main unit (RMU) philosophy (on MV level) must be followed for circuit breaker configuration. | 1 | P004 Single line diagram.pdf | 1 | [8 empty] | 1 |  | Pass
Zte | MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Bills of Materials, BoMs: (glass, encapsulant, backsheet, ribbon, adhesives, cable, junction box, connector) | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Zte | MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Current at the maximum current point | 1 | \3-Response to Section 2\2-Schedules to Bid\Schedule F - Specific Operation Plant and Equipment Detail\3-Data Sheets, Instructions, Manuals\Module | 1 |  |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | [5 empty] | 1 |  | Pass
Zte | MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Degradation Curve from Manufacturer | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Zte | MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Manufacturers confirmation for the suitability of module for specific weather conditions and the high UV-radiation | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  | especially reliability at high UV irridiance / Product warranty | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Zte | MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Manufacturers installation guidelines | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | only LDK, not Suntech |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Zte | MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Materials and workmanship warranty of a minimum of 10 years | 1 | \3-Response to Section 2\2-Schedules to Bid\Schedule F - Specific Operation Plant and Equipment Detail\3-Data Sheets, Instructions, Manuals\Module | 1 |  |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | [5 empty] | 1 |  | Pass
Zte | MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Maximum rated power | 1 | \3-Response to Section 2\2-Schedules to Bid\Schedule F - Specific Operation Plant and Equipment Detail\3-Data Sheets, Instructions, Manuals\Module | 1 |  |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  |  |  |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | 1 |  | Pass
Zte | MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Maximum system voltage | 1 | \3-Response to Section 2\2-Schedules to Bid\Schedule F - Specific Operation Plant and Equipment Detail\3-Data Sheets, Instructions, Manuals\Module | 1 | [5 empty] | … at SK-II safety class |  |  | 1 |  | Pass
Zte | MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Minimum efficiency at 200 W/m² (25°, AM 1.5) | 1 | \3-Response to Section 2\2-Schedules to Bid\Schedule F - Specific Operation Plant and Equipment Detail\3-Data Sheets, Instructions, Manuals\Module | 1 |  |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | [5 empty] | 1 |  | Pass
Zte | MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Open-circuit voltage | 1 | \3-Response to Section 2\2-Schedules to Bid\Schedule F - Specific Operation Plant and Equipment Detail\3-Data Sheets, Instructions, Manuals\Module | 1 |  |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | [5 empty] | 1 |  | Pass
Zte | MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Operating temperature range and nominal operating cell temperature NOCT | 1 | \3-Response to Section 2\2-Schedules to Bid\Schedule F - Specific Operation Plant and Equipment Detail\3-Data Sheets, Instructions, Manuals\Module | 1 |  |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  | What range is acceptable | There is as small range anyway Will result in the PR losses |  |  | 1 |  | Pass
Zte | MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Power warranty/performance guarantee of a minimum of 25 years: the power output should not fall below 90% within 10 years, and below 80% within 25 years; linear warranty mandatory | 1 | \3-Response to Section 2\2-Schedules to Bid\Schedule F - Specific Operation Plant and Equipment Detail\3-Data Sheets, Instructions, Manuals\Module | 1 |  |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | [5 empty] | 1 |  | Pass
Zte | MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Provide guarantees and data sheets (to be transferred to Employer upon COD) | 1 | \3-Response to Section 2\2-Schedules to Bid\Schedule F - Specific Operation Plant and Equipment Detail\3-Data Sheets, Instructions, Manuals\Module | 1 | [8 empty] | 1 |  | Pass
Zte | MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Rated power tolerance | 1 | \3-Response to Section 2\2-Schedules to Bid\Schedule F - Specific Operation Plant and Equipment Detail\3-Data Sheets, Instructions, Manuals\Module | 1 |  |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  |  |  |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | 1 |  | Pass
Zte | MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Short-circuit current | 1 | \3-Response to Section 2\2-Schedules to Bid\Schedule F - Specific Operation Plant and Equipment Detail\3-Data Sheets, Instructions, Manuals\Module | 1 |  |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | [5 empty] | 1 |  | Pass
Zte | MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Specify number of modules and total MWp to be provided | 1 |  | 1 | [8 empty] | 1 |  | Pass
Zte | MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Tolerance to wind (maximum load) impact (mechanical load) | 1 | \3-Response to Section 2\2-Schedules to Bid\Schedule F - Specific Operation Plant and Equipment Detail\3-Data Sheets, Instructions, Manuals\Module | 1 |  |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  |  | minimum 2400 Pa |  |  | 1 |  | Pass
Zte | MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Type of cells comprising the module, and number of cells in series | 1 | \3-Response to Section 2\2-Schedules to Bid\Schedule F - Specific Operation Plant and Equipment Detail\3-Data Sheets, Instructions, Manuals\Module | 1 |  |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  |  | manufacturer |  |  | 1 |  | Pass
Zte | MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Voltage at the maximum power point | 1 | \3-Response to Section 2\2-Schedules to Bid\Schedule F - Specific Operation Plant and Equipment Detail\3-Data Sheets, Instructions, Manuals\Module | 1 |  |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | [5 empty] | 1 |  | Pass
Zte | JBS | Equipment guarantees | Modules | Guarantees | 1.28.1 | The Successful bidder shall provide a Module warranty of at least 10 years. The performance warranty of the module shall be linear with a fixed factor over 25 years. | 1 | 1. SoC to Bidding Document 30-01-14.pdf | 1 |  |  |  |  | To be discussed |  |  |  | 1 |  | Pass
Zte | MAW | Modules | Modules | Pre-shipment quality assurance | 1.14.4 | All modules must undergo Electroluminiscense (EL) inspection with a resolution of minimum 4 MPixel prior to shipment. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Cannot be evaluated at this stage. | compliance necessary | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Zte | MAW | Modules | Modules | Pre-shipment quality assurance | 1.14.7 | Warranties and evidence shall be given by the bidder that their selected modules have been tested for susceptibility to Potential Induced Degradation (PID). | 1 |  | 1 |  |  |  | LDK and Suntech |  |  |  |  | 1 |  | Pass
Zte | MAW | Modules | Modules | Pre-shipment quality assurance | 1.14.4 | A sufficient EVA cross linking has to be verified per production line through a gel content test supervised by an accredited (IEC 17025 or national pendant) independent certified module testing agency. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Cannot be evaluated at this stage. | compliance necessary | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Zte | MAW | Modules | Modules | Pre-shipment quality assurance | 1.14.4 | Pre-shipment flash tested data Quality assurance for PV modules on-site and in laboratory simulator must meet the class AAA requirements of IEC 60904-9. The sun simulator must be calibrated with a reference cell, which itself was calibrated by a member of the WPVS scheme, with a maximum uncertainty of Isc of 1%. unique barcode (SNr) and labelled performance headlines (P(mpp), I(sc), U(oc), I(mpp), U(mpp) maximum current, maximum voltage Positive power sorting | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Cannot be evaluated at this stage. | compliance necessary | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Zte | MAW | Modules | Modules | Quality assurance on site | 1.14.5 | The modules shall undergo an incoming inspection at arrival on construction site. | 1 |  |  |  | 1 |  |  | Cannot be evaluated at this stage. | stated and accepted | C |  | 1 |  | Open
Zte | MAW | Modules | Modules | Standards (as applicable to crystalline silicion or thin-film) | 1.14.3 | IEC 60364-4-41 | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? | no, just a statement of compliance 'protection against electric shock | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Zte | MAW | Modules | Modules | Standards (as applicable to crystalline silicion or thin-film) | 1.14.3 | IEC 60904-1, IEC 60904-3 | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? | no, just a statement of compliance | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Zte | MAW | Modules | Modules | Standards (as applicable to crystalline silicion or thin-film) | 1.14.3 | IEC 61215 | 1 | \3-Response to Section 2\2-Schedules to Bid\Schedule F - Specific Operation Plant and Equipment Detail\3-Data Sheets, Instructions, Manuals\Module |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | Suntech: ok, LDK: missing | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? | no, just a statement of compliance | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Zte | MAW | Modules | Modules | Standards (as applicable to crystalline silicion or thin-film) | 1.14.3 | IEC 61416 | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? | not existing | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Zte | MAW | Modules | Modules | Standards (as applicable to crystalline silicion or thin-film) | 1.14.3 | IEC 61646 | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? | no, just a statement of compliance | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Zte | MAW | Modules | Modules | Standards (as applicable to crystalline silicion or thin-film) | 1.14.3 | IEC 61701 | 1 | \3-Response to Section 2\2-Schedules to Bid\Schedule F - Specific Operation Plant and Equipment Detail\3-Data Sheets, Instructions, Manuals\Module | 1 |  |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? | no, just a statement of compliance |  |  | 1 |  | Pass
Zte | MAW | Modules | Modules | Standards (as applicable to crystalline silicion or thin-film) | 1.14.3 | IEC 61730 | 1 |  | 1 |  |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? | no, just a statement of compliance |  |  | 1 |  | Pass
Zte | MAW | Inverters | Monitoring | Functionalities | 1.18.3 | Advanced communication, with intelligent alerts/warnings, to the SCADA server | 1 | \3-Response to Section 2\2-Schedules to Bid\Schedule F - Specific Operation Plant and Equipment Detail\3-Data Sheets, Instructions, Manuals\Inverter\Datasheet |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Zte | JBS | Equipment guarantees | Mounting | Guarantees | 1.28.3 | The Successful Bidder shall provide a product warranty for the structure of at least 10 years. | 1 | 1. SoC to Bidding Document 30-01-14.pdf | 1 | [8 empty] | 1 |  | Pass
Zte | RM | Mounting | Mounting | Specific Requirements | 1.13.8 | The mounting structures must be earthed | 1 | P012 | 1 | [8 empty] | 1 |  | Pass
Zte | RM | Mounting | Mounting | Specific Requirements | 1.13.1 | The system is fixed-tilted. Tilt angle is specified. | 1 |  | 1 |  |  |  | 27° |  |  |  |  | 1 |  | Pass
Zte | RM | Mounting | Mounting | Specific Requirements | 1.13.5 | All fastening structures must be verified for durability and resistance to environmental degradation for 25 years | 1 |  |  |  | 1 | please confirm durability |  | What sort of mechanism is required for verification? | Sub structure description / materials double to line 172 - 175 |  |  | 1 |  | Open
Zte | RM | Mounting | Mounting | Specific Requirements | 1.13.3 | Mounting structure is made of durable material, resistant to sandstorms and compatible with the module frame material so as to avoid any adverse electrolytic/galvanic effects. | 1 | 1.TP | 1 |  |  |  |  | Information about materials to be known before evaluation. | right |  |  | 1 |  | Pass
Zte | RM | Mounting | Mounting | Specific Requirements | 1.13.3 | Mounting system resists corrosion (passing the salt spray test IEC 61701, among other verification), | 1 |  | 1 |  |  |  |  | Information about materials to be known before evaluation. | right |  |  | 1 |  | Pass
Zte | RM | Mounting | Mounting | Specific Requirements | 1.13.3 | Mounting system resists high wind speeds (up to 40 m/s) | 1 |  | 1 | [8 empty] | 1 |  | Pass
Zte | RM | Mounting | Mounting | Specific Requirements | 1.13.3 | Mounting system resists UV induced degradation | 1 |  | 1 | [8 empty] | 1 |  | Pass
Zte | RM | Mounting | Mounting | Specific Requirements | 1.13.9 | Specific site conditions have been considered. | 1 |  | 1 |  |  |  |  | Needs to be discussed. | … specific requirements of the soil conditions Static |  |  | 1 |  | Pass
Zte | JBU | Step-up Transformers/MV Switchgear | MV Switchgear | Design factors to be provided | 1.21.4 | Rated lightning impulse voltage | 1 |  | 1 | [8 empty] | 1 |  | Pass
Zte | JBU | Step-up Transformers/MV Switchgear | MV Switchgear | Design factors to be provided | 1.21.4 | Rated power frequency withstand voltage | 1 |  | 1 | [8 empty] | 1 |  | Pass
Zte | JBU | Step-up Transformers/MV Switchgear | MV Switchgear | Design factors to be provided | 1.21.4 | Rated short circuit current | 1 |  | 1 | [8 empty] | 1 |  | Pass
Zte | JBU | Step-up Transformers/MV Switchgear | MV Switchgear | Design factors to be provided | 1.21.4 | System maximum voltage | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  |  |  | C |  | 1 |  | Open
Zte | JBU | Step-up Transformers/MV Switchgear | MV Switchgear | Design factors to be provided | 1.21.4 | System nominal voltage | 1 |  | 1 | [8 empty] | 1 |  | Pass
Zte | JBU | Step-up Transformers/MV Switchgear | MV Switchgear | Specific Requirements | 1.21.4 | Interlocks will also be mechanically interlocked between line MV switchgears. | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  |  |  | C |  | 1 |  | Open
Zte | JBU | Step-up Transformers/MV Switchgear | MV Switchgear | Specific Requirements | 1.21.4 | MV Switchgears shall be SF6 gas insulated or VCB (Vacuum circuit breaker). | 1 |  | 1 | [8 empty] | 1 |  | Pass
Zte | JBU | Step-up Transformers/MV Switchgear | MV Switchgear | Specific Requirements | 1.21.4 | The separating equipment shall be installed with visible disconnection (pivotable disconnectors). | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  | Cannot be evaluated at this stage |  | C |  | 1 |  | Open
Zte | JBU | Step-up Transformers/MV Switchgear | MV Switchgear | Standards | 1.21.5 | IEC 60529 | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  | C |  | 1 |  | Open
Zte | JBU | Step-up Transformers/MV Switchgear | MV Switchgear | Standards | 1.21.5 | IEC 62271-200 | 1 |  | 1 |  |  |  |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  |  |  | 1 |  | Pass
Zte | JBU | Step-up Transformers/MV Switchgear | MV Switchgear | Standards | 1.21.5 | IEC 62446 | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  | C |  | 1 |  | Open
Zte | JUE | Deactivation | O&M | Allowed deactivation periods | 2.6.1 | Approved by The Employer to ensure consideration of Employer's obligations | 2 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing |  |  |  |  | 1 |  | Open
Zte | JUE | Deactivation | O&M | Allowed deactivation periods | 2.6.1 | Approved from grid operator | 2 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing |  |  |  |  | 1 |  | Open
Zte | JUE | Deactivation | O&M | Allowed deactivation periods | 2.6.1 | Times with irradiation level < 300 W/m² | 2 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing |  |  |  |  | 1 |  | Open
Zte | JUE | Main Annual Inspection | O&M | Auxiliary system | 2.4.5 | If existing: inspection of requirements out of the building permit | 2 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing |  |  |  |  | 1 |  | Open
Zte | JUE | Main Annual Inspection | O&M | Auxiliary system | 2.4.5 | Inspection of security system inclusive fence, all gates, all cameras etc. Random test of the fence fastening, if necessary retightening of the screws | 2 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing |  |  |  |  | 1 |  | Open
Zte | JUE | Main Annual Inspection | O&M | Auxiliary system | 2.4.5 | Maintenance of all components according to manufacturer instruction | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing |  |  |  |  | 1 |  | Open
Zte | JUE | Initial Inspection | O&M | General Requirements | 2.2.2 | Maintenance routines, inspection check-lists, working files, | 1 |  |  |  | 1 | Unclear: We do not understand your proposal, please detail your proposal. Especially confirm that you are compliant with our requested criteria. | not completely described |  |  |  |  | 1 |  | Open
Zte | JUE | Scope of the Bid | O&M | General Requirements | 2.1.2 | Cleaning of Modules and irradiation sensors to prevent dust accumulation to undesirable level. | 1 |  |  |  | 1 | Unclear: We do not understand your proposal, please detail your proposal. Especially confirm that you are compliant with our requested criteria. | not correct described |  |  |  |  | 1 |  | Open
Zte | JUE | Scope of the Bid | O&M | General Requirements | 2.1.2 | Cleaning of the Plant, preventive and corrective maintenance of the civil works and the fences. | 1 |  |  |  | 1 | Unclear: We do not understand your proposal, please detail your proposal. Especially confirm that you are compliant with our requested criteria. | not correct described |  |  |  |  | 1 |  | Open
Zte | JUE | Initial Inspection | O&M | General Requirements | 2.2.3 | coordinate with the Employer and keep him updated regarding his progress of preparation, status of construction, pending issues of Construction, Commissioning and testing. | 2 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | Cannot be evaluated at this stage |  |  |  |  | 1 |  | Open
Zte | JUE | Scope of the Bid | O&M | General Requirements | 2.1.2 | Coordination and compliance with NTDC requirements | 1 |  | 1 | [8 empty] | 1 |  | Pass
Zte | JUE | Scope of the Bid | O&M | General Requirements | 2.1.2 | Corrective maintenance with guaranteed response times | 1 |  |  |  | 1 | Unclear: We do not understand your proposal, please detail your proposal. Especially confirm that you are compliant with our requested criteria. | not correct described |  |  |  |  | 1 |  | Open
Zte | JUE | Scope of the Bid | O&M | General Requirements | 2.1.2 | Daily, monthly and yearly performance and production reporting | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | no reporting is described |  |  |  |  | 1 |  | Open
Zte | JUE | Initial Inspection | O&M | General Requirements | 2.2.1 | familiarize himself with the specific plant equipment and specific maintenance requirements / training of staff | 1 | 3. Operation & Maintenance Services Proposal_v1.0_20140218.pdf 3.1 Page 13 |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 3 3.1 Inspection personnel should be trained and get certificate. |  |  |  |  | 1 |  | Open
Zte | JUE | Scope of the Bid | O&M | General Requirements | 2.1.2 | Insuring products at different levels but for sensible costs; the insurance policy shall not become expensive compared to the replacement cost of the item | 3 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing |  |  |  |  | 1 |  | Open
Zte | JUE | Scope of the Bid | O&M | General Requirements | 2.1.2 | Maintaining a customer support hotline for the Employer/NTDC | 3 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing |  |  |  |  | 1 |  | Open
Zte | JUE | Scope of the Bid | O&M | General Requirements | 2.1.2 | Maintaining adequate reserves for timely replacement | 2 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing |  |  |  |  | 1 |  | Open
Zte | JUE | Scope of the Bid | O&M | General Requirements | 2.1.2 | Negotiating a warranty reserve for replacements with the suppliers | 3 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing |  |  |  |  | 1 |  | Open
Zte | JUE | Scope of the Bid | O&M | General Requirements | 2.1.2 | On site Security services. | 3 |  |  |  | 1 | Unclear: We do not understand your proposal, please detail your proposal. Especially confirm that you are compliant with our requested criteria. | not completely described |  |  |  |  | 1 |  | Open
Zte | JUE | Scope of the Bid | O&M | General Requirements | 2.1.2 | Operation of the Plant (including 24/7 presence of O&M and security staff on the project site). | 1 |  | 1 | [8 empty] | 1 |  | Pass
Zte | JUE | Scope of the Bid | O&M | General Requirements | 2.1.2 | Optimal level of SCADA monitoring | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us | [5 empty] | 1 |  | Open
Zte | JUE | Scope of the Bid | O&M | General Requirements | 2.1.2 | Ordinary road and land maintenance to the extent required for proper maintenance of the Plant. | 3 |  |  |  | 1 | Unclear: We do not understand your proposal, please detail your proposal. Especially confirm that you are compliant with our requested criteria. | not described |  |  |  |  | 1 |  | Open
Zte | JUE | Scope of the Bid | O&M | General Requirements | 2.1.2 | Performance variance analysis of the module strings and inverters | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing |  |  |  |  | 1 |  | Open
Zte | JUE | Scope of the Bid | O&M | General Requirements | 2.1.2 | Periodic maintenance of inverter, transformer, combiner boxes etc., according manufacturer's requirements | 1 |  |  |  | 1 | Unclear: We do not understand your proposal, please detail your proposal. Especially confirm that you are compliant with our requested criteria. | no period is described |  |  |  |  | 1 |  | Open
Zte | JUE | Scope of the Bid | O&M | General Requirements | 2.1.2 | Preventive maintenance | 2 |  | 1 | [8 empty] | 1 |  | Pass
Zte | JUE | Scope of the Bid | O&M | General Requirements | 2.1.2 | Provide all O&M Staff, trained and certified as far as applicable. For security reasons, a 24 h/ 7 days a week staffing of security and maintenance shall be provided. The staffing concept and selected key employees shall be presented to the Employer for approval. | 1 | 2. Operation & Maintenance Services Proposal_v1.0_20140218.pdf 3.1 Page 13 |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 3 3.1 Inspection personnel should be trained and get certificate. |  |  |  |  | 1 |  | Open
Zte | JUE | Scope of the Bid | O&M | General Requirements | 2.1.2 | Providing regular reports of repairs, maintenance, and tests | 3 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing |  |  |  |  | 1 |  | Open
Zte | JUE | Scope of the Bid | O&M | General Requirements | 2.1.2 | Provision and Installation of spare parts, keeping of spare parts stock (refill of used spares). Reporting of status and consumption to be continuously updated | 2 |  |  |  | 1 | Unclear: We do not understand your proposal, please detail your proposal. Especially confirm that you are compliant with our requested criteria. | not completely described |  |  |  |  | 1 |  | Open
Zte | JUE | Scope of the Bid | O&M | General Requirements | 2.1.2 | Reporting the monitoring and surveillance system. | 3 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing |  |  |  |  | 1 |  | Open
Zte | JUE | Scope of the Bid | O&M | General Requirements | 2.1.2 | Responsibility to keep Performance Ratio and Availability at highest levels | 1 |  | 1 | [8 empty] | 1 |  | Pass
Zte | JUE | Scope of the Bid | O&M | General Requirements | 2.1.2 | Scheduled maintenance routines: e.g., inspections of modules with polarized sunglasses to check for discolouration, the first signs of de-lamination, loose wires in the electronics, corrosion of mounting structures, erosion | 1 |  | 1 | [8 empty] | 1 |  | Pass
Zte | JUE | Scope of the Bid | O&M | General Requirements | 2.1.2 | Smooth functioning of all interconnections and data communications of the system performance | 2 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing |  |  |  |  | 1 |  | Open
Zte | JUE | Scope of the Bid | O&M | General Requirements | 2.1.2 | Technical report elaboration. | 3 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing |  |  |  |  | 1 |  | Open
Zte | JUE | Scope of the Bid | O&M | General Requirements | 2.1.2 | Track chronic negative deviations in the module string output, i.e., power tolerances consistently in the negative | 3 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing |  |  |  |  | 1 |  | Open
Zte | JUE | Scope of the Bid | O&M | General Requirements | 2.1.2 | Warranties and insurance policies should be assignable/transferrable to the Employer in case it decides to take over the O&M | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing |  |  |  |  | 1 |  | Open
Zte | MAW | Inverters | O&M | Guarantees | 1.18.2 | For central inverters concept: the bidder shall ensure with an undertaking from the manufacturer that the concerned skilled staff will be made available at the site within 24 hours of reporting the defect to the manufacturer. | 1 | \3-Response to Section 2\2-Schedules to Bid\Schedule F - Specific Operation Plant and Equipment Detail\3-Data Sheets, Instructions, Manuals\Inverter\Datasheet |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Zte | JUE | Main Annual Inspection | O&M | Inverter (100%) | 2.4.2 | Check of control and auxiliary voltages | 2 |  | 1 | [8 empty] | 1 |  | Pass
Zte | JUE | Main Annual Inspection | O&M | Inverter (100%) | 2.4.2 | Check of the safety circuit for the interruption of the AC-grid protection in the case of failure (emergency shut-off, over-/ under-voltage, over temperature, etc.) based on the local conditions | 1 |  | 1 | [8 empty] | 1 |  | Pass
Zte | JUE | Bi-annual inspection | O&M | Inverter (100%) | 2.3.2 | Cleaning of the filter mats in the air leaks | 2 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing |  |  |  |  | 1 |  | Open
Zte | JUE | Main Annual Inspection | O&M | Inverter (100%) | 2.4.2 | Functional check of internal and external over- and under-voltage monitoring through operation of test terminal | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing |  |  |  |  | 1 |  | Open
Zte | JUE | Main Annual Inspection | O&M | Inverter (100%) | 2.4.2 | Functional check of insulation monitoring | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing |  |  |  |  | 1 |  | Open
Zte | JUE | Bi-annual inspection | O&M | Inverter (100%) | 2.3.2 | Functional check of ventilator system of inverter station | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing |  |  |  |  | 1 |  | Open
Zte | JUE | Main Annual Inspection | O&M | Inverter (100%) | 2.4.2 | Inspection of over-voltage protection and upstream fuses regarding external damage | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing |  |  |  |  | 1 |  | Open
Zte | JUE | Bi-annual inspection | O&M | Inverter (100%) | 2.3.2 | Inspection of the interior of the electrical cabinet regarding dust deposit, dirtiness, humidity, water penetration from outside. If necessary the cabinet has to be cleaned. | 1 |  | 1 | [8 empty] | 1 |  | Pass
Zte | JUE | Main Annual Inspection | O&M | Inverter (100%) | 2.4.2 | Maintenance of inverters according to manufacturer instruction | 1 |  |  |  | 1 | Unclear: We do not understand your proposal, please detail your proposal. Especially confirm that you are compliant with our requested criteria. | not completely described |  |  |  |  | 1 |  | Open
Zte | JUE | Bi-annual inspection | O&M | Inverter (100%) | 2.3.2 | Maintenance of inverters according to manufacturer's instruction. | 1 |  |  |  |  | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing |  |  |  |  | 0 |  | Open
Zte | JUE | Bi-annual inspection | O&M | Inverter (100%) | 2.3.2 | Replacement of dirty filter mats | 2 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing |  |  |  |  | 1 |  | Open
Zte | JUE | Main Annual Inspection | O&M | Inverter (100%) | 2.4.2 | Test of the internal miniature circuit breakers and power switch, test of emergency shut-off | 1 |  | 1 | [8 empty] | 1 |  | Pass
Zte | JUE | Bi-annual inspection | O&M | Inverter (100%) | 2.3.2 | Testing of inverter features according to maintenance schedule of manufacturer. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing |  |  |  |  | 1 |  | Open
Zte | JUE | Main Annual Inspection | O&M | Inverter (100%) | 2.4.2 | Visual inspection of AC and DC clamps regarding tightness and colouring, tightening of clamps | 1 |  | 1 | [8 empty] | 1 |  | Pass
Zte | JUE | Main Annual Inspection | O&M | Inverter (100%) | 2.4.2 | Visual inspection of all fuses | 1 |  |  |  | 1 | Unclear: We do not understand your proposal, please detail your proposal. Especially confirm that you are compliant with our requested criteria. | not completely described |  |  |  |  | 1 |  | Open
Zte | JUE | Bi-annual inspection | O&M | Maintenance | 2.3.3 | Maintenance of all Power plant components according to manufacturer's instructions | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing |  |  |  |  | 1 |  | Open
Zte | JUE | Bi-annual inspection | O&M | Monitoring | 2.3.3 | Functionality testing of the monitoring system | 3 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing |  |  |  |  | 1 |  | Open
Zte | JUE | Bi-annual inspection | O&M | PV Generator | 2.3.1 | 100% visual inspection of modules regarding damage in spring | 1 |  |  |  | 1 | Unclear: We do not understand your proposal, please detail your proposal. Especially confirm that you are compliant with our requested criteria. | not completely described |  |  |  |  | 1 |  | Open
Zte | JUE | Bi-annual inspection | O&M | PV Generator | 2.3.1 | Cleaning of all modules | 1 |  | 1 | [8 empty] | 1 |  | Pass
Zte | JUE | Bi-annual inspection | O&M | PV Generator | 2.3.1 | Cleaning of sensors and switches | 1 |  |  |  |  | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | sensors shall be done by independent Meteo Station Operator |  |  |  |  | 0 |  | Open
Zte | JUE | Bi-annual inspection | O&M | PV Generator | 2.3.1 | Documentation of wear and tear of moving components, monitoring of dust intrusion and corrosion. | 2 |  | 1 | [8 empty] | 1 |  | Pass
Zte | JUE | Main Annual Inspection | O&M | PV Generator | 2.4.1 | Inspection of DC distribution box: Visual inspection of all clamps and degree of pollution. Testing of over-voltage protection | 1 |  | 1 | [8 empty] | 1 |  | Pass
Zte | JUE | Main Annual Inspection | O&M | PV Generator | 2.4.1 | Maintenance of sensors based on manufacturer’s instructions | 1 |  |  |  | 1 | [6 empty] | 1 |  | Open
Zte | JUE | Bi-annual inspection | O&M | PV Generator | 2.3.1 | Random check of module clip with respect to loosening; if necessary replacement of clips (min. 10%, documentation of location, during 5 years inspection of whole PV plant) | 2 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | Cannot be evaluated at this stage missing |  |  |  |  | 1 |  | Open
Zte | JUE | Bi-annual inspection | O&M | PV Generator | 2.3.1 | Random testing of the steadiness of the mounting foundation/system and random inspection regarding corrosion at substructure (min. 10%, documentation of location, during 10 years inspection of whole PV plant) | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing |  |  |  |  | 1 |  | Open
Zte | JUE | Bi-annual inspection | O&M | PV Generator | 2.3.1 | Random visual inspection of modules regarding damage in autumn | 2 |  |  |  | 1 |  | Cannot be evaluated at this stage |  |  |  |  | 1 |  | Open
Zte | JUE | Main Annual Inspection | O&M | PV Generator | 2.4.1 | Visual inspection of all accessible cable trenches and cable trays regarding damage | 1 |  | 1 | [8 empty] | 1 |  | Pass
Zte | JUE | Main Annual Inspection | O&M | PV Generator | 2.4.1 | Visual inspection and random testing of string connector (min. 10% with Documentation of location , during 10 years testing of whole PV plant) | 1 |  | 1 | [8 empty] | 1 |  | Pass
Zte | JUE | Main Annual Inspection | O&M | Roads | 2.4.3 | Visual inspection of roads within the PV plant shall be carried out to ascertain that these are maintained in good condition for the intended purpose. | 2 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing |  |  |  |  | 1 |  | Open
Zte | JUE | On-site monitoring | O&M | Specific Requirements | 2.9.2 | Bidder shall arrange service contracts with specialized sub-contractors | 2 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing |  |  |  |  | 1 |  | Open
Zte | JUE | Reaction to Fault Messages / Response Times | O&M | Specific Requirements | 2.11.1 | Every fault message has to be registered in the monitoring software. According to the fault message, the Bidder shall issue a fault diagnosis within a response time of 2 hours (24/7) | 1 |  |  |  | 1 | Unclear: We do not understand your proposal, please detail your proposal. Especially confirm that you are compliant with our requested criteria. | not completely described |  |  |  |  | 1 |  | Open
Zte | JUE | Fault Management / Warranty defects | O&M | Specific Requirements | 2.12.5 | Operational defects, which are not considered as warranty defects - see repair works section below | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing |  |  |  |  | 1 |  | Open
Zte | JUE | Fault Calls | O&M | Specific Requirements | 2.13.2 | The minimum response time in case of failure must meet the EPA requirements | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing |  |  |  |  | 1 |  | Open
Zte | JUE | Remote Supervision | O&M | Specific Requirements | 2.10.6 | The remote supervision shall also include the taking of measures for removal of faults. | 2 |  |  |  | 1 | Unclear: We do not understand your proposal, please detail your proposal. Especially confirm that you are compliant with our requested criteria. | not completely described |  |  |  |  | 1 |  | Open
Zte | JUE | Spare Parts and Tools | O&M | Specific Requirements | 2.14 | provide the necessary set of spare parts and maintenance tools as required to perform the services | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing |  |  |  |  | 1 |  | Open
Zte | JUE | Fault Calls | O&M | Specific Requirements | 2.13.2 | --> Time Model: Response Times for Priorities 1-3 (12h / 24h / 1 week) | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing |  |  |  |  | 1 |  | Open
Zte | JUE | Fault Management / Warranty defects | O&M | Specific Requirements | 2.12.6 | All defects shall be documented within the same day of detection, | 2 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing |  |  |  |  | 1 |  | Open
Zte | JUE | Working Time | O&M | Specific Requirements | 2.17 | All working times of Bidders personnel shall be included in the Bidders annual remuneration. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing |  |  |  |  | 1 |  | Open
Zte | JUE | Deactivation | O&M | Specific Requirements | 2.6.2 | All deactivations during maintenance works shall be completely documented. | 2 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing |  |  |  |  | 1 |  | Open
Zte | JUE | On-site monitoring | O&M | Specific Requirements | 2.9.3 | All operational data shall be logged on-site in parallel to the remote data storage | 2 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing |  |  |  |  | 1 |  | Open
Zte | JUE | Documentation | O&M | Specific Requirements | 2.19 | All repair works and compensations shall have to be documented and to be submitted to the Employer within two weeks. | 2 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing |  |  |  |  | 1 |  | Open
Zte | JUE | Remote Supervision | O&M | Specific Requirements | 2.10.2 | Any reductions in performance shall have to be logged. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing |  |  |  |  | 1 |  | Open
Zte | JUE | Special inspection (every 4 years) | O&M | Specific Requirements | 2.5.1 | Control of station equipment | 2 |  | 1 | [8 empty] | 1 |  | Pass
Zte | JUE | Performance of maintenance and repair works | O&M | Specific Requirements | 2.8.1 | Corresponding regulations of the respective component manufacturer shall have to be followed during maintenance works | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing |  |  |  |  | 1 |  | Open
Zte | JUE | Spare Parts and Tools | O&M | Specific Requirements | 2.14.1 | cover all cost for supply and re-stocking of spare parts from his annual remuneration. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing |  |  |  |  | 1 |  | Open
Zte | JUE | Deactivation | O&M | Specific Requirements | 2.6.3 | Deactivation shall not be considered as permitted downtime. | 2 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing |  |  |  |  | 1 |  | Open
Zte | JUE | Performance of maintenance and repair works | O&M | Specific Requirements | 2.8.5 | During his work the Bidder shall be held responsible for the public safety of the PV plant | 2 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing |  |  |  |  | 1 |  | Open
Zte | JUE | Approval | O&M | Specific Requirements | 2.18 | Extensive repairs have to be approved by the Employer. | 2 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing |  |  |  |  | 1 |  | Open
Zte | JUE | Fault Calls | O&M | Specific Requirements | 2.13.3 | failure time response does not match the response time of EPA >> failure time response does not match the response time of EPA | 3 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing |  |  |  |  | 1 |  | Open
Zte | JUE | Fault Calls | O&M | Specific Requirements | 2.13.5 | Fault calls can be performed without prior consent of the Employer. | 3 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing |  |  |  |  | 1 |  | Open
Zte | JUE | Fault Management / Warranty defects | O&M | Specific Requirements | 2.12.3 | Fault Management = without repair works | 3 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing |  |  |  |  | 1 |  | Open
Zte | JUE | Fault Management / Warranty defects | O&M | Specific Requirements | 2.12.1 | Fault Management: all handling and communication | 2 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing |  |  |  |  | 1 |  | Open
Zte | JUE | Fault Management / Warranty defects | O&M | Specific Requirements | 2.12.2 | Fault Management: Handling / correspondence with third parties | 2 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing |  |  |  |  | 1 |  | Open
Zte | JUE | Ground Maintenance | O&M | Specific Requirements | 2.21 | Ground maintenance shall include all procedures that are necessary to avoid module shading and an incorrect operation of the trackers. This shall include the levelling of sand drifts. Necessary switching operations shall be coordinated by the Bidder with responsible authorities | 2 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing |  |  |  |  | 1 |  | Open
Zte | JUE | Reduced Output of the Plant | O&M | Specific Requirements | 2.15.1 | Identified reduced output shall be justified. Reduced output shall be recovered and liquidated damages determined. | 1 |  |  |  | 1 |  | missing liquidated --> means --> performance |  |  |  |  | 1 |  | Open
Zte | JUE | Fault Calls | O&M | Specific Requirements | 2.13.6 | If the elimination of faults is not possible within the response time / and additional travelling, this is Repair Work | 3 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing |  |  |  |  | 1 |  | Open
Zte | JUE | Special inspection (every 4 years) | O&M | Specific Requirements | 2.5.1 | Measurement of inverters and generators according to recognized international standards and according to results from commissioning certificates (insulation, loop resistance, earthing, DC-open circuit voltage) | 2 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing |  |  |  |  | 1 |  | Open
Zte | JUE | Remote Supervision | O&M | Specific Requirements | 2.10.8 | Monthly / quarterly and annual reports based on the data of the remote supervision provided to the Employer 4 weeks after the last period of reporting at the latest. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing |  |  |  |  | 1 |  | Open
Zte | JUE | Reduced Output of the Plant | O&M | Specific Requirements | 2.15 | Monthly comparison of the specific performance of all measuring channels among each other. 5% reduced output results in general check of all the channels and shall be documented. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing |  |  |  |  | 1 |  | Open
Zte | JUE | Performance of maintenance and repair works | O&M | Specific Requirements | 2.8.4 | Observe and respect the local law, regulations and international PV standards. | 3 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing |  |  |  |  | 1 |  | Open
Zte | JUE | Performance of maintenance and repair works | O&M | Specific Requirements | 2.8.3 | Observe and respect the maintenance and operation specifications of the manufacturer of the components | 3 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing |  |  |  |  | 1 |  | Open
Zte | JUE | Special inspection (every 4 years) | O&M | Specific Requirements | 2.5.1 | Oil check of transformers | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing |  |  |  |  | 1 |  | Open
Zte | JUE | Remote Supervision | O&M | Specific Requirements | 2.10.1 | On-call service provided for the Employer for availability outside business hours and during weekends (24/7). | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing |  |  |  |  | 1 |  | Open
Zte | JUE | On-site monitoring | O&M | Specific Requirements | 2.9.1 | Permanent (24/7) staffing of the Power Plant, consisting of security and O&M personnel. | 1 |  | 1 | [8 empty] | 1 |  | Pass
Zte | JUE | Fault Management / Warranty defects | O&M | Specific Requirements | 2.12.4 | Product warranties in favour of contractor / Bidder (responsible) to claim all warranties for at least 5 years | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing |  |  |  |  | 1 |  | Open
Zte | JUE | Reaction to Fault Messages / Response Times | O&M | Specific Requirements | 2.11.2 | profit relevant Fault Events: Downtime registration/ reasons/ repair/ in monthly report (blanc of monthly report?) | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing |  |  |  |  | 1 |  | Open
Zte | JUE | Special inspection (every 4 years) | O&M | Specific Requirements | 2.5.1 | Protection systems of medium voltage switching panels of the stations | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing |  |  |  |  | 1 |  | Open
Zte | JUE | Spare Parts and Tools | O&M | Specific Requirements | 2.14.2 | refill spare parts immediately after consumption | 2 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing |  |  |  |  | 1 |  | Open
Zte | JUE | Repair time and cost | O&M | Specific Requirements | 2.16 | Repair times are considered as part of the availability guaranty of the Bidder. All cost of repair shall be part of the Bidders annual remuneration. For the avoidance of doubt that includes any repairs due to lightening, theft and vandalism. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing |  |  |  |  | 1 |  | Open
Zte | JUE | Performance of maintenance and repair works | O&M | Specific Requirements | 2.8.2 | Report document for maintenance works (blanc sample requiered for bid) | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing |  |  |  |  | 1 |  | Open
Zte | JUE | Person in Control of PV plant | O&M | Specific Requirements | 2.22 | The Bidder shall propose an organigram for the O& M personnel with one main responsible | 2 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing |  |  |  |  | 1 |  | Open
Zte | JUE | Remote Supervision | O&M | Specific Requirements | 2.10.7 | The Bidder shall provide to the Employer permanent online access to the power plant control system for parallel monitoring | 1 |  |  |  | 1 | [6 empty] | 1 |  | Open
Zte | JUE | On-site monitoring | O&M | Specific Requirements | 2.9.4 | The data of irradiation sensors shall be monitored by an independent expert on a continuous basis | 2 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing |  |  |  |  | 1 |  | Open
Zte | JUE | Remote Supervision | O&M | Specific Requirements | 2.10.4 | The data shall present the status of the plant such as the performance ratio annual overview and the current feed-in power | 2 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing |  |  |  |  | 1 |  | Open
Zte | JUE | Fault Calls | O&M | Specific Requirements | 2.13.1 | The scope of service shall include any working times for all fault calls including travelling times and costs. | 1 |  |  |  | 1 | Unclear: We do not understand your proposal, please detail your proposal. Especially confirm that you are compliant with our requested criteria. | not completely described |  |  |  |  | 1 |  | Open
Zte | JUE | Reporting | O&M | Specific Requirements | 2.23 | The Bidder shall deliver to the Employer regular reports on monthly, quarterly and annual basis. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing |  |  |  |  | 1 |  | Open
Zte | JUE | Remote Supervision | O&M | Specific Requirements | 2.10.3 | The data will comprise, apart from electrical parameters of the PV plant: currents, voltages, irradiation values, kind and period of reductions in performance such as curtailment by the grid operator | 2 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing |  |  |  |  | 1 |  | Open
Zte | JUE | Inspection of Repair Works | O&M | Specific Requirements | 2.20 | The Employer can inspect the repair works within one month (30 days) after receiving the documentation | 2 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing |  |  |  |  | 1 |  | Open
Zte | JUE | Fault Calls | O&M | Specific Requirements | 2.13.4 | The fault call shall include the fault diagnosis on site as well as an immediate error correction if possible. The fault shall have to be corrected within the response time and, failing this, a diagnosis of the fault has to be effect indicating further measures. | 2 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing |  |  |  |  | 1 |  | Open
Zte | JUE | Remote Supervision | O&M | Specific Requirements | 2.10.9 | The fees for telephone connection and/or data transfer services are included in the annual remuneration. | 2 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing |  |  |  |  | 1 |  | Open
Zte | JUE | Remote Supervision | O&M | Specific Requirements | 2.10.5 | The remote supervision shall also control the operation of the PV plant. | 2 |  |  |  | 1 | Unclear: We do not understand your proposal, please detail your proposal. Especially confirm that you are compliant with our requested criteria. | not completely described |  |  |  |  | 1 |  | Open
Zte | JUE | Change of Inspection and Maintenance Work procedures | O&M | Specific Requirements | 2.7 | work in accordance with all applicable laws | 2 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing |  |  |  |  | 1 |  | Open
Zte | JUE | Main Annual Inspection | O&M | Substation and Transmission Line | 2.4.4 | Maintenance of substation and transmission line according to manufacturer instruction | 1 |  |  |  | 1 | Unclear: We do not understand your proposal, please detail your proposal. Especially confirm that you are compliant with our requested criteria. | not completely described |  |  |  |  | 1 |  | Open
Zte | JUE | Main Annual Inspection | O&M | Substation and Transmission Line | 2.4.4 | Visual inspection of transformer and switchboard rooms and cleaning if necessary | 1 |  |  |  | 1 | Unclear: We do not understand your proposal, please detail your proposal. Especially confirm that you are compliant with our requested criteria. | not completely described |  |  |  |  | 1 |  | Open
Zte | JUE | Main Annual Inspection | O&M | Substation and Transmission Line | 2.4.4 | Visual inspection of Transmission Line and report of damage to the grid operator | 2 |  |  |  | 1 | Unclear: We do not understand your proposal, please detail your proposal. Especially confirm that you are compliant with our requested criteria. | not completely described |  |  |  |  | 1 |  | Open
Zte | JBS | Physical layout | Physical layout plan | Specific Requirements | 1.7.7 | Detailed top view of the PV mounting structure, including module sizes and spacing between the module rows | 1 | P002 PV module support structure.pdf, P003 PV array layout.pdf | 1 | [8 empty] | 1 |  | Pass
Zte | JBS | Physical layout | Physical layout plan | Specific Requirements | 1.7.7 | Detailed view of the distribution of inverters and connections to the PV string/array | 1 | P001 100MW PV Power plant layout.pdf, P006 1 MWp PV generation subsystem.pdf | 1 | [8 empty] | 1 |  | Pass
Zte | JBS | Physical layout | Physical layout plan | Specific Requirements | 1.7.7 | Detailed side and front view of the PV mounting structure | 1 | P002 PV module support structure.pdf | 1 |  |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | [5 empty] | 1 |  | Pass
Zte | JBS | Physical layout | Physical layout plan | Specific Requirements | 1.7.7 | Detailed top view of electrical cabling interconnections | 1 |  | 1 |  |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | [5 empty] | 1 |  | Pass
Zte | JBS | Physical layout | Physical layout plan | Specific Requirements | 1.7.7 | Floor plans and elevations for all buildings, housing units, containers on site: e.g. , substations, the SCADA operational room, inverters, O&M, storage facilities | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  |  |  | U |  | 1 |  | Open
Zte | JBS | Physical layout | Physical layout plan | Specific Requirements | 1.7.7 | Location of the system metering and grid connection point | 1 | P004 Single line diagram.pdf | 1 |  |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | [5 empty] | 1 |  | Pass
Zte | JBS | Power plant documentation | Power plant documentation | Quality Assurance | 1.27.1 | Flash report list of all modules shall be provided in digital form. | 1 | 1. SoC to Bidding Document 30-01-14.pdf | 1 | [8 empty] | 1 |  | Pass
Zte | JBS | Power plant documentation | Power plant documentation | Quality Assurance | 1.27.1 | The Bidder shall confirm that the complete as-built documentation of the plant will be provided in compliance with IEC 62446. Additionally all module serial numbers shall be listed with their individual location. | 1 | 1. SoC to Bidding Document 30-01-14.pdf | 1 |  |  |  |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  |  |  | 1 |  | Pass
Zte | JBS | Workflow, Project Management Plan and Timelines | Project schedule / Project management | Project schedule | 1.8.1 | Interdependencies between the tasks | 1 | 1. Time Schedule for QA Soar Park.pdf | 1 | [8 empty] | 1 |  | Pass
Zte | JBS | Workflow, Project Management Plan and Timelines | Project schedule / Project management | Project schedule | 1.8.1 | Interdependencies of tasks with equipment order and delivery times | 1 | 1. Time Schedule for QA Soar Park.pdf | 1 | [8 empty] | 1 |  | Pass
Zte | JBS | Workflow, Project Management Plan and Timelines | Project schedule / Project management | Project schedule | 1.8.1 | Key milestones to indicate that the progress in on schedule | 1 | 1. Time Schedule for QA Soar Park.pdf | 1 | [8 empty] | 1 |  | Pass
Zte | JBS | Workflow, Project Management Plan and Timelines | Project schedule / Project management | Project schedule | 1.8.1 | Provide installation schedule in compliance with sub-clause 8.2 of Particular Conditions (Time for Completion is 225 days after Commencement Date). | 1 | 1. Time Schedule for QA Soar Park.pdf | 1 |  |  |  |  | Find sub-clause 8.2 of Particular Conditions |  |  |  | 1 |  | Pass
Zte | JBS | Workflow, Project Management Plan and Timelines | Project schedule / Project management | Project schedule | 1.8.1 | Provide work breakdown structures, activity decomposition and sequencing and dependability with the baseline schedule clearly showing the critical path | 1 | 1. Time Schedule for QA Soar Park.pdf | 1 | [8 empty] | 1 |  | Pass
Zte | JBS | Workflow, Project Management Plan and Timelines | Project schedule / Project management | Project schedule | 1.8.1 | Schedule of tasks | 1 | 1. Time Schedule for QA Soar Park.pdf | 1 | [8 empty] | 1 |  | Pass
Zte | JBS | Workflow, Project Management Plan and Timelines | Project schedule / Project management | Project schedule | 1.8.1 | Teams, the number and skills of personnel to be deployed for each task | 1 | Implementation proposal-0218.pdf |  |  | 1 | Unclear: We do not understand your proposal, please detail your proposal. Especially confirm that you are compliant with our requested criteria. | [5 empty] | 1 |  | Open
Zte | JBS | Workflow, Project Management Plan and Timelines | Project schedule / Project management | Quality Assurance | 1.8.3 | Inspection of equipment delivery | 1 |  |  |  | 1 | Unclear: We do not understand your proposal, please detail your proposal. Especially confirm that you are compliant with our requested criteria. | fail |  |  | C |  | 1 |  | Open
Zte | JBS | Workflow, Project Management Plan and Timelines | Project schedule / Project management | Quality Assurance | 1.8.3 | Milestones for the completion of civil, mechanical, and electrical works | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | fail |  | dobble to 105 and 111 | C |  | 1 |  | Open
Zte | JBS | Workflow, Project Management Plan and Timelines | Project schedule / Project management | Quality Assurance | 1.8.3 | Quality control of delivered modules | 1 |  |  |  | 1 | Unclear: We do not understand your proposal, please detail your proposal. Especially confirm that you are compliant with our requested criteria. | fail |  |  | C |  | 1 |  | Open
Zte | JBS | Workflow, Project Management Plan and Timelines | Project schedule / Project management | Quality Assurance | 1.8.3 | Risk analysis and mitigation plan | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | fail |  |  | C |  | 1 |  | Open
Zte | JBS | Workflow, Project Management Plan and Timelines | Project schedule / Project management | Quality Assurance | 1.8.3 | System acceptance QA procedure by the Employer | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | fail |  |  | C |  | 1 |  | Open
Zte | JBS | Miscellaneous | Project schedule / Project management | Specific Requirements | 1.29.9 | The Bidder shall submit an organizational chart illustrating management and functional relationships among all project team members including consultants, sub-contractors and vendors at each significant stage of the work, such as permitting, design, construction, testing and commissioning and O&M. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Zte | RM | Supervisory Control and Data Acquisition (SCADA) | SCADA | Specific Requirements | 1.9.2 | Alarms/alerts and timely notification of key performance indicators | 1 |  | 1 | [8 empty] | 1 |  | Pass
Zte | RM | Supervisory Control and Data Acquisition (SCADA) | SCADA | Specific Requirements | 1.9.2 | All communication/data cables outside of buildings must be fiber-optic cables | 1 |  | 1 | [8 empty] | 1 |  | Pass
Zte | RM | Supervisory Control and Data Acquisition (SCADA) | SCADA | Specific Requirements | 1.9.2 | Back-up power for a minimum of twelve hours | 1 |  |  |  | 1 | please confirm 12 h back-up | [5 empty] | 1 |  | Open
Zte | RM | Supervisory Control and Data Acquisition (SCADA) | SCADA | Specific Requirements | 1.9.2 | Control room to remotely monitor and manage the whole system, on a 24 x 7 basis, with the capability of Web-based information sharing | 1 | 1.TP, 5.3.2 1.TP, 7.1 | 1 | [8 empty] | 1 |  | Pass
Zte | RM | Supervisory Control and Data Acquisition (SCADA) | SCADA | Specific Requirements | 1.9.2 | Data must be readily available for the fulfilment of all warranties and performance guarantees | 1 |  |  |  | 1 | please describe and confirm |  | Cannot be evaluated at this stage. | statement |  |  | 1 |  | Open
Zte | RM | Supervisory Control and Data Acquisition (SCADA) | SCADA | Specific Requirements | 1.9.2 | Data logging at intervals of not less than one minute, processing, transmission, and back-up | 1 |  |  |  | 1 | please confirm | hint: correct meaning is: no longer interval than 1 minute |  | not more (!) |  |  | 1 |  | Open
Zte | RM | Supervisory Control and Data Acquisition (SCADA) | SCADA | Specific Requirements | 1.9.2 | Data shall be provided via FTP (Push/Pull) to the Employer | 1 |  |  |  | 1 | please confirm | [5 empty] | 1 |  | Open
Zte | RM | Supervisory Control and Data Acquisition (SCADA) | SCADA | Specific Requirements | 1.9.1 | Remote access to all operational data for independent monitoring purposes shall be possible (NTDC requirements) | 1 | 1.TP, p87, p94 P005 | 1 |  |  |  | "5.2.4.4 Relaying Protection Information Management Sub-station " "NTDC relaying protection dispatching information net,…" |  |  |  |  | 1 |  | Pass
Zte | RM | Supervisory Control and Data Acquisition (SCADA) | SCADA | Specific Requirements | 1.9.1 | Safe and redundant archive for operational data. | 1 | 1.TP, p17 1.TP, p87 annex P005 “ Comprehensive Monitoring” | 1 |  |  | please explain "data processing" on site. Explain redundant archive | Monitoring struckture overview |  |  |  |  | 1 |  | Pass
Zte | RM | Supervisory Control and Data Acquisition (SCADA) | SCADA | Specific Requirements | 1.9.2 | Separate inverter, zone, and string level (current and voltage) monitoring | 1 |  | 1 | [8 empty] | 1 |  | Pass
Zte | RM | Supervisory Control and Data Acquisition (SCADA) | SCADA | Specific Requirements | 1.9.1 | The system has to provide different access-levels with different access rights allocated. | 1 |  |  |  | 1 | please confirm different levels of "read only", "write", User authority | [5 empty] | 1 |  | Open
Zte | RM | Earthworks | Site Preparation and site access | Design factors to be provided | 1.12 | All earth works required have to be specified and included in the offer | 1 |  |  |  | 1 | burried cable installaton (P015) please describe protection against rodents; please provide description for foundation for MV container | [5 empty] | 1 |  | Open
Zte | RM | Earthworks | Site Preparation and site access | Specific Requirements | 1.12, 1.13.4, 1.7.7 | Cross-sections of foundations for stations shall be provided, including explanation of the foundations laying down, height, penetration, and method of installing foundation posts, mounting fixtures | 1 | P002 | 1 | [8 empty] | 1 |  | Pass
Zte | RM | Earthworks | Site Preparation and site access | Specific Requirements | 1.12 | Position and specification of underground cable connections must be documented during installation | 1 |  |  |  | 1 | please confirm delivery with documentation |  | Cannot be avaluated at this stage. |  |  |  | 1 |  | Open
Zte | RM | Site Preparation and site access | Site Preparation and site access | Specific Requirements | 1.11.1 | The Bidder shall provide foundations and structures in accordance with the actual soil conditions. | 1 | 1.TP, p126 P002 | 1 |  |  |  | strip footing in Portland Cement P002: screw pile |  | refer to Soil study |  |  | 1 |  | Pass
Zte | RM | Earthworks | Site Preparation and site access | Specific Requirements | 1.12 | After completion of construction and all earthworks ground shall be levelled and stabilized. | 1 |  |  |  | 1 | please confirm leveling because soil stabilizes in the left form after short time | afforesting is described |  | (maintanance, dust) |  |  | 1 |  | Open
Zte | RM | Earthworks | Site Preparation and site access | Specific Requirements | 1.12 | Within the plant boundary limits, access roads to all stations shall be suitable for heavy load trucks (axle load: min. 12 tonn). | 1 | 1.TP, p120 P014 | 1 |  |  | please confirm sutibility for heavy load | access road: 6m wide internal road: 4m wide |  |  |  |  | 1 |  | Pass
Zte | JBS | Power plant documentation | Spare parts | Warranty | 1.27.2 | The successful bidder shall provide all warranty spares for a warranty period of 5 years. | 1 | 1. SoC to Bidding Document 30-01-14.pdf | 1 | [8 empty] | 1 |  | Pass
Zte | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Design factors to be provided | 1.21.2 | 3-phase, double wound, continuously rated, oil-cooled, enclosed transformers, use of low loss core steel and close coupled copper windings | 1 | Technical Proposal of 100MW Solar Power Plant, page 64 |  | 1 |  | Unclear: We do not understand your proposal, please detail your proposal. Especially confirm that you are compliant with our requested criteria. | dry type transformer will be used |  |  | U |  | 1 | 1 | Fail
Zte | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Design factors to be provided | 1.21.2 | Cooling method | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | no datasheet |  |  | C |  | 1 |  | Open
Zte | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Design factors to be provided | 1.21.2 | Efficiency | 1 | Technical Proposal of 100MW Solar Power Plant, page 115 |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | no datasheet, combined AC and transformer loss is 1% according to Pvsyst simulation |  |  | C |  | 1 |  | Open
Zte | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Design factors to be provided | 1.21.2 | Humidity tolerance | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | no datasheet |  |  | C |  | 1 |  | Open
Zte | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Design factors to be provided | 1.21.2 | Incoming terminals | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  |  |  | C |  | 1 |  | Open
Zte | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Design factors to be provided | 1.21.2 | Insulation type | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | no datasheet |  |  | C |  | 1 |  | Open
Zte | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Design factors to be provided | 1.21.2 | kVA rating | 1 |  | 1 | [8 empty] | 1 |  | Pass
Zte | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Design factors to be provided | 1.21.2 | Maximum ambient temperature and altitude | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | no datasheet |  |  | C |  | 1 |  | Open
Zte | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Design factors to be provided | 1.21.2 | No-load losses | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | no datasheet |  |  | C |  | 1 |  | Open
Zte | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Design factors to be provided | 1.21.2 | Operating temperature range | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | no datasheet |  |  | C |  | 1 |  | Open
Zte | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Design factors to be provided | 1.21.2 | Operational data shall be logged in central operating system (e.g. oil temperature, oil level, pressure, Temperature probes (one per phase): Alarm and trip of cell etc.) | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | no datasheet |  |  | C |  | 1 |  | Open
Zte | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Design factors to be provided | 1.21.2 | Outgoing terminals | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  |  |  | C |  | 1 |  | Open
Zte | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Design factors to be provided | 1.21.2 | Primary side voltage | 1 |  | 1 | [8 empty] | 1 |  | Pass
Zte | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Design factors to be provided | 1.21.2 | Protection system | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | no datasheet |  |  | C |  | 1 |  | Open
Zte | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Design factors to be provided | 1.21.2 | Secondary side voltage | 1 |  | 1 | [8 empty] | 1 |  | Pass
Zte | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Design factors to be provided | 1.21.2 | Short-circuit impedance | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | no datasheet |  |  | C |  | 1 |  | Open
Zte | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Standards | 1.21.3 | IEC 60076 | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | no datasheet | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  | C |  | 1 |  | Open
Zte | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Standards | 1.21.3 | IEC 60085 | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | no datasheet | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  | C |  | 1 |  | Open
Zte | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Standards | 1.21.3 | IEC 60137 | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | no datasheet | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  | C |  | 1 |  | Open
Zte | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Standards | 1.21.3 | IEC 60214 | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | no datasheet | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  | C |  | 1 |  | Open
Zte | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Standards | 1.21.3 | IEC 62446 | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | no datasheet | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  | C |  | 1 |  | Open
Zte | JBU | Step-up Transformers/MV Switchgear | Step-up Transformers/MV Switchgear | Guarantees | 1.21.1 | Compatibility with NTDC grid connection code must be ensured | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  |  |  | C |  | 1 |  | Open
Zte | GD | PR and System Performance Guarantee | System PR | Guarantees | 1.4.1 | A 25 years commitment, in the form of a whole System performance guarantee, is required. The performance guarantee is based on measuring the PR with the actual kWh-AC delivery per year adjusted for the actual POA irradiation for the same period | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  | Only to be checked in list of deviations. |  |  |  | 1 | 1 | Open
Zte | JBS | System PR Specification | System PR | Losses included in PR calculation | 1.5.4 | Auxiliary loads | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | fail | We don’t understand the question. Kindly clarify. | see relevant chapter 1.5.4 List of "losses" = auxilary loads from PV Energy that make the PR | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Zte | JBS | System PR Specification | System PR | Losses included in PR calculation | 1.5.4 | Inverter (operating efficiency, operating voltage variations, power/voltage levels) | 1 | 1. SoC to Bidding Document 30-01-14.pdf Page 114 | 1 |  |  |  |  | We don’t understand the question. Kindly clarify. | see relevant chapter 1.5.4 List of technical losses that make the PR |  |  | 1 |  | Pass
Zte | JBS | System PR Specification | System PR | Losses included in PR calculation | 1.5.4 | Module Array (temperature dependence, soiling, low light inefficiency, shading, mismatches in array) | 1 | 1. SoC to Bidding Document 30-01-14.pdf Page 114 |  | 1 |  | Unclear: We do not understand your proposal, please detail your proposal. Especially confirm that you are compliant with our requested criteria. | keine Verschattung gerechnet, Soiling zu gering, Qualitätsaufschlag eindeutig zu hoch. | We don’t understand the question. Kindly clarify. | we want to see these losses specified. Thos need to be aligned with O+M Startegy and System composition |  |  | 1 | 1 | Fail
Zte | JBS | System PR Specification | System PR | Losses included in PR calculation | 1.5.4 | Ohmic losses in cables | 1 | 1. SoC to Bidding Document 30-01-14.pdf Page 114 |  | 1 |  | Unclear: We do not understand your proposal, please detail your proposal. Especially confirm that you are compliant with our requested criteria. | fail | We don’t understand the question. Kindly clarify. | see relevant chapter 1.5.4 List of technical losses that make the PR |  |  | 1 | 1 | Fail
Zte | JBS | System PR Specification | System PR | Losses included in PR calculation | 1.5.4 | Transformer losses | 1 | 1. SoC to Bidding Document 30-01-14.pdf Page 114 | 1 |  |  |  | Trocken-Transfomer Datenblatt nicht vorhanden. | We don’t understand the question. Kindly clarify. | see relevant chapter 1.5.4 List of technical losses that make the PR |  |  | 1 |  | Pass
Zte | JBS | System PR Specification | System PR | O&M | 1.5.2 | The target PR specification at the time of commissioning the System is equal to or greater than 0.75 (75%). | 1 | 1. SoC to Bidding Document 30-01-14.pdf Page 107 |  |  | 1 | [6 empty] | 1 |  | Open
Zte | JBS | Physical layout | System PR | Specific Requirements | 1.7.1 | Provide a report using Solar GIS data provided by the Employer | 1 | 1. SoC to Bidding Document 30-01-14.pdf Page 101 | 1 |  |  |  |  | Replace 'Report' with ' PV-Syst report'. | 'Report' is original wording in ER in 1.7.1 |  |  | 1 |  | Pass
Zte | JBS | Physical layout | System PR | Specific Requirements | 1.7.1, 1.1.8 | Layout calculations of predicted kWh over the system lifetime and PR using the tool PVSyst V5.62 or higher | 1 | 1. SoC to Bidding Document 30-01-14.pdf Page 106 | 1 | [8 empty] | 1 |  | Pass
Zte | GD | PR and System Performance Guarantee | System PR | System PR | 1.4.2 | Guaranteed PR values in the form of the Table in 1.4.1 for the acceptance phase and annual output of the PV system shall be specified. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Link to table in Documents sheet |  |  |  | 1 | 1 | Open
Zte | GD | PR and System Performance Guarantee | System PR | System PR | 1.4.1 | The billing system/metering system will be installed at interconnection point of 132 kV bus bar of HV substation to be installed by the EPC Contractor and the 132 kV Transmission line of NTDC existing at site. | 2 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  | Only to be checked in list of deviations. |  |  |  | 1 |  | Open
Zte | GD | PR and System Performance Guarantee | System PR | System PR | 1.4.4 | The initial PR will be first measured after the time of commissioning of the completed PV System during the acceptance phase of 30 days. | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  | Cannot be evaluated at this stage. Only to be checked in list of deviations. |  |  |  | 1 | 1 | Open
Zte | JBS | Equipment guarantees | Warranty | Guarantees | 1.28.4, 1.6 | A detailed list of all guarantee conditions for the main equipments (beside modules and inverters) shall be provided by the Successful Bidder with the technical offer. The product warranty shall be at least 5 years. | 1 | 1. SoC to Bidding Document 30-01-14.pdf | 1 | [8 empty] | 1 |  | Pass
Zte | JBS | Equipment guarantees | Warranty | Guarantees | 1.28 | The overall Guarantee and Power Plant Acceptance Procedures required for the Project are described in Sections 1.3, 1.4, 1.14, 1.18 and Schedule D and shall be met. | 1 | 1. SoC to Bidding Document 30-01-14.pdf | 1 |  |  |  |  | Link |  |  |  | 1 |  | Pass
Zte | JBS | Basic Scope of Supply | Warranty | Quality Assurance | 1.6 | The Product Warranties shall be given for a duration of at least 5 years | 1 | 1. SoC to Bidding Document 30-01-14.pdf Page 101 | 1 |  |  |  |  | Cannot be evaluated at this stage. Only to be checked in list of deviations. |  |  |  | 1 |  | Pass
Zte | MAW | Inverters | Warranty | Warranty option | 1.18.1 | The Bidder shall arrange a full-service package for the selected inverters for a product warranty period of 5 years, with an option to cover additional 20 years including provisions for any necessary replacements including O&M service plan guaranteeing 99% availability. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Juwi | AR | HV Substation | HV Substation | Specific Requirements | 1.23.1 | The HV Substation includes the respective MV switch gears, Transformer MV/ HV. The HV connection is designed to connect to the HV line. | 3 |  | 1 | [8 empty] | 1 |  | Pass
Juwi | AR | HV Substation | HV Substation | Specific Requirements | 1.23.2 | Availability and delivery time of the chosen components is detailed | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | [5 empty] | 1 |  | Open
Juwi | AR | HV Substation | HV Substation -HV part | Specific Requirements | 1.23.3 | The substation is separated into 2 parts: Medium Voltage part including HV transformer and HV portion of the plant excluding the HV transformer | 1 |  |  |  | 1 | [5 empty] | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | 1 |  | Open
Juwi | AR | HV Substation | HV Substation -HV part | Specific Requirements | 1.23.3 | Double Busbar single breaker scheme shall be designed for HV portion of HV substation | 1 |  | 1 | [8 empty] | 1 |  | Pass
Juwi | AR | HV Substation | HV Substation -HV part | HV portion components | 1.23.3 | 132 kV Transformer Bays as per design | 1 |  | 1 | [8 empty] | 1 |  | Pass
Juwi | AR | HV Substation | HV Substation -HV part | HV portion components | 1.23.3 | 2x132 kV Line Bays | 1 |  | 1 | [8 empty] | 1 |  | Pass
Juwi | AR | HV Substation | HV Substation -HV part | HV portion components | 1.23.3 | 2x132 kV PT bays | 1 |  |  |  | 1 | [5 empty] | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | 1 |  | Open
Juwi | AR | HV Substation | HV Substation -HV part | HV portion components | 1.23.3 | 132 kV Bus Coupler Bay | 1 |  | 1 | [8 empty] | 1 |  | Pass
Juwi | AR | HV Substation | HV Substation -HV part | HV portion components | 1.23.3 | Telecom and PLC Equipment | 1 |  |  |  | 1 |  |  | Which speification are acepted |  |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | 1 |  | Open
Juwi | AR | HV Substation | HV Substation -HV part | Standards | 1.23.3 | All the schemes including SCADA, PLC, protection scheme, control and monitoring scheme and other design factors, shall be in compliance with the NTDC grid code. | 1 |  |  |  | 1 |  |  | Link to NTDC grid code |  |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | 1 |  | Open
Juwi | AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | 3-phase, double wound, continuously rated, oil-cooled, enclosed transformers, use of low loss core steel and close coupled copper windings | 1 |  | 1 |  |  |  | No Specification or Tech data |  |  |  |  | 1 |  | Pass
Juwi | AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | Enclosure specifications (e.g., steel floor, fluid tight, sealed tank) | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | [5 empty] | 1 |  | Open
Juwi | AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | Incoming terminals | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | [5 empty] | 1 |  | Open
Juwi | AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | Outgoing terminals | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | [5 empty] | 1 |  | Open
Juwi | AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | kVA rating | 1 |  | 1 | [8 empty] | 1 |  | Pass
Juwi | AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | Primary side voltage | 1 |  | 1 | [8 empty] | 1 |  | Pass
Juwi | AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | Secondary side voltage | 1 |  | 1 | [8 empty] | 1 |  | Pass
Juwi | AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | Vector group | 3 |  | 1 |  |  |  |  | to be discussed |  |  |  | 1 |  | Pass
Juwi | AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | Insulation type | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | [5 empty] | 1 |  | Open
Juwi | AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | Frequency rating | 1 |  | 1 | [8 empty] | 1 |  | Pass
Juwi | AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | Short-circuit impedance | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | [5 empty] | 1 |  | Open
Juwi | AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | Own consumption | 3 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | [5 empty] | 1 |  | Open
Juwi | AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | No-load losses | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | [5 empty] | 1 |  | Open
Juwi | AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | Efficiency | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | [5 empty] | 1 |  | Open
Juwi | AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | Operating temperature range | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | [5 empty] | 1 |  | Open
Juwi | AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | Maximum ambient temperature and altitude | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  | to be discussed |  |  |  | 1 |  | Open
Juwi | AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | Humidity tolerance | 2 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | [5 empty] | 1 |  | Open
Juwi | AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | Cooling method | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | [5 empty] | 1 |  | Open
Juwi | AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | Dimensions and weight | 3 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | [5 empty] | 1 |  | Open
Juwi | AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | Oil weight | 3 | [10 empty] | 0 |  | Open
Juwi | AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | Protection system | 1 |  | 1 | [8 empty] | 1 |  | Pass
Juwi | AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | Auxiliary service lines | 1 |  | 1 | [8 empty] | 1 |  | Pass
Juwi | AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | Fittings with the transformer | 3 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | [5 empty] | 1 |  | Open
Juwi | AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | Noise levels | 3 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | [5 empty] | 1 |  | Open
Juwi | AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | Warranty and insurance | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | [5 empty] | 1 |  | Open
Juwi | AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | Tests and inspection routines | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | [5 empty] | 1 |  | Open
Juwi | AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | Operational data shall be logged in central operating system (e.g. oil temperature, oil level, pressure, temperature probes (one per phase): Alarm and trip of cell etc.) | 2 |  |  |  | 1 | [5 empty] | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | 1 |  | Open
Juwi | AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | All documentation, certificates and test protocols shall be provided | 2 |  |  |  | 1 | [5 empty] | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | 1 |  | Open
Juwi | AR | HV Substation | HV Substation -MV/HV Transformer | Standards | 1.23.7 | IEC 62446 | 1 |  |  |  | 1 |  |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | 1 |  | Open
Juwi | AR | HV Substation | HV Substation -MV/HV Transformer | Standards | 1.23.7 | IEC 60076 | 1 |  |  |  | 1 |  |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | 1 |  | Open
Juwi | AR | HV Substation | HV Substation -MV/HV Transformer | Standards | 1.23.7 | IEC 60085 | 1 |  |  |  | 1 |  |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | 1 |  | Open
Juwi | AR | HV Substation | HV Substation -MV/HV Transformer | Standards | 1.23.7 | IEC 60214 | 1 |  |  |  | 1 |  |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | 1 |  | Open
Juwi | AR | HV Substation | HV Substation -MV/HV Transformer | Standards | 1.23.7 | IEC 60137 | 1 |  |  |  | 1 |  |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | 1 |  | Open
Juwi | AR | HV Substation | HV Substation -MV/HV Transformer | Standards | 1.23.7 | ASTM d-3487 | 1 |  |  |  | 1 |  |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | 1 |  | Open
Juwi | AR | HV Substation | HV Substation -MV/HV Transformer | Quality Assurance | 1.23.7 | Factory witness testing shall be required for MV/HV transformer and switchgear to be installed at this project. | 1 |  |  |  | 1 |  |  | Cannot be evaluated at this stage |  |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | 1 |  | Open
Juwi | AR | HV Substation | HV Substation -MV/HV Transformer | Quality Assurance | 1.23.7 | Type test reports from an independent reputable laboratory shall be submitted with the bid. | 1 |  |  |  | 1 | [5 empty] | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | 1 |  | Open
Juwi | AR | HV Substation | Due Diligence | Quality Assurance | 1.23.7 | The cost of the due diligence for the HV station to be carried by the Employer through an independent technical consultant will be taken over by the successful bidder up to an amount of 30,000 USD. | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | [5 empty] | 1 |  | Open
Juwi | AR | HV Substation | HV Substation -MV/HV Transformer | Design | 1.23.8 | The separating equipment shall be installed with visible disconnection (pivotable disconnectors). | 1 |  |  |  | 1 |  |  | Cannot be evaluated at this stage |  |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | 1 |  | Open
Juwi | AR | HV Substation | HV Substation -MV/HV Transformer | Design | 1.23.9 | Insulation with PCB (polychlorinated biphenyl) has not been used. | 1 |  |  |  | 1 | [5 empty] | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | 1 |  | Open
Juwi | AR | HV Substation | HV Substation -MV/HV Transformer | Design | 1.23.10 | The preliminary design of the substation is submitted with the technical bid according to the requirements of Appendix 1 | 1 |  |  |  | 1 |  |  | Link to Appendix 1 |  |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | 1 |  | Open
Juwi | AR | HV Substation | HV Substation -MV/HV Transformer | Energy Metering System | 1.23.11 | The Energy Metering System will be placed on the HV side of the substation | 1 |  |  |  | 1 | [5 empty] | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | 1 |  | Open
Juwi | AR | HV Substation | HV Substation -MV/HV Transformer | Energy Metering System -NTDC specifications | 1.23.11 | Metering Equipment for Electric Energy Transfer between the Companies (Specification No. P-199-08) | 1 |  |  |  | 1 | [5 empty] | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | 1 |  | Open
Juwi | AR | HV Substation | HV Substation -MV/HV Transformer | Energy Metering System -NTDC specifications | 1.23.11 | Energy Meters for Grid Metering (Specification No. P-202-2012) | 1 |  |  |  | 1 | [5 empty] | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | 1 |  | Open
Juwi | AR | HV Substation | HV Substation -MV/HV Transformer | Energy Metering System -NTDC specifications | 1.23.11 | Voltage Transformers for Special Application (Energy Metering; Specifications No. P-206-05) | 1 |  |  |  | 1 | [5 empty] | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | 1 |  | Open
Juwi | AR | HV Substation | HV Substation -MV/HV Transformer | Energy Metering System -NTDC specifications | 1.23.11 | Current Transformers for Special Application (spec.No P-205-2005) | 1 | 1 | [9 empty] | 0 |  | Open
Juwi | AR | HV Switchgear | HV Switchgear | Project Schedule | 1.24.1 | The switchgear design and order time, for the 132 kV transmission line is detailed and corresponds with the envisaged project schedule. | 1 |  |  |  | 1 | [5 empty] | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | 1 |  | Open
Juwi | AR | HV Switchgear | HV Switchgear | Functionalities | 1.24.1 | Nominal system voltage, kV 132 | 1 |  | 1 | [8 empty] | 1 |  | Pass
Juwi | AR | HV Switchgear | HV Switchgear | Functionalities | 1.24.1 | Rated voltage of switch gear, kV 145 | 1 |  | 1 | [8 empty] | 1 |  | Pass
Juwi | AR | HV Switchgear | HV Switchgear | Functionalities | 1.24.1 | Maximum system voltage, kV 145 | 1 |  | 1 | [8 empty] | 1 |  | Pass
Juwi | AR | HV Switchgear | HV Switchgear | Functionalities | 1.24.1 | Rated frequency, Hz 50 | 1 |  | 1 | [8 empty] | 1 |  | Pass
Juwi | AR | HV Switchgear | HV Switchgear | Design factors to be provided | 1.24.2 | Rated voltage | 1 |  | 1 | [8 empty] | 1 |  | Pass
Juwi | AR | HV Switchgear | HV Switchgear | Design factors to be provided | 1.24.2 | Short-duration power withstand frequency voltage | 3 |  |  |  | 1 | [5 empty] | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | 1 |  | Open
Juwi | AR | HV Switchgear | HV Switchgear | Design factors to be provided | 1.24.2 | Rated lightning impulse withstand voltage | 3 |  |  |  | 1 | [5 empty] | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | 1 |  | Open
Juwi | AR | HV Switchgear | HV Switchgear | Design factors to be provided | 1.24.2 | Rated frequency | 3 |  | 1 | [8 empty] | 1 |  | Pass
Juwi | AR | HV Switchgear | HV Switchgear | Design factors to be provided | 1.24.2 | Peak-withstand current | 2 |  |  |  | 1 | [5 empty] | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | 1 |  | Open
Juwi | AR | HV Switchgear | HV Switchgear | Design factors to be provided | 1.24.2 | Short-circuit making current | 2 |  |  |  | 1 | [5 empty] | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | 1 |  | Open
Juwi | AR | HV Switchgear | HV Switchgear | Design factors to be provided | 1.24.2 | Short-time withstand current | 2 |  |  |  | 1 | [5 empty] | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | 1 |  | Open
Juwi | AR | HV Switchgear | HV Switchgear | Design factors to be provided | 1.24.2 | Short-circuit breaking current | 2 |  |  |  | 1 | [5 empty] | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | 1 |  | Open
Juwi | AR | HV Switchgear | HV Switchgear | Design factors to be provided | 1.24.2 | Insulating medium | 2 |  |  |  | 1 | [5 empty] | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | 1 |  | Open
Juwi | AR | HV Switchgear | HV Switchgear | Design factors to be provided | 1.24.2 | Second fault rating | 2 |  | 1 | [8 empty] | 1 |  | Pass
Juwi | AR | HV Switchgear | HV Switchgear | Design factors to be provided | 1.24.2 | Busbars | 3 |  | 1 | [8 empty] | 1 |  | Pass
Juwi | AR | HV Switchgear | HV Switchgear | Design factors to be provided | 1.24.2 | Rated normal current for busbars | 3 |  | 1 | [8 empty] | 1 |  | Pass
Juwi | AR | HV Switchgear | HV Switchgear | Design factors to be provided | 1.24.2 | Rated normal current for feeders | 3 |  | 1 | [8 empty] | 1 |  | Pass
Juwi | AR | HV Switchgear | HV Switchgear | Design factors to be provided | 1.24.2 | Degree of protection | 2 |  |  |  | 1 | [5 empty] | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | 1 |  | Open
Juwi | AR | HV Switchgear | HV Switchgear | Design factors to be provided | 1.24.2 | Second internal arc rating | 3 |  |  |  | 1 | [5 empty] | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | 1 |  | Open
Juwi | AR | HV Switchgear | HV Switchgear | Design factors to be provided | 1.24.2 | Circuit breakers: protection and metering | 1 |  |  |  | 1 | [5 empty] | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | 1 |  | Open
Juwi | AR | HV Switchgear | HV Switchgear | Design factors to be provided | 1.24.2 | Protection relay | 1 |  |  |  | 1 | [5 empty] | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | 1 |  | Open
Juwi | AR | HV Switchgear | HV Switchgear | Design factors to be provided | 1.24.2 | Switch disconnector panel | 2 |  |  |  | 1 | [5 empty] | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | 1 |  | Open
Juwi | AR | HV Switchgear | HV Switchgear | Design factors to be provided | 1.24.2 | Operating temperature range | 1 |  |  |  | 1 | [5 empty] | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | 1 |  | Open
Juwi | AR | HV Switchgear | HV Switchgear | Design factors to be provided | 1.24.2 | Warranty and insurance | 1 |  |  |  | 1 | [5 empty] | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | 1 |  | Open
Juwi | AR | HV Switchgear | HV Switchgear | Design factors to be provided | 1.24.2 | Dimensions and weight | 3 |  |  |  | 1 | [5 empty] | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | 1 |  | Open
Juwi | AR | HV Switchgear | HV Switchgear | Design factors to be provided | 1.24.2 | NEMA enclosure type and IP code | 1 |  |  |  | 1 | [5 empty] | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | 1 |  | Open
Juwi | AR | HV Switchgear | HV Switchgear | Standards | 1.24.2 | IEC 60038 | 1 |  |  |  | 1 |  |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | 1 |  | Open
Juwi | AR | HV Switchgear | HV Switchgear | Standards | 1.24.2 | IEC 60095 | 1 |  |  |  | 1 |  |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | 1 |  | Open
Juwi | AR | HV Switchgear | HV Switchgear | Standards | 1.24.2 | IEC 62271-200 | 1 |  |  |  | 1 |  |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | 1 |  | Open
Juwi | AR | HV Switchgear | HV Switchgear | Standards | 1.24.2 | IEC 60364 | 1 |  |  |  | 1 |  |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | 1 |  | Open
Juwi | AR | HV Switchgear | HV Switchgear | Standards | 1.24.2 | Factory witness testing will are required for HV switchgear | 1 |  |  |  | 1 |  |  | Cannot be evaluated at this stage |  |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | 1 |  | Open
Juwi | AR | HV Switchgear | HV Switchgear | Standards | 1.24.3 | Type test reports from an independent reputable laboratory shall be submitted | 1 |  |  |  | 1 | [5 empty] | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | 1 |  | Open
Juwi | AR | HV Switchgear | Due Diligence | Quality Assurance | 1.24.3 | The cost of the due diligence to be carried by the Employer through an independent technical consultant will be taken over by the successful bidder up to an amount of 50,000 USD. | 1 |  |  |  | 1 | [5 empty] | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | 1 |  | Open
Sumec | AR | HV Substation | HV Substation | Specific Requirements | 1.23.1 | The HV Substation includes the respective MV switch gears, Transformer MV/ HV. The HV connection is designed to connect to the HV line. | 3 |  | 1 |  |  |  | detail layout |  |  |  |  | 1 |  | Pass
Sumec | AR | HV Substation | HV Substation | Specific Requirements | 1.23.2 | Availability and delivery time of the chosen components is detailed | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | not submitted |  |  |  |  | 1 |  | Open
Sumec | AR | HV Substation | HV Substation -HV part | Specific Requirements | 1.23.3 | The substation is separated into 2 parts: Medium Voltage part including HV transformer and HV portion of the plant excluding the HV transformer | 1 |  | 1 | [8 empty] | 1 |  | Pass
Sumec | AR | HV Substation | HV Substation -HV part | Specific Requirements | 1.23.3 | Double Busbar single breaker scheme shall be designed for HV portion of HV substation | 1 |  | 1 | [8 empty] | 1 |  | Pass
Sumec | AR | HV Substation | HV Substation -HV part | HV portion components | 1.23.3 | 132 kV Transformer Bays as per design | 1 |  | 1 |  |  |  | one Transformer only 100 MVA |  |  |  |  | 1 |  | Pass
Sumec | AR | HV Substation | HV Substation -HV part | HV portion components | 1.23.3 | 2x132 kV Line Bays | 1 |  | 1 |  |  |  | detail SLD |  |  |  |  | 1 |  | Pass
Sumec | AR | HV Substation | HV Substation -HV part | HV portion components | 1.23.3 | 2x132 kV PT bays | 1 |  | 1 |  |  |  | detail SLD |  |  |  |  | 1 |  | Pass
Sumec | AR | HV Substation | HV Substation -HV part | HV portion components | 1.23.3 | 132 kV Bus Coupler Bay | 1 |  | 1 |  |  |  | detail SLD |  |  |  |  | 1 |  | Pass
Sumec | AR | HV Substation | HV Substation -HV part | HV portion components | 1.23.3 | Telecom and PLC Equipment | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | detail required | Which speification are acepted |  |  |  | 1 |  | Open
Sumec | AR | HV Substation | HV Substation -HV part | Standards | 1.23.3 | All the schemes including SCADA, PLC, protection scheme, control and monitoring scheme and other design factors, shall be in compliance with the NTDC grid code. | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | detail is requied | Link to NTDC grid code |  |  |  | 1 |  | Open
Sumec | AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | 3-phase, double wound, continuously rated, oil-cooled, enclosed transformers, use of low loss core steel and close coupled copper windings | 1 |  | 1 |  |  |  | one Transformer only 100 MVA |  |  |  |  | 1 |  | Pass
Sumec | AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | Enclosure specifications (e.g., steel floor, fluid tight, sealed tank) | 1 |  | 1 | [8 empty] | 1 |  | Pass
Sumec | AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | Incoming terminals | 1 |  | 1 | [8 empty] | 1 |  | Pass
Sumec | AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | Outgoing terminals | 1 |  | 1 | [8 empty] | 1 |  | Pass
Sumec | AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | kVA rating | 1 |  | 1 | [8 empty] | 1 |  | Pass
Sumec | AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | Primary side voltage | 1 |  | 1 | [8 empty] | 1 |  | Pass
Sumec | AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | Secondary side voltage | 1 |  | 1 | [8 empty] | 1 |  | Pass
Sumec | AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | Vector group | 3 |  | 1 |  |  |  |  | to be discussed |  |  |  | 1 |  | Pass
Sumec | AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | Insulation type | 1 |  | 1 | [8 empty] | 1 |  | Pass
Sumec | AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | Frequency rating | 1 |  | 1 | [8 empty] | 1 |  | Pass
Sumec | AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | Short-circuit impedance | 1 |  | 1 |  |  |  | need verification |  |  |  |  | 1 |  | Pass
Sumec | AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | Own consumption | 3 |  | 1 |  |  |  | need verification |  |  |  |  | 1 |  | Pass
Sumec | AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | No-load losses | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | to submitt |  |  |  |  | 1 |  | Open
Sumec | AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | Efficiency | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | to submitt |  |  |  |  | 1 |  | Open
Sumec | AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | Operating temperature range | 1 | [5 empty] | to submitt |  |  |  |  | 0 |  | Open
Sumec | AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | Maximum ambient temperature and altitude | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | to submitt | to be discussed |  |  |  | 1 |  | Open
Sumec | AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | Humidity tolerance | 2 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | to submitt |  |  |  |  | 1 |  | Open
Sumec | AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | Cooling method | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | to submitt |  |  |  |  | 1 |  | Open
Sumec | AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | Dimensions and weight | 3 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | to submitt |  |  |  |  | 1 |  | Open
Sumec | AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | Oil weight | 3 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | to submitt |  |  |  |  | 1 |  | Open
Sumec | AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | Protection system | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | to submitt |  |  |  |  | 1 |  | Open
Sumec | AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | Auxiliary service lines | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | to submitt |  |  |  |  | 1 |  | Open
Sumec | AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | Fittings with the transformer | 3 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | to submitt |  |  |  |  | 1 |  | Open
Sumec | AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | Noise levels | 3 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | to submitt |  |  |  |  | 1 |  | Open
Sumec | AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | Warranty and insurance | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | to submitt |  |  |  |  | 1 |  | Open
Sumec | AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | Tests and inspection routines | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | to submitt |  |  |  |  | 1 |  | Open
Sumec | AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | Operational data shall be logged in central operating system (e.g. oil temperature, oil level, pressure, temperature probes (one per phase): Alarm and trip of cell etc.) | 2 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | to submitt |  |  |  |  | 1 |  | Open
Sumec | AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | All documentation, certificates and test protocols shall be provided | 2 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | to submitt |  |  |  |  | 1 |  | Open
Sumec | AR | HV Substation | HV Substation -MV/HV Transformer | Standards | 1.23.7 | IEC 62446 | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | to submitt | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  |  |  | 1 |  | Open
Sumec | AR | HV Substation | HV Substation -MV/HV Transformer | Standards | 1.23.7 | IEC 60076 | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | to submitt | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  |  |  | 1 |  | Open
Sumec | AR | HV Substation | HV Substation -MV/HV Transformer | Standards | 1.23.7 | IEC 60085 | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | to submitt | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  |  |  | 1 |  | Open
Sumec | AR | HV Substation | HV Substation -MV/HV Transformer | Standards | 1.23.7 | IEC 60214 | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | to submitt | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  |  |  | 1 |  | Open
Sumec | AR | HV Substation | HV Substation -MV/HV Transformer | Standards | 1.23.7 | IEC 60137 | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | to submitt | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  |  |  | 1 |  | Open
Sumec | AR | HV Substation | HV Substation -MV/HV Transformer | Standards | 1.23.7 | ASTM d-3487 | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | to submitt | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  |  |  | 1 |  | Open
Sumec | AR | HV Substation | HV Substation -MV/HV Transformer | Quality Assurance | 1.23.7 | Factory witness testing shall be required for MV/HV transformer and switchgear to be installed at this project. | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | to confirm | Cannot be evaluated at this stage |  |  |  | 1 |  | Open
Sumec | AR | HV Substation | HV Substation -MV/HV Transformer | Quality Assurance | 1.23.7 | Type test reports from an independent reputable laboratory shall be submitted with the bid. | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | to submitt |  |  |  |  | 1 |  | Open
Sumec | AR | HV Substation | Due Diligence | Quality Assurance | 1.23.7 | The cost of the due diligence for the HV station to be carried by the Employer through an independent technical consultant will be taken over by the successful bidder up to an amount of 30,000 USD. | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | to confirm |  |  |  |  | 1 |  | Open
Sumec | AR | HV Substation | HV Substation -MV/HV Transformer | Design | 1.23.8 | The separating equipment shall be installed with visible disconnection (pivotable disconnectors). | 1 |  | 1 |  |  |  |  | Cannot be evaluated at this stage |  |  |  | 1 |  | Pass
Sumec | AR | HV Substation | HV Substation -MV/HV Transformer | Design | 1.23.9 | Insulation with PCB (polychlorinated biphenyl) has not been used. | 1 |  | 1 |  |  |  | to confirm |  |  |  |  | 1 |  | Pass
Sumec | AR | HV Substation | HV Substation -MV/HV Transformer | Design | 1.23.10 | The preliminary design of the substation is submitted with the technical bid according to the requirements of Appendix 1 | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | SLD , layout not included | Link to Appendix 1 |  |  |  | 1 |  | Open
Sumec | AR | HV Substation | HV Substation -MV/HV Transformer | Energy Metering System | 1.23.11 | The Energy Metering System will be placed on the HV side of the substation | 1 |  | 1 |  |  |  | detail |  |  |  |  | 1 |  | Pass
Sumec | AR | HV Substation | HV Substation -MV/HV Transformer | Energy Metering System -NTDC specifications | 1.23.11 | Metering Equipment for Electric Energy Transfer between the Companies (Specification No. P-199-08) | 1 |  | 1 |  |  |  | detail |  |  |  |  | 1 |  | Pass
Sumec | AR | HV Substation | HV Substation -MV/HV Transformer | Energy Metering System -NTDC specifications | 1.23.11 | Energy Meters for Grid Metering (Specification No. P-202-2012) | 1 |  | 1 |  |  |  | detail |  |  |  |  | 1 |  | Pass
Sumec | AR | HV Substation | HV Substation -MV/HV Transformer | Energy Metering System -NTDC specifications | 1.23.11 | Voltage Transformers for Special Application (Energy Metering; Specifications No. P-206-05) | 1 |  | 1899-12-31 |  |  |  | detal |  |  |  |  | 1 |  | Pass
Sumec | AR | HV Substation | HV Substation -MV/HV Transformer | Energy Metering System -NTDC specifications | 1.23.11 | Current Transformers for Special Application (spec.No P-205-2005) | 1 |  | 1 |  |  |  | subject to calculations |  |  |  |  | 1 |  | Pass
Sumec | AR | HV Switchgear | HV Switchgear | Project Schedule | 1.24.1 | The switchgear design and order time, for the 132 kV transmission line is detailed and corresponds with the envisaged project schedule. | 1 | [5 empty] | need detail drawing |  |  |  |  | 0 |  | Open
Sumec | AR | HV Switchgear | HV Switchgear | Functionalities | 1.24.1 | Nominal system voltage, kV 132 | 1 |  | 1 | [8 empty] | 1 |  | Pass
Sumec | AR | HV Switchgear | HV Switchgear | Functionalities | 1.24.1 | Rated voltage of switch gear, kV 145 | 1 |  | 1 | [8 empty] | 1 |  | Pass
Sumec | AR | HV Switchgear | HV Switchgear | Functionalities | 1.24.1 | Maximum system voltage, kV 145 | 1 |  | 1 | [8 empty] | 1 |  | Pass
Sumec | AR | HV Switchgear | HV Switchgear | Functionalities | 1.24.1 | Rated frequency, Hz 50 | 1 |  | 1 | [8 empty] | 1 |  | Pass
Sumec | AR | HV Switchgear | HV Switchgear | Design factors to be provided | 1.24.2 | Rated voltage | 1 |  | 1 | [8 empty] | 1 |  | Pass
Sumec | AR | HV Switchgear | HV Switchgear | Design factors to be provided | 1.24.2 | Short-duration power withstand frequency voltage | 3 |  | 1 |  |  |  | detai report |  |  |  |  | 1 |  | Pass
Sumec | AR | HV Switchgear | HV Switchgear | Design factors to be provided | 1.24.2 | Rated lightning impulse withstand voltage | 3 |  | 1 |  |  |  | detai report |  |  |  |  | 1 |  | Pass
Sumec | AR | HV Switchgear | HV Switchgear | Design factors to be provided | 1.24.2 | Rated frequency | 3 |  | 1 | [8 empty] | 1 |  | Pass
Sumec | AR | HV Switchgear | HV Switchgear | Design factors to be provided | 1.24.2 | Peak-withstand current | 2 |  | 1 | [8 empty] | 1 |  | Pass
Sumec | AR | HV Switchgear | HV Switchgear | Design factors to be provided | 1.24.2 | Short-circuit making current | 2 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | detail report |  |  |  |  | 1 |  | Open
Sumec | AR | HV Switchgear | HV Switchgear | Design factors to be provided | 1.24.2 | Short-time withstand current | 2 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | detail report |  |  |  |  | 1 |  | Open
Sumec | AR | HV Switchgear | HV Switchgear | Design factors to be provided | 1.24.2 | Short-circuit breaking current | 2 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | detail report |  |  |  |  | 1 |  | Open
Sumec | AR | HV Switchgear | HV Switchgear | Design factors to be provided | 1.24.2 | Insulating medium | 2 |  | 1 | [8 empty] | 1 |  | Pass
Sumec | AR | HV Switchgear | HV Switchgear | Design factors to be provided | 1.24.2 | Second fault rating | 2 |  | 1 | [8 empty] | 1 |  | Pass
Sumec | AR | HV Switchgear | HV Switchgear | Design factors to be provided | 1.24.2 | Busbars | 3 |  | 1 | [8 empty] | 1 |  | Pass
Sumec | AR | HV Switchgear | HV Switchgear | Design factors to be provided | 1.24.2 | Rated normal current for busbars | 3 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | [5 empty] | 1 |  | Open
Sumec | AR | HV Switchgear | HV Switchgear | Design factors to be provided | 1.24.2 | Rated normal current for feeders | 3 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | [5 empty] | 1 |  | Open
Sumec | AR | HV Switchgear | HV Switchgear | Design factors to be provided | 1.24.2 | Degree of protection | 2 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | [5 empty] | 1 |  | Open
Sumec | AR | HV Switchgear | HV Switchgear | Design factors to be provided | 1.24.2 | Second internal arc rating | 3 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | [5 empty] | 1 |  | Open
Sumec | AR | HV Switchgear | HV Switchgear | Design factors to be provided | 1.24.2 | Circuit breakers: protection and metering | 1 |  |  |  | 1 | [5 empty] | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | 1 |  | Open
Sumec | AR | HV Switchgear | HV Switchgear | Design factors to be provided | 1.24.2 | Protection relay | 1 |  |  |  | 1 | [5 empty] | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | 1 |  | Open
Sumec | AR | HV Switchgear | HV Switchgear | Design factors to be provided | 1.24.2 | Switch disconnector panel | 2 |  | 1 | [8 empty] | 1 |  | Pass
Sumec | AR | HV Switchgear | HV Switchgear | Design factors to be provided | 1.24.2 | Operating temperature range | 1 |  |  |  | 1 | [5 empty] | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | 1 |  | Open
Sumec | AR | HV Switchgear | HV Switchgear | Design factors to be provided | 1.24.2 | Warranty and insurance | 1 |  |  |  | 1 | [5 empty] | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | 1 |  | Open
Sumec | AR | HV Switchgear | HV Switchgear | Design factors to be provided | 1.24.2 | Dimensions and weight | 3 |  |  |  | 1 | [5 empty] | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | 1 |  | Open
Sumec | AR | HV Switchgear | HV Switchgear | Design factors to be provided | 1.24.2 | NEMA enclosure type and IP code | 1 |  |  |  | 1 | [5 empty] | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | 1 |  | Open
Sumec | AR | HV Switchgear | HV Switchgear | Standards | 1.24.2 | IEC 60038 | 1 |  |  |  | 1 |  |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | 1 |  | Open
Sumec | AR | HV Switchgear | HV Switchgear | Standards | 1.24.2 | IEC 60095 | 1 |  |  |  | 1 |  |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | 1 |  | Open
Sumec | AR | HV Switchgear | HV Switchgear | Standards | 1.24.2 | IEC 62271-200 | 1 |  |  |  | 1 |  |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | 1 |  | Open
Sumec | AR | HV Switchgear | HV Switchgear | Standards | 1.24.2 | IEC 60364 | 1 |  |  |  | 1 |  |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | 1 |  | Open
Sumec | AR | HV Switchgear | HV Switchgear | Standards | 1.24.2 | Factory witness testing will are required for HV switchgear | 1 |  |  |  | 1 |  |  | Cannot be evaluated at this stage |  |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | 1 |  | Open
Sumec | AR | HV Switchgear | HV Switchgear | Standards | 1.24.3 | Type test reports from an independent reputable laboratory shall be submitted | 1 |  |  |  | 1 | [5 empty] | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | 1 |  | Open
Sumec | AR | HV Switchgear | Due Diligence | Quality Assurance | 1.24.3 | The cost of the due diligence to be carried by the Employer through an independent technical consultant will be taken over by the successful bidder up to an amount of 50,000 USD. | 1 |  |  |  | 1 | [5 empty] | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | 1 |  | Open
CHINT | AR | HV Substation | HV Substation | Specific Requirements | 1.23.1 | The HV Substation includes the respective MV switch gears, Transformer MV/ HV. The HV connection is designed to connect to the HV line. | 3 |  |  |  | 1 | [5 empty] | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | 1 |  | Open
Chint | AR | HV Substation | HV Substation | Specific Requirements | 1.23.2 | Availability and delivery time of the chosen components is detailed | 1 |  |  |  | 1 | [5 empty] | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | 1 |  | Open
Chint | AR | HV Substation | HV Substation -HV part | Specific Requirements | 1.23.3 | The substation is separated into 2 parts: Medium Voltage part including HV transformer and HV portion of the plant excluding the HV transformer | 1 |  |  |  | 1 | [5 empty] | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | 1 |  | Open
Chint | AR | HV Substation | HV Substation -HV part | Specific Requirements | 1.23.3 | Double Busbar single breaker scheme shall be designed for HV portion of HV substation | 1 |  |  |  | 1 | [5 empty] | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | 1 |  | Open
Chint | AR | HV Substation | HV Substation -HV part | HV portion components | 1.23.3 | 132 kV Transformer Bays as per design | 1 |  |  |  | 1 | [5 empty] | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | 1 |  | Open
Chint | AR | HV Substation | HV Substation -HV part | HV portion components | 1.23.3 | 2x132 kV Line Bays | 1 |  |  |  | 1 | [5 empty] | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | 1 |  | Open
Chint | AR | HV Substation | HV Substation -HV part | HV portion components | 1.23.3 | 2x132 kV PT bays | 1 |  |  |  | 1 | [5 empty] | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | 1 |  | Open
Chint | AR | HV Substation | HV Substation -HV part | HV portion components | 1.23.3 | 132 kV Bus Coupler Bay | 1 |  |  |  | 1 | [5 empty] | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | 1 |  | Open
Chint | AR | HV Substation | HV Substation -HV part | HV portion components | 1.23.3 | Telecom and PLC Equipment | 1 |  |  |  | 1 |  |  | Which speification are acepted |  |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | 1 |  | Open
Chint | AR | HV Substation | HV Substation -HV part | Standards | 1.23.3 | All the schemes including SCADA, PLC, protection scheme, control and monitoring scheme and other design factors, shall be in compliance with the NTDC grid code. | 1 |  |  |  | 1 |  |  | Link to NTDC grid code |  |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | 1 |  | Open
Chint | AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | 3-phase, double wound, continuously rated, oil-cooled, enclosed transformers, use of low loss core steel and close coupled copper windings | 1 |  | 1 | [8 empty] | 1 |  | Pass
Chint | AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | Enclosure specifications (e.g., steel floor, fluid tight, sealed tank) | 1 |  | 1 | [8 empty] | 1 |  | Pass
Chint | AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | Incoming terminals | 1 |  | 1 | [8 empty] | 1 |  | Pass
Chint | AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | Outgoing terminals | 1 |  | 1 | [8 empty] | 1 |  | Pass
Chint | AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | kVA rating | 1 |  | 1 | [8 empty] | 1 |  | Pass
Chint | AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | Primary side voltage | 1 |  | 1 | [8 empty] | 1 |  | Pass
Chint | AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | Secondary side voltage | 1 |  | 1 | [8 empty] | 1 |  | Pass
Chint | AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | Vector group | 3 |  | 1 |  |  |  | need to be verified | to be discussed |  |  |  | 1 |  | Pass
Chint | AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | Insulation type | 1 |  | 1 | [8 empty] | 1 |  | Pass
Chint | AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | Frequency rating | 1 |  | 1 | [8 empty] | 1 |  | Pass
Chint | AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | Short-circuit impedance | 1 |  | 1 | [8 empty] | 1 |  | Pass
Chint | AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | Own consumption | 3 |  | 1 | [8 empty] | 1 |  | Pass
Chint | AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | No-load losses | 1 |  | 1 | [8 empty] | 1 |  | Pass
Chint | AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | Efficiency | 1 |  | 1 | [8 empty] | 1 |  | Pass
Chint | AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | Operating temperature range | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | [5 empty] | 1 |  | Open
Chint | AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | Maximum ambient temperature and altitude | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  | to be discussed |  |  |  | 1 |  | Open
Chint | AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | Humidity tolerance | 2 |  | 1 | [8 empty] | 1 |  | Pass
Chint | AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | Cooling method | 1 |  | 1 | [8 empty] | 1 |  | Pass
Chint | AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | Dimensions and weight | 3 |  | 1 | [8 empty] | 1 |  | Pass
Chint | AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | Oil weight | 3 |  |  |  | 1 | [5 empty] | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | 1 |  | Open
Chint | AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | Protection system | 1 |  |  |  | 1 | [5 empty] | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | 1 |  | Open
Chint | AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | Auxiliary service lines | 1 |  |  |  | 1 | [5 empty] | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | 1 |  | Open
Chint | AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | Fittings with the transformer | 3 |  | 1 | [8 empty] | 1 |  | Pass
Chint | AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | Noise levels | 3 |  | 1 | [8 empty] | 1 |  | Pass
Chint | AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | Warranty and insurance | 1 |  | 1 | [8 empty] | 1 |  | Pass
Chint | AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | Tests and inspection routines | 1 |  | 1 | [8 empty] | 1 |  | Pass
Chint | AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | Operational data shall be logged in central operating system (e.g. oil temperature, oil level, pressure, temperature probes (one per phase): Alarm and trip of cell etc.) | 2 | [10 empty] | 0 |  | Open
Chint | AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | All documentation, certificates and test protocols shall be provided | 2 | [10 empty] | 0 |  | Open
Chint | AR | HV Substation | HV Substation -MV/HV Transformer | Standards | 1.23.7 | IEC 62446 | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  |  |  | 1 |  | Open
Chint | AR | HV Substation | HV Substation -MV/HV Transformer | Standards | 1.23.7 | IEC 60076 | 1 |  |  |  | 1 |  |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | 1 |  | Open
Chint | AR | HV Substation | HV Substation -MV/HV Transformer | Standards | 1.23.7 | IEC 60085 | 1 |  |  |  | 1 |  |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | 1 |  | Open
Chint | AR | HV Substation | HV Substation -MV/HV Transformer | Standards | 1.23.7 | IEC 60214 | 1 |  |  |  | 1 |  |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | 1 |  | Open
Chint | AR | HV Substation | HV Substation -MV/HV Transformer | Standards | 1.23.7 | IEC 60137 | 1 |  |  |  | 1 |  |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | 1 |  | Open
Chint | AR | HV Substation | HV Substation -MV/HV Transformer | Standards | 1.23.7 | ASTM d-3487 | 1 |  |  |  | 1 |  |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | 1 |  | Open
Chint | AR | HV Substation | HV Substation -MV/HV Transformer | Quality Assurance | 1.23.7 | Factory witness testing shall be required for MV/HV transformer and switchgear to be installed at this project. | 1 |  |  |  | 1 |  |  | Cannot be evaluated at this stage |  |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | 1 |  | Open
Chint | AR | HV Substation | HV Substation -MV/HV Transformer | Quality Assurance | 1.23.7 | Type test reports from an independent reputable laboratory shall be submitted with the bid. | 1 |  | 1 |  |  |  | need copyfrom orginal |  |  |  |  | 1 |  | Pass
Chint | AR | HV Substation | Due Diligence | Quality Assurance | 1.23.7 | The cost of the due diligence for the HV station to be carried by the Employer through an independent technical consultant will be taken over by the successful bidder up to an amount of 30,000 USD. | 1 |  |  |  | 1 | [5 empty] | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | 1 |  | Open
Chint | AR | HV Substation | HV Substation -MV/HV Transformer | Design | 1.23.8 | The separating equipment shall be installed with visible disconnection (pivotable disconnectors). | 1 |  |  |  | 1 |  |  | Cannot be evaluated at this stage |  |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | 1 |  | Open
Chint | AR | HV Substation | HV Substation -MV/HV Transformer | Design | 1.23.9 | Insulation with PCB (polychlorinated biphenyl) has not been used. | 1 |  | 1 | [8 empty] | 1 |  | Pass
Chint | AR | HV Substation | HV Substation -MV/HV Transformer | Design | 1.23.10 | The preliminary design of the substation is submitted with the technical bid according to the requirements of Appendix 1 | 1 |  |  |  | 1 |  |  | Link to Appendix 1 |  |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | 1 |  | Open
Chint | AR | HV Substation | HV Substation -MV/HV Transformer | Energy Metering System | 1.23.11 | The Energy Metering System will be placed on the HV side of the substation | 1 | [10 empty] | 0 |  | Open
Chint | AR | HV Substation | HV Substation -MV/HV Transformer | Energy Metering System -NTDC specifications | 1.23.11 | Metering Equipment for Electric Energy Transfer between the Companies (Specification No. P-199-08) | 1 |  |  |  | 1 | [5 empty] | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | 1 |  | Open
Chint | AR | HV Substation | HV Substation -MV/HV Transformer | Energy Metering System -NTDC specifications | 1.23.11 | Energy Meters for Grid Metering (Specification No. P-202-2012) | 1 |  |  |  | 1 | [5 empty] | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | 1 |  | Open
Chint | AR | HV Substation | HV Substation -MV/HV Transformer | Energy Metering System -NTDC specifications | 1.23.11 | Voltage Transformers for Special Application (Energy Metering; Specifications No. P-206-05) | 1 |  |  |  | 1 | [5 empty] | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | 1 |  | Open
Chint | AR | HV Substation | HV Substation -MV/HV Transformer | Energy Metering System -NTDC specifications | 1.23.11 | Current Transformers for Special Application (spec.No P-205-2005) | 1 |  |  |  | 1 | [5 empty] | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | 1 |  | Open
Chint | AR | HV Switchgear | HV Switchgear | Project Schedule | 1.24.1 | The switchgear design and order time, for the 132 kV transmission line is detailed and corresponds with the envisaged project schedule. | 1 |  |  |  | 1 | [5 empty] | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | 1 |  | Open
Chint | AR | HV Switchgear | HV Switchgear | Functionalities | 1.24.1 | Nominal system voltage, kV 132 | 1 |  | 1 | [8 empty] | 1 |  | Pass
Chint | AR | HV Switchgear | HV Switchgear | Functionalities | 1.24.1 | Rated voltage of switch gear, kV 145 | 1 |  | 1 | [8 empty] | 1 |  | Pass
Chint | AR | HV Switchgear | HV Switchgear | Functionalities | 1.24.1 | Maximum system voltage, kV 145 | 1 |  | 1 | [8 empty] | 1 |  | Pass
Chint | AR | HV Switchgear | HV Switchgear | Functionalities | 1.24.1 | Rated frequency, Hz 50 | 1 |  | 1 | [8 empty] | 1 |  | Pass
Chint | AR | HV Switchgear | HV Switchgear | Design factors to be provided | 1.24.2 | Rated voltage | 1 |  | 1 | [8 empty] | 1 |  | Pass
Chint | AR | HV Switchgear | HV Switchgear | Design factors to be provided | 1.24.2 | Short-duration power withstand frequency voltage | 3 |  | 1 | [8 empty] | 1 |  | Pass
Chint | AR | HV Switchgear | HV Switchgear | Design factors to be provided | 1.24.2 | Rated lightning impulse withstand voltage | 3 |  | 1 | [8 empty] | 1 |  | Pass
Chint | AR | HV Switchgear | HV Switchgear | Design factors to be provided | 1.24.2 | Rated frequency | 3 |  | 1 | [8 empty] | 1 |  | Pass
Chint | AR | HV Switchgear | HV Switchgear | Design factors to be provided | 1.24.2 | Peak-withstand current | 2 |  | 1 | [8 empty] | 1 |  | Pass
Chint | AR | HV Switchgear | HV Switchgear | Design factors to be provided | 1.24.2 | Short-circuit making current | 2 |  |  |  | 1 | [5 empty] | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | 1 |  | Open
Chint | AR | HV Switchgear | HV Switchgear | Design factors to be provided | 1.24.2 | Short-time withstand current | 2 |  |  |  | 1 | [5 empty] | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | 1 |  | Open
Chint | AR | HV Switchgear | HV Switchgear | Design factors to be provided | 1.24.2 | Short-circuit breaking current | 2 |  |  |  | 1 | [5 empty] | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | 1 |  | Open
Chint | AR | HV Switchgear | HV Switchgear | Design factors to be provided | 1.24.2 | Insulating medium | 2 |  | 1 | [8 empty] | 1 |  | Pass
Chint | AR | HV Switchgear | HV Switchgear | Design factors to be provided | 1.24.2 | Second fault rating | 2 |  |  |  | 1 | [5 empty] | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | 1 |  | Open
Chint | AR | HV Switchgear | HV Switchgear | Design factors to be provided | 1.24.2 | Busbars | 3 |  | 1 | [8 empty] | 1 |  | Pass
Chint | AR | HV Switchgear | HV Switchgear | Design factors to be provided | 1.24.2 | Rated normal current for busbars | 3 |  | 1 | [8 empty] | 1 |  | Pass
Chint | AR | HV Switchgear | HV Switchgear | Design factors to be provided | 1.24.2 | Rated normal current for feeders | 3 |  | 1 | [8 empty] | 1 |  | Pass
Chint | AR | HV Switchgear | HV Switchgear | Design factors to be provided | 1.24.2 | Degree of protection | 2 |  |  |  | 1 | [5 empty] | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | 1 |  | Open
Chint | AR | HV Switchgear | HV Switchgear | Design factors to be provided | 1.24.2 | Second internal arc rating | 3 |  |  |  | 1 | [5 empty] | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | 1 |  | Open
Chint | AR | HV Switchgear | HV Switchgear | Design factors to be provided | 1.24.2 | Circuit breakers: protection and metering | 1 |  |  |  | 1 | [5 empty] | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | 1 |  | Open
Chint | AR | HV Switchgear | HV Switchgear | Design factors to be provided | 1.24.2 | Protection relay | 1 |  |  |  | 1 | [5 empty] | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | 1 |  | Open
Chint | AR | HV Switchgear | HV Switchgear | Design factors to be provided | 1.24.2 | Switch disconnector panel | 2 |  |  |  | 1 | [5 empty] | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | 1 |  | Open
Chint | AR | HV Switchgear | HV Switchgear | Design factors to be provided | 1.24.2 | Operating temperature range | 1 |  |  |  | 1 | [5 empty] | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | 1 |  | Open
Chint | AR | HV Switchgear | HV Switchgear | Design factors to be provided | 1.24.2 | Warranty and insurance | 1 | 1 | [9 empty] | 0 |  | Open
Chint | AR | HV Switchgear | HV Switchgear | Design factors to be provided | 1.24.2 | Dimensions and weight | 3 |  |  |  | 1 | [5 empty] | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | 1 |  | Open
Chint | AR | HV Switchgear | HV Switchgear | Design factors to be provided | 1.24.2 | NEMA enclosure type and IP code | 1 |  |  |  | 1 | [5 empty] | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | 1 |  | Open
Chint | AR | HV Switchgear | HV Switchgear | Standards | 1.24.2 | IEC 60038 | 1 |  |  |  | 1 |  |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | 1 |  | Open
Chint | AR | HV Switchgear | HV Switchgear | Standards | 1.24.2 | IEC 60095 | 1 |  |  |  | 1 |  |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | 1 |  | Open
Chint | AR | HV Switchgear | HV Switchgear | Standards | 1.24.2 | IEC 62271-200 | 1 |  |  |  | 1 |  |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | 1 |  | Open
Chint | AR | HV Switchgear | HV Switchgear | Standards | 1.24.2 | IEC 60364 | 1 |  |  |  | 1 |  |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | 1 |  | Open
Chint | AR | HV Switchgear | HV Switchgear | Standards | 1.24.2 | Factory witness testing will are required for HV switchgear | 1 |  |  |  | 1 |  |  | Cannot be evaluated at this stage |  |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | 1 |  | Open
Chint | AR | HV Switchgear | HV Switchgear | Standards | 1.24.3 | Type test reports from an independent reputable laboratory shall be submitted | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | [5 empty] | 1 |  | Open
Chint | AR | HV Switchgear | Due Diligence | Quality Assurance | 1.24.3 | The cost of the due diligence to be carried by the Employer through an independent technical consultant will be taken over by the successful bidder up to an amount of 50,000 USD. | 1 |  |  |  | 1 | [5 empty] | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | 1 |  | Open
Zte | AR | HV Substation | HV Substation | Specific Requirements | 1.23.1 | The HV Substation includes the respective MV switch gears, Transformer MV/ HV. The HV connection is designed to connect to the HV line. | 3 |  | 1 | [8 empty] | 1 |  | Pass
Zte | AR | HV Substation | HV Substation | Specific Requirements | 1.23.2 | Availability and delivery time of the chosen components is detailed | 1 |  |  |  | 1 | [5 empty] | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | 1 |  | Open
Zte | AR | HV Substation | HV Substation -HV part | Specific Requirements | 1.23.3 | The substation is separated into 2 parts: Medium Voltage part including HV transformer and HV portion of the plant excluding the HV transformer | 1 |  | 1 | [8 empty] | 1 |  | Pass
Zte | AR | HV Substation | HV Substation -HV part | Specific Requirements | 1.23.3 | Double Busbar single breaker scheme shall be designed for HV portion of HV substation | 1 |  | 1 | [8 empty] | 1 |  | Pass
Zte | AR | HV Substation | HV Substation -HV part | HV portion components | 1.23.3 | 132 kV Transformer Bays as per design | 1 |  | 1 | [8 empty] | 1 |  | Pass
Zte | AR | HV Substation | HV Substation -HV part | HV portion components | 1.23.3 | 2x132 kV Line Bays | 1 |  | 1 | [8 empty] | 1 |  | Pass
Zte | AR | HV Substation | HV Substation -HV part | HV portion components | 1.23.3 | 2x132 kV PT bays | 1 |  | 1 | [8 empty] | 1 |  | Pass
Zte | AR | HV Substation | HV Substation -HV part | HV portion components | 1.23.3 | 132 kV Bus Coupler Bay | 1 |  | 1 | [8 empty] | 1 |  | Pass
Zte | AR | HV Substation | HV Substation -HV part | HV portion components | 1.23.3 | Telecom and PLC Equipment | 1 |  |  |  | 1 |  |  | Which speification are acepted |  |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | 1 |  | Open
Zte | AR | HV Substation | HV Substation -HV part | Standards | 1.23.3 | All the schemes including SCADA, PLC, protection scheme, control and monitoring scheme and other design factors, shall be in compliance with the NTDC grid code. | 1 |  |  |  | 1 |  |  | Link to NTDC grid code |  |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | 1 |  | Open
Zte | AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | 3-phase, double wound, continuously rated, oil-cooled, enclosed transformers, use of low loss core steel and close coupled copper windings | 1 |  | 1 | [8 empty] | 1 |  | Pass
Zte | AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | Enclosure specifications (e.g., steel floor, fluid tight, sealed tank) | 1 |  | 1 | [8 empty] | 1 |  | Pass
Zte | AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | Incoming terminals | 1 |  | 1 | [8 empty] | 1 |  | Pass
Zte | AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | Outgoing terminals | 1 |  | 1 | [8 empty] | 1 |  | Pass
Zte | AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | kVA rating | 1 |  | 1 | [8 empty] | 1 |  | Pass
Zte | AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | Primary side voltage | 1 |  | 1 | [8 empty] | 1 |  | Pass
Zte | AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | Secondary side voltage | 1 |  | 1 | [8 empty] | 1 |  | Pass
Zte | AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | Vector group | 3 |  | 1 |  |  |  |  | to be discussed |  |  |  | 1 |  | Pass
Zte | AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | Insulation type | 1 |  | 1 | [8 empty] | 1 |  | Pass
Zte | AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | Frequency rating | 1 |  | 1 | [8 empty] | 1 |  | Pass
Zte | AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | Short-circuit impedance | 1 |  | 1 | [8 empty] | 1 |  | Pass
Zte | AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | Own consumption | 3 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | [5 empty] | 1 |  | Open
Zte | AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | No-load losses | 1 |  | 1 | [8 empty] | 1 |  | Pass
Zte | AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | Efficiency | 1 |  | 1 | [8 empty] | 1 |  | Pass
Zte | AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | Operating temperature range | 1 |  | 1 | [8 empty] | 1 |  | Pass
Zte | AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | Maximum ambient temperature and altitude | 1 |  | 1 |  |  |  |  | to be discussed |  |  |  | 1 |  | Pass
Zte | AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | Humidity tolerance | 2 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | [5 empty] | 1 |  | Open
Zte | AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | Cooling method | 1 |  | 1 | [8 empty] | 1 |  | Pass
Zte | AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | Dimensions and weight | 3 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | [5 empty] | 1 |  | Open
Zte | AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | Oil weight | 3 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | [5 empty] | 1 |  | Open
Zte | AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | Protection system | 1 |  | 1 | [8 empty] | 1 |  | Pass
Zte | AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | Auxiliary service lines | 1 |  | 1 | [8 empty] | 1 |  | Pass
Zte | AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | Fittings with the transformer | 3 |  | 1 | [8 empty] | 1 |  | Pass
Zte | AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | Noise levels | 3 |  |  |  | 1 | [5 empty] | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | 1 |  | Open
Zte | AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | Warranty and insurance | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | [5 empty] | 1 |  | Open
Zte | AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | Tests and inspection routines | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | [5 empty] | 1 |  | Open
Zte | AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | Operational data shall be logged in central operating system (e.g. oil temperature, oil level, pressure, temperature probes (one per phase): Alarm and trip of cell etc.) | 2 |  | 1 | [8 empty] | 1 |  | Pass
Zte | AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | All documentation, certificates and test protocols shall be provided | 2 |  |  |  | 1 | [5 empty] | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | 1 |  | Open
Zte | AR | HV Substation | HV Substation -MV/HV Transformer | Standards | 1.23.7 | IEC 62446 | 1 |  |  |  | 1 |  |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | 1 |  | Open
Zte | AR | HV Substation | HV Substation -MV/HV Transformer | Standards | 1.23.7 | IEC 60076 | 1 |  | 1 |  |  |  |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  |  |  | 1 |  | Pass
Zte | AR | HV Substation | HV Substation -MV/HV Transformer | Standards | 1.23.7 | IEC 60085 | 1 |  |  |  | 1 |  |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | 1 |  | Open
Zte | AR | HV Substation | HV Substation -MV/HV Transformer | Standards | 1.23.7 | IEC 60214 | 1 |  |  |  | 1 |  |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | 1 |  | Open
Zte | AR | HV Substation | HV Substation -MV/HV Transformer | Standards | 1.23.7 | IEC 60137 | 1 |  |  |  | 1 |  |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | 1 |  | Open
Zte | AR | HV Substation | HV Substation -MV/HV Transformer | Standards | 1.23.7 | ASTM d-3487 | 1 |  |  |  | 1 |  |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | 1 |  | Open
Zte | AR | HV Substation | HV Substation -MV/HV Transformer | Quality Assurance | 1.23.7 | Factory witness testing shall be required for MV/HV transformer and switchgear to be installed at this project. | 1 |  |  |  | 1 |  |  | Cannot be evaluated at this stage |  |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | 1 |  | Open
Zte | AR | HV Substation | HV Substation -MV/HV Transformer | Quality Assurance | 1.23.7 | Type test reports from an independent reputable laboratory shall be submitted with the bid. | 1 |  |  |  | 1 | [5 empty] | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | 1 |  | Open
Zte | AR | HV Substation | Due Diligence | Quality Assurance | 1.23.7 | The cost of the due diligence for the HV station to be carried by the Employer through an independent technical consultant will be taken over by the successful bidder up to an amount of 30,000 USD. | 1 |  |  |  | 1 | [5 empty] | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | 1 |  | Open
Zte | AR | HV Substation | HV Substation -MV/HV Transformer | Design | 1.23.8 | The separating equipment shall be installed with visible disconnection (pivotable disconnectors). | 1 |  | 1 |  |  |  |  | Cannot be evaluated at this stage |  |  |  | 1 |  | Pass
Zte | AR | HV Substation | HV Substation -MV/HV Transformer | Design | 1.23.9 | Insulation with PCB (polychlorinated biphenyl) has not been used. | 1 |  |  |  | 1 | [5 empty] | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | 1 |  | Open
Zte | AR | HV Substation | HV Substation -MV/HV Transformer | Design | 1.23.10 | The preliminary design of the substation is submitted with the technical bid according to the requirements of Appendix 1 | 1 |  | 1 |  |  |  |  | Link to Appendix 1 |  |  |  | 1 |  | Pass
Zte | AR | HV Substation | HV Substation -MV/HV Transformer | Energy Metering System | 1.23.11 | The Energy Metering System will be placed on the HV side of the substation | 1 |  |  |  | 1 | [5 empty] | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | 1 |  | Open
Zte | AR | HV Substation | HV Substation -MV/HV Transformer | Energy Metering System -NTDC specifications | 1.23.11 | Metering Equipment for Electric Energy Transfer between the Companies (Specification No. P-199-08) | 1 |  |  |  | 1 | [5 empty] | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | 1 |  | Open
Zte | AR | HV Substation | HV Substation -MV/HV Transformer | Energy Metering System -NTDC specifications | 1.23.11 | Energy Meters for Grid Metering (Specification No. P-202-2012) | 1 |  |  |  | 1 | [5 empty] | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | 1 |  | Open
Zte | AR | HV Substation | HV Substation -MV/HV Transformer | Energy Metering System -NTDC specifications | 1.23.11 | Voltage Transformers for Special Application (Energy Metering; Specifications No. P-206-05) | 1 |  | 1899-12-31 | [8 empty] | 1 |  | Pass
Zte | AR | HV Substation | HV Substation -MV/HV Transformer | Energy Metering System -NTDC specifications | 1.23.11 | Current Transformers for Special Application (spec.No P-205-2005) | 1 |  | 1 | [8 empty] | 1 |  | Pass
Zte | AR | HV Switchgear | HV Switchgear | Project Schedule | 1.24.1 | The switchgear design and order time, for the 132 kV transmission line is detailed and corresponds with the envisaged project schedule. | 1 |  |  |  | 1 | [5 empty] | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | 1 |  | Open
Zte | AR | HV Switchgear | HV Switchgear | Functionalities | 1.24.1 | Nominal system voltage, kV 132 | 1 |  | 1 | [8 empty] | 1 |  | Pass
Zte | AR | HV Switchgear | HV Switchgear | Functionalities | 1.24.1 | Rated voltage of switch gear, kV 145 | 1 |  | 1 | [8 empty] | 1 |  | Pass
Zte | AR | HV Switchgear | HV Switchgear | Functionalities | 1.24.1 | Maximum system voltage, kV 145 | 1 |  | 1 | [8 empty] | 1 |  | Pass
Zte | AR | HV Switchgear | HV Switchgear | Functionalities | 1.24.1 | Rated frequency, Hz 50 | 1 |  | 1 | [8 empty] | 1 |  | Pass
Zte | AR | HV Switchgear | HV Switchgear | Design factors to be provided | 1.24.2 | Rated voltage | 1 |  | 1 | [8 empty] | 1 |  | Pass
Zte | AR | HV Switchgear | HV Switchgear | Design factors to be provided | 1.24.2 | Short-duration power withstand frequency voltage | 3 |  |  |  | 1 | [5 empty] | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | 1 |  | Open
Zte | AR | HV Switchgear | HV Switchgear | Design factors to be provided | 1.24.2 | Rated lightning impulse withstand voltage | 3 |  |  |  | 1 | [5 empty] | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | 1 |  | Open
Zte | AR | HV Switchgear | HV Switchgear | Design factors to be provided | 1.24.2 | Rated frequency | 3 |  | 1 | [8 empty] | 1 |  | Pass
Zte | AR | HV Switchgear | HV Switchgear | Design factors to be provided | 1.24.2 | Peak-withstand current | 2 |  |  |  | 1 | [5 empty] | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | 1 |  | Open
Zte | AR | HV Switchgear | HV Switchgear | Design factors to be provided | 1.24.2 | Short-circuit making current | 2 |  |  |  | 1 | [5 empty] | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | 1 |  | Open
Zte | AR | HV Switchgear | HV Switchgear | Design factors to be provided | 1.24.2 | Short-time withstand current | 2 |  |  |  | 1 | [5 empty] | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | 1 |  | Open
Zte | AR | HV Switchgear | HV Switchgear | Design factors to be provided | 1.24.2 | Short-circuit breaking current | 2 |  |  |  | 1 | [5 empty] | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | 1 |  | Open
Zte | AR | HV Switchgear | HV Switchgear | Design factors to be provided | 1.24.2 | Insulating medium | 2 |  | 1 | [8 empty] | 1 |  | Pass
Zte | AR | HV Switchgear | HV Switchgear | Design factors to be provided | 1.24.2 | Second fault rating | 2 |  |  |  | 1 | [5 empty] | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | 1 |  | Open
Zte | AR | HV Switchgear | HV Switchgear | Design factors to be provided | 1.24.2 | Busbars | 3 |  | 1 | [8 empty] | 1 |  | Pass
Zte | AR | HV Switchgear | HV Switchgear | Design factors to be provided | 1.24.2 | Rated normal current for busbars | 3 |  | 1 | [8 empty] | 1 |  | Pass
Zte | AR | HV Switchgear | HV Switchgear | Design factors to be provided | 1.24.2 | Rated normal current for feeders | 3 |  | 1 | [8 empty] | 1 |  | Pass
Zte | AR | HV Switchgear | HV Switchgear | Design factors to be provided | 1.24.2 | Degree of protection | 2 |  |  |  | 1 | [5 empty] | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | 1 |  | Open
Zte | AR | HV Switchgear | HV Switchgear | Design factors to be provided | 1.24.2 | Second internal arc rating | 3 |  |  |  | 1 | [5 empty] | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | 1 |  | Open
Zte | AR | HV Switchgear | HV Switchgear | Design factors to be provided | 1.24.2 | Circuit breakers: protection and metering | 1 |  |  |  | 1 | [5 empty] | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | 1 |  | Open
Zte | AR | HV Switchgear | HV Switchgear | Design factors to be provided | 1.24.2 | Protection relay | 1 |  |  |  | 1 | [5 empty] | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | 1 |  | Open
Zte | AR | HV Switchgear | HV Switchgear | Design factors to be provided | 1.24.2 | Switch disconnector panel | 2 |  |  |  | 1 | [5 empty] | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | 1 |  | Open
Zte | AR | HV Switchgear | HV Switchgear | Design factors to be provided | 1.24.2 | Operating temperature range | 1 |  |  |  | 1 | [5 empty] | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | 1 |  | Open
Zte | AR | HV Switchgear | HV Switchgear | Design factors to be provided | 1.24.2 | Warranty and insurance | 1 |  |  |  | 1 | [5 empty] | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | 1 |  | Open
Zte | AR | HV Switchgear | HV Switchgear | Design factors to be provided | 1.24.2 | Dimensions and weight | 3 |  |  |  | 1 | [5 empty] | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | 1 |  | Open
Zte | AR | HV Switchgear | HV Switchgear | Design factors to be provided | 1.24.2 | NEMA enclosure type and IP code | 1 |  |  |  | 1 | [5 empty] | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | 1 |  | Open
Zte | AR | HV Switchgear | HV Switchgear | Standards | 1.24.2 | IEC 60038 | 1 |  |  |  | 1 |  |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | 1 |  | Open
Zte | AR | HV Switchgear | HV Switchgear | Standards | 1.24.2 | IEC 60095 | 1 |  |  |  | 1 |  |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | 1 |  | Open
Zte | AR | HV Switchgear | HV Switchgear | Standards | 1.24.2 | IEC 62271-200 | 1 |  |  |  | 1 |  |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | 1 |  | Open
Zte | AR | HV Switchgear | HV Switchgear | Standards | 1.24.2 | IEC 60364 | 1 |  |  |  | 1 |  |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | 1 |  | Open
Zte | AR | HV Switchgear | HV Switchgear | Standards | 1.24.2 | Factory witness testing will are required for HV switchgear | 1 | [6 empty] | Cannot be evaluated at this stage |  |  |  | 0 |  | Open
Zte | AR | HV Switchgear | HV Switchgear | Standards | 1.24.3 | Type test reports from an independent reputable laboratory shall be submitted | 1 | [10 empty] | 0 |  | Open
Zte | AR | HV Switchgear | Due Diligence | Quality Assurance | 1.24.3 | The cost of the due diligence to be carried by the Employer through an independent technical consultant will be taken over by the successful bidder up to an amount of 50,000 USD. | 1 | [10 empty] | 0 |  | Open
Tbea | AR | HV Substation | HV Substation | Specific Requirements | 1.23.1 | The HV Substation includes the respective MV switch gears, Transformer MV/ HV. The HV connection is designed to connect to the HV line. | 3 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | AR | HV Substation | HV Substation | Specific Requirements | 1.23.2 | Availability and delivery time of the chosen components is detailed | 1 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | AR | HV Substation | HV Substation -HV part | Specific Requirements | 1.23.3 | The substation is separated into 2 parts: Medium Voltage part including HV transformer and HV portion of the plant excluding the HV transformer | 1 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | AR | HV Substation | HV Substation -HV part | Specific Requirements | 1.23.3 | Double Busbar single breaker scheme shall be designed for HV portion of HV substation | 1 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | AR | HV Substation | HV Substation -HV part | HV portion components | 1.23.3 | 132 kV Transformer Bays as per design | 1 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | AR | HV Substation | HV Substation -HV part | HV portion components | 1.23.3 | 2x132 kV Line Bays | 1 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | AR | HV Substation | HV Substation -HV part | HV portion components | 1.23.3 | 2x132 kV PT bays | 1 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | AR | HV Substation | HV Substation -HV part | HV portion components | 1.23.3 | 132 kV Bus Coupler Bay | 1 |  |  |  | 1 | [5 empty] | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | 1 |  | Open
Tbea | AR | HV Substation | HV Substation -HV part | HV portion components | 1.23.3 | Telecom and PLC Equipment | 1 |  |  |  | 1 |  |  | Which speification are acepted |  |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | 1 |  | Open
Tbea | AR | HV Substation | HV Substation -HV part | Standards | 1.23.3 | All the schemes including SCADA, PLC, protection scheme, control and monitoring scheme and other design factors, shall be in compliance with the NTDC grid code. | 1 |  | 1 |  |  |  |  | Link to NTDC grid code |  |  |  | 1 |  | Pass
Tbea | AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | 3-phase, double wound, continuously rated, oil-cooled, enclosed transformers, use of low loss core steel and close coupled copper windings | 1 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | Enclosure specifications (e.g., steel floor, fluid tight, sealed tank) | 1 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | Incoming terminals | 1 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | Outgoing terminals | 1 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | kVA rating | 1 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | Primary side voltage | 1 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | Secondary side voltage | 1 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | Vector group | 3 |  | 1 |  |  |  |  | to be discussed |  |  |  | 1 |  | Pass
Tbea | AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | Insulation type | 1 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | Frequency rating | 1 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | Short-circuit impedance | 1 |  |  |  | 1 | [5 empty] | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | 1 |  | Open
Tbea | AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | Own consumption | 3 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | No-load losses | 1 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | Efficiency | 1 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | Operating temperature range | 1 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | Maximum ambient temperature and altitude | 1 |  |  |  | 1 |  |  | to be discussed |  |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | 1 |  | Open
Tbea | AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | Humidity tolerance | 2 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | [5 empty] | 1 |  | Open
Tbea | AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | Cooling method | 1 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | Dimensions and weight | 3 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | [5 empty] | 1 |  | Open
Tbea | AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | Oil weight | 3 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | [5 empty] | 1 |  | Open
Tbea | AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | Protection system | 1 |  | 1 |  |  |  | to be submitted and confirm to meet the requirements |  |  |  |  | 1 |  | Pass
Tbea | AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | Auxiliary service lines | 1 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | Fittings with the transformer | 3 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | Noise levels | 3 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | [5 empty] | 1 |  | Open
Tbea | AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | Warranty and insurance | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | [5 empty] | 1 |  | Open
Tbea | AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | Tests and inspection routines | 1 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | Operational data shall be logged in central operating system (e.g. oil temperature, oil level, pressure, temperature probes (one per phase): Alarm and trip of cell etc.) | 2 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | All documentation, certificates and test protocols shall be provided | 2 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | [5 empty] | 1 |  | Open
Tbea | AR | HV Substation | HV Substation -MV/HV Transformer | Standards | 1.23.7 | IEC 62446 | 1 |  | 1 |  |  |  |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  |  |  | 1 |  | Pass
Tbea | AR | HV Substation | HV Substation -MV/HV Transformer | Standards | 1.23.7 | IEC 60076 | 1 |  | 1 |  |  |  |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  |  |  | 1 |  | Pass
Tbea | AR | HV Substation | HV Substation -MV/HV Transformer | Standards | 1.23.7 | IEC 60085 | 1 |  | 1 |  |  |  |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  |  |  | 1 |  | Pass
Tbea | AR | HV Substation | HV Substation -MV/HV Transformer | Standards | 1.23.7 | IEC 60214 | 1 |  | 1 |  |  |  |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  |  |  | 1 |  | Pass
Tbea | AR | HV Substation | HV Substation -MV/HV Transformer | Standards | 1.23.7 | IEC 60137 | 1 |  | 1 |  |  |  |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  |  |  | 1 |  | Pass
Tbea | AR | HV Substation | HV Substation -MV/HV Transformer | Standards | 1.23.7 | ASTM d-3487 | 1 |  | 1 |  |  |  |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  |  |  | 1 |  | Pass
Tbea | AR | HV Substation | HV Substation -MV/HV Transformer | Quality Assurance | 1.23.7 | Factory witness testing shall be required for MV/HV transformer and switchgear to be installed at this project. | 1 |  |  |  | 1 |  |  | Cannot be evaluated at this stage |  |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | 1 |  | Open
Tbea | AR | HV Substation | HV Substation -MV/HV Transformer | Quality Assurance | 1.23.7 | Type test reports from an independent reputable laboratory shall be submitted with the bid. | 1 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | AR | HV Substation | Due Diligence | Quality Assurance | 1.23.7 | The cost of the due diligence for the HV station to be carried by the Employer through an independent technical consultant will be taken over by the successful bidder up to an amount of 30,000 USD. | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | [5 empty] | 1 |  | Open
Tbea | AR | HV Substation | HV Substation -MV/HV Transformer | Design | 1.23.8 | The separating equipment shall be installed with visible disconnection (pivotable disconnectors). | 1 |  | 1 |  |  |  |  | Cannot be evaluated at this stage |  |  |  | 1 |  | Pass
Tbea | AR | HV Substation | HV Substation -MV/HV Transformer | Design | 1.23.9 | Insulation with PCB (polychlorinated biphenyl) has not been used. | 1 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | AR | HV Substation | HV Substation -MV/HV Transformer | Design | 1.23.10 | The preliminary design of the substation is submitted with the technical bid according to the requirements of Appendix 1 | 1 |  | 1 |  |  |  |  | Link to Appendix 1 |  |  |  | 1 |  | Pass
Tbea | AR | HV Substation | HV Substation -MV/HV Transformer | Energy Metering System | 1.23.11 | The Energy Metering System will be placed on the HV side of the substation | 1 |  |  |  | 1 | [5 empty] | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | 1 |  | Open
Tbea | AR | HV Substation | HV Substation -MV/HV Transformer | Energy Metering System -NTDC specifications | 1.23.11 | Metering Equipment for Electric Energy Transfer between the Companies (Specification No. P-199-08) | 1 |  |  |  | 1 | [5 empty] | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | 1 |  | Open
Tbea | AR | HV Substation | HV Substation -MV/HV Transformer | Energy Metering System -NTDC specifications | 1.23.11 | Energy Meters for Grid Metering (Specification No. P-202-2012) | 1 |  |  |  | 1 | [5 empty] | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | 1 |  | Open
Tbea | AR | HV Substation | HV Substation -MV/HV Transformer | Energy Metering System -NTDC specifications | 1.23.11 | Voltage Transformers for Special Application (Energy Metering; Specifications No. P-206-05) | 1 |  | 1899-12-31 | [8 empty] | 1 |  | Pass
Tbea | AR | HV Substation | HV Substation -MV/HV Transformer | Energy Metering System -NTDC specifications | 1.23.11 | Current Transformers for Special Application (spec.No P-205-2005) | 1 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | AR | HV Switchgear | HV Switchgear | Project Schedule | 1.24.1 | The switchgear design and order time, for the 132 kV transmission line is detailed and corresponds with the envisaged project schedule. | 1 |  |  |  | 1 | [5 empty] | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | 1 |  | Open
Tbea | AR | HV Switchgear | HV Switchgear | Functionalities | 1.24.1 | Nominal system voltage, kV 132 | 1 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | AR | HV Switchgear | HV Switchgear | Functionalities | 1.24.1 | Rated voltage of switch gear, kV 145 | 1 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | AR | HV Switchgear | HV Switchgear | Functionalities | 1.24.1 | Maximum system voltage, kV 145 | 1 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | AR | HV Switchgear | HV Switchgear | Functionalities | 1.24.1 | Rated frequency, Hz 50 | 1 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | AR | HV Switchgear | HV Switchgear | Design factors to be provided | 1.24.2 | Rated voltage | 1 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | AR | HV Switchgear | HV Switchgear | Design factors to be provided | 1.24.2 | Short-duration power withstand frequency voltage | 3 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | [5 empty] | 1 |  | Open
Tbea | AR | HV Switchgear | HV Switchgear | Design factors to be provided | 1.24.2 | Rated lightning impulse withstand voltage | 3 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | [5 empty] | 1 |  | Open
Tbea | AR | HV Switchgear | HV Switchgear | Design factors to be provided | 1.24.2 | Rated frequency | 3 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | AR | HV Switchgear | HV Switchgear | Design factors to be provided | 1.24.2 | Peak-withstand current | 2 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | [5 empty] | 1 |  | Open
Tbea | AR | HV Switchgear | HV Switchgear | Design factors to be provided | 1.24.2 | Short-circuit making current | 2 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | [5 empty] | 1 |  | Open
Tbea | AR | HV Switchgear | HV Switchgear | Design factors to be provided | 1.24.2 | Short-time withstand current | 2 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | [5 empty] | 1 |  | Open
Tbea | AR | HV Switchgear | HV Switchgear | Design factors to be provided | 1.24.2 | Short-circuit breaking current | 2 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | [5 empty] | 1 |  | Open
Tbea | AR | HV Switchgear | HV Switchgear | Design factors to be provided | 1.24.2 | Insulating medium | 2 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | AR | HV Switchgear | HV Switchgear | Design factors to be provided | 1.24.2 | Second fault rating | 2 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | [5 empty] | 1 |  | Open
Tbea | AR | HV Switchgear | HV Switchgear | Design factors to be provided | 1.24.2 | Busbars | 3 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | [5 empty] | 1 |  | Open
Tbea | AR | HV Switchgear | HV Switchgear | Design factors to be provided | 1.24.2 | Rated normal current for busbars | 3 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | [5 empty] | 1 |  | Open
Tbea | AR | HV Switchgear | HV Switchgear | Design factors to be provided | 1.24.2 | Rated normal current for feeders | 3 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | [5 empty] | 1 |  | Open
Tbea | AR | HV Switchgear | HV Switchgear | Design factors to be provided | 1.24.2 | Degree of protection | 2 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | [5 empty] | 1 |  | Open
Tbea | AR | HV Switchgear | HV Switchgear | Design factors to be provided | 1.24.2 | Second internal arc rating | 3 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | [5 empty] | 1 |  | Open
Tbea | AR | HV Switchgear | HV Switchgear | Design factors to be provided | 1.24.2 | Circuit breakers: protection and metering | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | [5 empty] | 1 |  | Open
Tbea | AR | HV Switchgear | HV Switchgear | Design factors to be provided | 1.24.2 | Protection relay | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | [5 empty] | 1 |  | Open
Tbea | AR | HV Switchgear | HV Switchgear | Design factors to be provided | 1.24.2 | Switch disconnector panel | 2 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | [5 empty] | 1 |  | Open
Tbea | AR | HV Switchgear | HV Switchgear | Design factors to be provided | 1.24.2 | Operating temperature range | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | [5 empty] | 1 |  | Open
Tbea | AR | HV Switchgear | HV Switchgear | Design factors to be provided | 1.24.2 | Warranty and insurance | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | [5 empty] | 1 |  | Open
Tbea | AR | HV Switchgear | HV Switchgear | Design factors to be provided | 1.24.2 | Dimensions and weight | 3 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | [5 empty] | 1 |  | Open
Tbea | AR | HV Switchgear | HV Switchgear | Design factors to be provided | 1.24.2 | NEMA enclosure type and IP code | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | [5 empty] | 1 |  | Open
Tbea | AR | HV Switchgear | HV Switchgear | Standards | 1.24.2 | IEC 60038 | 1 |  | 1 |  |  |  |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  |  |  | 1 |  | Pass
Tbea | AR | HV Switchgear | HV Switchgear | Standards | 1.24.2 | IEC 60095 | 1 |  | 1 |  |  |  |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  |  |  | 1 |  | Pass
Tbea | AR | HV Switchgear | HV Switchgear | Standards | 1.24.2 | IEC 62271-200 | 1 |  | 1 |  |  |  |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  |  |  | 1 |  | Pass
Tbea | AR | HV Switchgear | HV Switchgear | Standards | 1.24.2 | IEC 60364 | 1 |  | 1 |  |  |  |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  |  |  | 1 |  | Pass
Tbea | AR | HV Switchgear | HV Switchgear | Standards | 1.24.2 | Factory witness testing will are required for HV switchgear | 1 | [6 empty] | Cannot be evaluated at this stage |  |  |  | 0 |  | Open
Tbea | AR | HV Switchgear | HV Switchgear | Standards | 1.24.3 | Type test reports from an independent reputable laboratory shall be submitted | 1 |  |  |  | 1 | [5 empty] | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | 1 |  | Open
Tbea | AR | HV Switchgear | Due Diligence | Quality Assurance | 1.24.3 | The cost of the due diligence to be carried by the Employer through an independent technical consultant will be taken over by the successful bidder up to an amount of 50,000 USD. | 1 |  |  |  | 1 | [5 empty] | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | 1 |  | Open

## Questions (hidden)
Bidder | Expert | Chapter in RfP | Topic | Subtopic | Clause | Criteria | 1 Vital 2 Valuable 3 Not Important | Link to Bidders Documents | Pass =1 | Fail =1 | Open =1 | Question to bidder for clarification | Comments | Comments QA on Criteria | Comment on "Comments" | Typical Questions to be send to bidders if Open status | Standard Text | Check | Prio | Result
Juwi | RM | Supervisory Control and Data Acquisition (SCADA) | SCADA | Specific Requirements | 1.9.1 | Safe and redundant archive for operational data. | 1 | Annex 11 | 1 |  |  |  | 1.14 page 25 ff >> Annex 11 on site data logging Analyse, compare, grafics, reports, fault management, overview, web interface, plant map, |  |  |  |  | 1 |  | Pass
Juwi | RM | Supervisory Control and Data Acquisition (SCADA) | SCADA | Specific Requirements | 1.9.1 | Remote access to all operational data for independent monitoring purposes shall be possible (NTDC requirements) | 1 |  | 1 |  |  |  | RS485 and CAN Bus fibre optics Web interface |  |  |  |  | 1 |  | Pass
Juwi | RM | Supervisory Control and Data Acquisition (SCADA) | SCADA | Specific Requirements | 1.9.1 | The system has to provide different access-levels with different access rights allocated. | 1 |  |  |  | 1 | please confirm and describe "read only", "write" | [5 empty] | 1 |  | Open
Juwi | RM | Supervisory Control and Data Acquisition (SCADA) | SCADA | Specific Requirements | 1.9.2 | Control room to remotely monitor and manage the whole system, on a 24 x 7 basis, with the capability of Web-based information sharing | 1 |  |  |  | 1 | please describe | [5 empty] | 1 |  | Open
Juwi | RM | Supervisory Control and Data Acquisition (SCADA) | SCADA | Specific Requirements | 1.9.2 | Alarms/alerts and timely notification of key performance indicators | 1 |  | 1 | [8 empty] | 1 |  | Pass
Juwi | RM | Supervisory Control and Data Acquisition (SCADA) | SCADA | Specific Requirements | 1.9.2 | Data must be readily available for the fulfilment of all warranties and performance guarantees | 1 |  | 1 |  |  | Please confirm seperately | by description of data management this is most likely possible | Cannot be evaluated at this stage. | statement |  |  | 1 |  | Pass
Juwi | RM | Supervisory Control and Data Acquisition (SCADA) | SCADA | Specific Requirements | 1.9.2 | Data logging at intervals of not less than one minute, processing, transmission, and back-up | 1 |  | 1 |  |  | Correct meaning was: maximum interval length of 1 minute. Please confirm. |  |  | not more (!) |  |  | 1 |  | Pass
Juwi | RM | Supervisory Control and Data Acquisition (SCADA) | SCADA | Specific Requirements | 1.9.2 | Separate inverter, zone, and string level (current and voltage) monitoring | 1 | p384 | 1 | [8 empty] | 1 |  | Pass
Juwi | RM | Supervisory Control and Data Acquisition (SCADA) | SCADA | Specific Requirements | 1.9.2 | Back-up power for a minimum of twelve hours | 1 |  | 1 |  |  |  | 40h |  |  |  |  | 1 |  | Pass
Juwi | RM | Supervisory Control and Data Acquisition (SCADA) | SCADA | Specific Requirements | 1.9.2 | Data shall be provided via FTP (Push/Pull) to the Employer | 1 | p385 | 1 |  |  | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | [5 empty] | 1 |  | Pass
Juwi | RM | Supervisory Control and Data Acquisition (SCADA) | SCADA | Specific Requirements | 1.9.2 | All communication/data cables outside of buildings must be fiber-optic cables | 1 |  | 1 |  |  | general option. Please confirm delivery | [5 empty] | 1 |  | Pass
Juwi | RM | Meteorological Sensors | Auxiliary Systems | Specific Requirements | 1.10.1 | Irradiation and temperature measurements are to be recorded at intervals of 15 min or less. | 1 |  | 1 |  |  |  | 1 min |  |  |  |  | 1 |  | Pass
Juwi | RM | Meteorological Sensors | Auxiliary Systems | Specific Requirements | 1.10.1 | The equipment should have the capability of recording and storing data for 24 hours using auxiliary DC power. | 1 |  | 1 |  |  |  | min. 2 weeks | Should be priority 1 question |  |  |  | 1 |  | Pass
Juwi | RM | Meteorological Sensors | Auxiliary Systems | Specific Requirements | 1.10.2 | The irradiation measurement equipment should be calibrated by an independent certified third party at least every two years. The calibration must be traceable to international standards. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Should be checked in list of deviations |  |  |  | 1 |  | Open
Juwi | RM | Meteorological Sensors | Auxiliary Systems | Specific Requirements | 1.10.2 | Seven pyranometers shall be placed : three for measuring the horizontal plane irradiation and the others for the in-plane irradiation. | 1 | p383 5.0 Monitoring SLD |  |  | 1 | SLD is not sharp enough presented Hardware concept not readable |  | As in 1.10.2, it is seven pyranometer per system, please clarify the word "per system" | 1.1.1: "100 MWp (DC capacity at Standard Testing Conditions, abbreviated STC … hereinafter called 'the System') " |  |  | 1 |  | Open
Juwi | RM | Meteorological Sensors | Auxiliary Systems | Specific Requirements | 1.10.2 | The pyranometers should conform to the standards of ISO 9060 (SR5: secondary standard) or the WMO classification, and IEC 60904. | 1 |  | 1 |  |  |  |  | Do we need to know some parameter values according to standards mentioned or just a statement of comlience with the standard would be sufficient? | compliance will be necessary, no data due diligence right now. |  |  | 1 |  | Pass
Juwi | RM | Meteorological Sensors | Auxiliary Systems | Specific Requirements | 1.10.3 | Ambient air and the module temperature shall be measured at every 5 installed MWp in conformity with IEC 60751 AA | 1 |  |  |  | 1 | SLD is not sharp enough presented Hardware concept not readable | [5 empty] | 1 |  | Open
Juwi | RM | Site Preparation and site access | Site Preparation and site access | Specific Requirements | 1.11.1 | The Bidder shall provide foundations and structures in accordance with the actual soil conditions. | 1 | p18 / 1.8 | 1 |  |  | tilt 10° - pleas explain with PVSyst analyse with 20° | additionial geo survey and pull-out test Screw piles tilt 10° (!!) |  | refer to Soil study |  |  | 1 |  | Pass
Juwi | RM | Earthworks | Site Preparation and site access | Specific Requirements | 1.12 | Within the plant boundary limits, access roads to all stations shall be suitable for heavy load trucks (axle load: min. 12 tonn). | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | [5 empty] | 1 |  | Open
Juwi | RM | Earthworks | Site Preparation and site access | Specific Requirements | 1.12 | Position and specification of underground cable connections must be documented during installation | 1 |  | 1 |  |  |  |  | Cannot be avaluated at this stage. |  |  |  | 1 |  | Pass
Juwi | RM | Earthworks | Site Preparation and site access | Specific Requirements | 1.12, 1.13.4, 1.7.7 | Cross-sections of foundations for stations shall be provided, including explanation of the foundations laying down, height, penetration, and method of installing foundation posts, mounting fixtures | 1 |  | 1 | [8 empty] | 1 |  | Pass
Juwi | RM | Earthworks | Site Preparation and site access | Design factors to be provided | 1.12 | All earth works required have to be specified and included in the offer | 1 |  |  |  | 1 | Location: Only nice pictures. We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | [5 empty] | 1 |  | Open
Juwi | RM | Earthworks | Site Preparation and site access | Specific Requirements | 1.12 | After completion of construction and all earthworks ground shall be levelled and stabilized. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  | (maintanance, dust) |  |  | 1 |  | Open
Juwi | RM | Mounting | Mounting | Specific Requirements | 1.13.1 | The system is fixed-tilted. Tilt angle is specified. | 1 |  | 1 |  |  | tilt 10° - pleas explain with PVSyst analyse with 20° | [5 empty] | 1 |  | Pass
Juwi | RM | Mounting | Mounting | Specific Requirements | 1.13.3 | Mounting structure is made of durable material, resistant to sandstorms and compatible with the module frame material so as to avoid any adverse electrolytic/galvanic effects. | 1 |  |  |  | 1 | Location: No information in Annexxure4. We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Information about materials to be known before evaluation. | right |  |  | 1 |  | Open
Juwi | RM | Mounting | Mounting | Specific Requirements | 1.13.3 | Mounting system resists high wind speeds (up to 40 m/s) | 1 |  |  |  | 1 | Location: No information in Annexxure4. We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | [5 empty] | 1 |  | Open
Juwi | RM | Mounting | Mounting | Specific Requirements | 1.13.3 | Mounting system resists corrosion (passing the salt spray test IEC 61701, among other verification), | 1 |  |  |  | 1 | Location: No information in Annexxure4. We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Information about materials to be known before evaluation. | right |  |  | 1 |  | Open
Juwi | RM | Mounting | Mounting | Specific Requirements | 1.13.3 | Mounting system resists UV induced degradation | 1 |  |  |  | 1 | Location: No information in Annexxure4. We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | [5 empty] | 1 |  | Open
Juwi | RM | Mounting | Mounting | Specific Requirements | 1.13.5 | All fastening structures must be verified for durability and resistance to environmental degradation for 25 years | 1 |  |  |  | 1 | Location: No information in Annexxure4. We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | What sort of mechanism is required for verification? | Sub structure description / materials double to line 172 - 175 |  |  | 1 |  | Open
Juwi | RM | Mounting | Mounting | Specific Requirements | 1.13.8 | The mounting structures must be earthed | 1 |  |  |  | 1 | [6 empty] | 1 |  | Open
Juwi | RM | Mounting | Mounting | Specific Requirements | 1.13.9 | Specific site conditions have been considered. | 1 |  | 1 |  |  |  |  | Needs to be discussed. | … specific requirements of the soil conditions Static |  |  | 1 |  | Pass
Juwi | RM | Other infrastructure | Auxiliary systems | Design factors to be provided | 1.25.1 | One administration and office building with car port for 10 vehicles shall be provided, with sufficient space for operating personal, control room, security office, regular office rooms for permanent and visiting staff, meeting room, kitchen sanitary systems (toilet, showers separate for male and female), first aid, control room, electrical rooms, etc. The building shall have windows for office rooms and air conditioning system (split units) for all office rooms. | 1 |  | 1 |  |  |  |  | Priority to be discussed |  |  |  | 1 |  | Pass
Juwi | RM | Other infrastructure | Auxiliary systems | Design factors to be provided | 1.25.1 | Warehouse for spare parts and workshop for minor mechanical/electrical works. | 1 |  | 1 | [8 empty] | 1 |  | Pass
Juwi | RM | Other infrastructure | Auxiliary systems | Design factors to be provided | 1.25.1 | Water storage facility for drinking water, sanitary water (sufficient for 1 week) | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | [5 empty] | 1 |  | Open
Juwi | RM | Other infrastructure | Auxiliary systems | Design factors to be provided | 1.25.1 | Service water system sufficiently sized for cleaning cycle of modules | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | [5 empty] | 1 |  | Open
Juwi | RM | Other infrastructure | Auxiliary systems | Design factors to be provided | 1.25.1 | Sewage system including sewage disposal for Construction and O&M phase | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | [5 empty] | 1 |  | Open
Juwi | RM | Other infrastructure | Auxiliary systems | Guarantees | 1.25.4 | All buildings should be designed in accordance with the requirements of the Pakistan Building Code (available at www.pec.org.pk/buildingcode.aspx) and latest Seismic Provisions 2007. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Link to code |  |  |  | 1 |  | Open
Juwi | RM | Other infrastructure | Auxiliary systems | Security Surveillance System | 1.25.5 | The system shall comply with insurance requirements | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | [5 empty] | 1 |  | Open
Juwi | RM | Other infrastructure | Auxiliary systems | Security Surveillance System | 1.25.5 | The Bidder shall provide security personnel for 24 h / 7 days a week for the whole year | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | [5 empty] | 1 |  | Open
Juwi | RM | Other infrastructure | Auxiliary systems | DC Backup System / uninterrupted power supply (UPS) | 1.25.6 | IEC-60051 and IEC-60439 standards apply | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  |  |  | 1 |  | Open
Zte | RM | Supervisory Control and Data Acquisition (SCADA) | SCADA | Specific Requirements | 1.9.1 | Safe and redundant archive for operational data. | 1 | 1.TP, p17 1.TP, p87 annex P005 “ Comprehensive Monitoring” | 1 |  |  | please explain "data processing" on site. Explain redundant archive | Monitoring struckture overview |  |  |  |  | 1 |  | Pass
Zte | RM | Supervisory Control and Data Acquisition (SCADA) | SCADA | Specific Requirements | 1.9.1 | Remote access to all operational data for independent monitoring purposes shall be possible (NTDC requirements) | 1 | 1.TP, p87, p94 P005 | 1 |  |  |  | "5.2.4.4 Relaying Protection Information Management Sub-station " "NTDC relaying protection dispatching information net,…" |  |  |  |  | 1 |  | Pass
Zte | RM | Supervisory Control and Data Acquisition (SCADA) | SCADA | Specific Requirements | 1.9.1 | The system has to provide different access-levels with different access rights allocated. | 1 |  |  |  | 1 | please confirm different levels of "read only", "write", User authority | [5 empty] | 1 |  | Open
Zte | RM | Supervisory Control and Data Acquisition (SCADA) | SCADA | Specific Requirements | 1.9.2 | Control room to remotely monitor and manage the whole system, on a 24 x 7 basis, with the capability of Web-based information sharing | 1 | 1.TP, 5.3.2 1.TP, 7.1 | 1 | [8 empty] | 1 |  | Pass
Zte | RM | Supervisory Control and Data Acquisition (SCADA) | SCADA | Specific Requirements | 1.9.2 | Alarms/alerts and timely notification of key performance indicators | 1 |  | 1 | [8 empty] | 1 |  | Pass
Zte | RM | Supervisory Control and Data Acquisition (SCADA) | SCADA | Specific Requirements | 1.9.2 | Data must be readily available for the fulfilment of all warranties and performance guarantees | 1 |  |  |  | 1 | please describe and confirm |  | Cannot be evaluated at this stage. | statement |  |  | 1 |  | Open
Zte | RM | Supervisory Control and Data Acquisition (SCADA) | SCADA | Specific Requirements | 1.9.2 | Data logging at intervals of not less than one minute, processing, transmission, and back-up | 1 |  |  |  | 1 | please confirm | hint: correct meaning is: no longer interval than 1 minute |  | not more (!) |  |  | 1 |  | Open
Zte | RM | Supervisory Control and Data Acquisition (SCADA) | SCADA | Specific Requirements | 1.9.2 | Separate inverter, zone, and string level (current and voltage) monitoring | 1 |  | 1 | [8 empty] | 1 |  | Pass
Zte | RM | Supervisory Control and Data Acquisition (SCADA) | SCADA | Specific Requirements | 1.9.2 | Back-up power for a minimum of twelve hours | 1 |  |  |  | 1 | please confirm 12 h back-up | [5 empty] | 1 |  | Open
Zte | RM | Supervisory Control and Data Acquisition (SCADA) | SCADA | Specific Requirements | 1.9.2 | Data shall be provided via FTP (Push/Pull) to the Employer | 1 |  |  |  | 1 | please confirm | [5 empty] | 1 |  | Open
Zte | RM | Supervisory Control and Data Acquisition (SCADA) | SCADA | Specific Requirements | 1.9.2 | All communication/data cables outside of buildings must be fiber-optic cables | 1 |  | 1 | [8 empty] | 1 |  | Pass
Zte | RM | Meteorological Sensors | Auxiliary Systems | Specific Requirements | 1.10.1 | Irradiation and temperature measurements are to be recorded at intervals of 15 min or less. | 1 |  |  |  | 1 | "Technical Proposal of 100MW Solar Power Plant.pdf" 5.2.10: more details requiered | [5 empty] | 1 |  | Open
Zte | RM | Meteorological Sensors | Auxiliary Systems | Specific Requirements | 1.10.1 | The equipment should have the capability of recording and storing data for 24 hours using auxiliary DC power. | 1 |  |  |  | 1 | DC control power system back-up 100Ah: pease confirm back-up time |  | Should be priority 1 question |  |  |  | 1 |  | Open
Zte | RM | Meteorological Sensors | Auxiliary Systems | Specific Requirements | 1.10.2 | The irradiation measurement equipment should be calibrated by an independent certified third party at least every two years. The calibration must be traceable to international standards. | 1 |  |  |  | 1 | please confirm |  | Should be checked in list of deviations |  |  |  | 1 |  | Open
Zte | RM | Meteorological Sensors | Auxiliary Systems | Specific Requirements | 1.10.2 | Seven pyranometers shall be placed : three for measuring the horizontal plane irradiation and the others for the in-plane irradiation. | 1 |  |  |  | 1 | please confirm Secondary Standard and 7 Py's as required |  | As in 1.10.2, it is seven pyranometer per system, please clarify the word "per system" | 1.1.1: "100 MWp (DC capacity at Standard Testing Conditions, abbreviated STC … hereinafter called 'the System') " |  |  | 1 |  | Open
Zte | RM | Meteorological Sensors | Auxiliary Systems | Specific Requirements | 1.10.2 | The pyranometers should conform to the standards of ISO 9060 (SR5: secondary standard) or the WMO classification, and IEC 60904. | 1 |  |  |  | 1 | please confirm |  | Do we need to know some parameter values according to standards mentioned or just a statement of comlience with the standard would be sufficient? | compliance will be necessary, no data due diligence right now. |  |  | 1 |  | Open
Zte | RM | Meteorological Sensors | Auxiliary Systems | Specific Requirements | 1.10.3 | Ambient air and the module temperature shall be measured at every 5 installed MWp in conformity with IEC 60751 AA | 1 |  |  |  | 1 | please confirm | [5 empty] | 1 |  | Open
Zte | RM | Site Preparation and site access | Site Preparation and site access | Specific Requirements | 1.11.1 | The Bidder shall provide foundations and structures in accordance with the actual soil conditions. | 1 | 1.TP, p126 P002 | 1 |  |  |  | strip footing in Portland Cement P002: screw pile |  | refer to Soil study |  |  | 1 |  | Pass
Zte | RM | Earthworks | Site Preparation and site access | Specific Requirements | 1.12 | Within the plant boundary limits, access roads to all stations shall be suitable for heavy load trucks (axle load: min. 12 tonn). | 1 | 1.TP, p120 P014 | 1 |  |  | please confirm sutibility for heavy load | access road: 6m wide internal road: 4m wide |  |  |  |  | 1 |  | Pass
Zte | RM | Earthworks | Site Preparation and site access | Specific Requirements | 1.12 | Position and specification of underground cable connections must be documented during installation | 1 |  |  |  | 1 | please confirm delivery with documentation |  | Cannot be avaluated at this stage. |  |  |  | 1 |  | Open
Zte | RM | Earthworks | Site Preparation and site access | Specific Requirements | 1.12, 1.13.4, 1.7.7 | Cross-sections of foundations for stations shall be provided, including explanation of the foundations laying down, height, penetration, and method of installing foundation posts, mounting fixtures | 1 | P002 | 1 | [8 empty] | 1 |  | Pass
Zte | RM | Earthworks | Site Preparation and site access | Design factors to be provided | 1.12 | All earth works required have to be specified and included in the offer | 1 |  |  |  | 1 | burried cable installaton (P015) please describe protection against rodents; please provide description for foundation for MV container | [5 empty] | 1 |  | Open
Zte | RM | Earthworks | Site Preparation and site access | Specific Requirements | 1.12 | After completion of construction and all earthworks ground shall be levelled and stabilized. | 1 |  |  |  | 1 | please confirm leveling because soil stabilizes in the left form after short time | afforesting is described |  | (maintanance, dust) |  |  | 1 |  | Open
Zte | RM | Mounting | Mounting | Specific Requirements | 1.13.1 | The system is fixed-tilted. Tilt angle is specified. | 1 |  | 1 |  |  |  | 27° |  |  |  |  | 1 |  | Pass
Zte | RM | Mounting | Mounting | Specific Requirements | 1.13.3 | Mounting structure is made of durable material, resistant to sandstorms and compatible with the module frame material so as to avoid any adverse electrolytic/galvanic effects. | 1 | 1.TP | 1 |  |  |  |  | Information about materials to be known before evaluation. | right |  |  | 1 |  | Pass
Zte | RM | Mounting | Mounting | Specific Requirements | 1.13.3 | Mounting system resists high wind speeds (up to 40 m/s) | 1 |  | 1 | [8 empty] | 1 |  | Pass
Zte | RM | Mounting | Mounting | Specific Requirements | 1.13.3 | Mounting system resists corrosion (passing the salt spray test IEC 61701, among other verification), | 1 |  | 1 |  |  |  |  | Information about materials to be known before evaluation. | right |  |  | 1 |  | Pass
Zte | RM | Mounting | Mounting | Specific Requirements | 1.13.3 | Mounting system resists UV induced degradation | 1 |  | 1 | [8 empty] | 1 |  | Pass
Zte | RM | Mounting | Mounting | Specific Requirements | 1.13.5 | All fastening structures must be verified for durability and resistance to environmental degradation for 25 years | 1 |  |  |  | 1 | please confirm durability |  | What sort of mechanism is required for verification? | Sub structure description / materials double to line 172 - 175 |  |  | 1 |  | Open
Zte | RM | Mounting | Mounting | Specific Requirements | 1.13.8 | The mounting structures must be earthed | 1 | P012 | 1 | [8 empty] | 1 |  | Pass
Zte | RM | Mounting | Mounting | Specific Requirements | 1.13.9 | Specific site conditions have been considered. | 1 |  | 1 |  |  |  |  | Needs to be discussed. | … specific requirements of the soil conditions Static |  |  | 1 |  | Pass
Zte | RM | Other infrastructure | Auxiliary systems | Design factors to be provided | 1.25.1 | One administration and office building with car port for 10 vehicles shall be provided, with sufficient space for operating personal, control room, security office, regular office rooms for permanent and visiting staff, meeting room, kitchen sanitary systems (toilet, showers separate for male and female), first aid, control room, electrical rooms, etc. The building shall have windows for office rooms and air conditioning system (split units) for all office rooms. | 1 |  | 1 |  |  |  |  | Priority to be discussed |  |  |  | 1 |  | Pass
Zte | RM | Other infrastructure | Auxiliary systems | Design factors to be provided | 1.25.1 | Warehouse for spare parts and workshop for minor mechanical/electrical works. | 1 |  | 1 | [8 empty] | 1 |  | Pass
Zte | RM | Other infrastructure | Auxiliary systems | Design factors to be provided | 1.25.1 | Water storage facility for drinking water, sanitary water (sufficient for 1 week) | 1 |  |  |  | 1 | description is exhaustive, but please confirm cormity with RFP | [5 empty] | 1 |  | Open
Zte | RM | Other infrastructure | Auxiliary systems | Design factors to be provided | 1.25.1 | Service water system sufficiently sized for cleaning cycle of modules | 1 |  | 1 | [8 empty] | 1 |  | Pass
Zte | RM | Other infrastructure | Auxiliary systems | Design factors to be provided | 1.25.1 | Sewage system including sewage disposal for Construction and O&M phase | 1 |  | 1 | [8 empty] | 1 |  | Pass
Zte | RM | Other infrastructure | Auxiliary systems | Guarantees | 1.25.4 | All buildings should be designed in accordance with the requirements of the Pakistan Building Code (available at www.pec.org.pk/buildingcode.aspx) and latest Seismic Provisions 2007. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Link to code |  |  |  | 1 |  | Open
Zte | RM | Other infrastructure | Auxiliary systems | Security Surveillance System | 1.25.5 | The system shall comply with insurance requirements | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | [5 empty] | 1 |  | Open
Zte | RM | Other infrastructure | Auxiliary systems | Security Surveillance System | 1.25.5 | The Bidder shall provide security personnel for 24 h / 7 days a week for the whole year | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | [5 empty] | 1 |  | Open
Zte | RM | Other infrastructure | Auxiliary systems | DC Backup System / uninterrupted power supply (UPS) | 1.25.6 | IEC-60051 and IEC-60439 standards apply | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  |  |  | 1 |  | Open
Tbea | RM | Supervisory Control and Data Acquisition (SCADA) | SCADA | Specific Requirements | 1.9.1 | Safe and redundant archive for operational data. | 1 |  | 1 |  |  | General understanding: expressions like "shall", "has to be", "must be" have the meaning of "will be delivered"? | [5 empty] | 1 |  | Pass
Tbea | RM | Supervisory Control and Data Acquisition (SCADA) | SCADA | Specific Requirements | 1.9.1 | Remote access to all operational data for independent monitoring purposes shall be possible (NTDC requirements) | 1 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | RM | Supervisory Control and Data Acquisition (SCADA) | SCADA | Specific Requirements | 1.9.1 | The system has to provide different access-levels with different access rights allocated. | 1 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | RM | Supervisory Control and Data Acquisition (SCADA) | SCADA | Specific Requirements | 1.9.2 | Control room to remotely monitor and manage the whole system, on a 24 x 7 basis, with the capability of Web-based information sharing | 1 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | RM | Supervisory Control and Data Acquisition (SCADA) | SCADA | Specific Requirements | 1.9.2 | Alarms/alerts and timely notification of key performance indicators | 1 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | RM | Supervisory Control and Data Acquisition (SCADA) | SCADA | Specific Requirements | 1.9.2 | Data must be readily available for the fulfilment of all warranties and performance guarantees | 1 |  | 1 |  |  |  |  | Cannot be evaluated at this stage. | statement |  |  | 1 |  | Pass
Tbea | RM | Supervisory Control and Data Acquisition (SCADA) | SCADA | Specific Requirements | 1.9.2 | Data logging at intervals of not less than one minute, processing, transmission, and back-up | 1 |  |  |  | 1 | Correct meaning was: maximum interval length of 1 minute. Please confirm. |  |  | not more (!) |  |  | 1 |  | Open
Tbea | RM | Supervisory Control and Data Acquisition (SCADA) | SCADA | Specific Requirements | 1.9.2 | Separate inverter, zone, and string level (current and voltage) monitoring | 1 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | RM | Supervisory Control and Data Acquisition (SCADA) | SCADA | Specific Requirements | 1.9.2 | Back-up power for a minimum of twelve hours | 1 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | RM | Supervisory Control and Data Acquisition (SCADA) | SCADA | Specific Requirements | 1.9.2 | Data shall be provided via FTP (Push/Pull) to the Employer | 1 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | RM | Supervisory Control and Data Acquisition (SCADA) | SCADA | Specific Requirements | 1.9.2 | All communication/data cables outside of buildings must be fiber-optic cables | 1 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | RM | Meteorological Sensors | Auxiliary Systems | Specific Requirements | 1.10.1 | Irradiation and temperature measurements are to be recorded at intervals of 15 min or less. | 1 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | RM | Meteorological Sensors | Auxiliary Systems | Specific Requirements | 1.10.1 | The equipment should have the capability of recording and storing data for 24 hours using auxiliary DC power. | 1 |  | 1 |  |  |  |  | Should be priority 1 question |  |  |  | 1 |  | Pass
Tbea | RM | Meteorological Sensors | Auxiliary Systems | Specific Requirements | 1.10.2 | The irradiation measurement equipment should be calibrated by an independent certified third party at least every two years. The calibration must be traceable to international standards. | 1 |  | 1 |  |  |  |  | Should be checked in list of deviations |  |  |  | 1 |  | Pass
Tbea | RM | Meteorological Sensors | Auxiliary Systems | Specific Requirements | 1.10.2 | Seven pyranometers shall be placed : three for measuring the horizontal plane irradiation and the others for the in-plane irradiation. | 1 |  | 1 |  |  |  |  | As in 1.10.2, it is seven pyranometer per system, please clarify the word "per system" | 1.1.1: "100 MWp (DC capacity at Standard Testing Conditions, abbreviated STC … hereinafter called 'the System') " |  |  | 1 |  | Pass
Tbea | RM | Meteorological Sensors | Auxiliary Systems | Specific Requirements | 1.10.2 | The pyranometers should conform to the standards of ISO 9060 (SR5: secondary standard) or the WMO classification, and IEC 60904. | 1 |  | 1 |  |  |  |  | Do we need to know some parameter values according to standards mentioned or just a statement of comlience with the standard would be sufficient? | compliance will be necessary, no data due diligence right now. |  |  | 1 |  | Pass
Tbea | RM | Meteorological Sensors | Auxiliary Systems | Specific Requirements | 1.10.3 | Ambient air and the module temperature shall be measured at every 5 installed MWp in conformity with IEC 60751 AA | 1 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | RM | Site Preparation and site access | Site Preparation and site access | Specific Requirements | 1.11.1 | The Bidder shall provide foundations and structures in accordance with the actual soil conditions. | 1 |  |  |  | 1 | I please describe so far calculations / plannings / uncertainties. Soil study is for information even if professionally executed. |  |  | refer to Soil study |  |  | 1 |  | Open
Tbea | RM | Earthworks | Site Preparation and site access | Specific Requirements | 1.12 | Within the plant boundary limits, access roads to all stations shall be suitable for heavy load trucks (axle load: min. 12 tonn). | 1 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | RM | Earthworks | Site Preparation and site access | Specific Requirements | 1.12 | Position and specification of underground cable connections must be documented during installation | 1 |  | 1 |  |  |  |  | Cannot be avaluated at this stage. |  |  |  | 1 |  | Pass
Tbea | RM | Earthworks | Site Preparation and site access | Specific Requirements | 1.12, 1.13.4, 1.7.7 | Cross-sections of foundations for stations shall be provided, including explanation of the foundations laying down, height, penetration, and method of installing foundation posts, mounting fixtures | 1 |  | 1 |  |  | Stated | TBEA-12 Appedices Structure solution not finalized. Site testings will be executed in advance. Check in detail. |  |  |  |  | 1 |  | Pass
Tbea | RM | Earthworks | Site Preparation and site access | Design factors to be provided | 1.12 | All earth works required have to be specified and included in the offer | 1 |  |  |  | 1 | How about access accross those trenches into rows / where located? What is the idea of the paved station suare? Please describe cross section of internal access roads (line 163) | TBEA-12 Appendices Structure foundaton+earthing Inverter Station foundation MV box foundation Station square Cabel trench (solid box), top cover is 150mm above (!) ground |  |  |  |  | 1 |  | Open
Tbea | RM | Earthworks | Site Preparation and site access | Specific Requirements | 1.12 | After completion of construction and all earthworks ground shall be levelled and stabilized. | 1 |  | 1 | [5 empty] | (maintanance, dust) |  |  | 1 |  | Pass
Tbea | RM | Mounting | Mounting | Specific Requirements | 1.13.1 | The system is fixed-tilted. Tilt angle is specified. | 1 |  | 1 |  |  |  | S.89 29° - 30° south |  |  |  |  | 1 |  | Pass
Tbea | RM | Mounting | Mounting | Specific Requirements | 1.13.3 | Mounting structure is made of durable material, resistant to sandstorms and compatible with the module frame material so as to avoid any adverse electrolytic/galvanic effects. | 1 |  | 1 |  |  |  |  | Information about materials to be known before evaluation. | right |  |  | 1 |  | Pass
Tbea | RM | Mounting | Mounting | Specific Requirements | 1.13.3 | Mounting system resists high wind speeds (up to 40 m/s) | 1 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | RM | Mounting | Mounting | Specific Requirements | 1.13.3 | Mounting system resists corrosion (passing the salt spray test IEC 61701, among other verification), | 1 |  | 1 |  |  |  |  | Information about materials to be known before evaluation. | right |  |  | 1 |  | Pass
Tbea | RM | Mounting | Mounting | Specific Requirements | 1.13.3 | Mounting system resists UV induced degradation | 1 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | RM | Mounting | Mounting | Specific Requirements | 1.13.5 | All fastening structures must be verified for durability and resistance to environmental degradation for 25 years | 1 |  | 1 |  |  | "Applicable construction codes" not mentioned in TBEA-12 / 8… Please add. |  | What sort of mechanism is required for verification? | Sub structure description / materials double to line 172 - 175 |  |  | 1 |  | Pass
Tbea | RM | Mounting | Mounting | Specific Requirements | 1.13.8 | The mounting structures must be earthed | 1 |  |  |  | 1 | We cant find the information in the Bid. Please provide Location TBEA-12/11 is only catodic protection | [5 empty] | 1 |  | Open
Tbea | RM | Mounting | Mounting | Specific Requirements | 1.13.9 | Specific site conditions have been considered. | 1 |  |  |  | 1 | Please confirm that at minimum IEC stadards are fullfilled |  | Needs to be discussed. | … specific requirements of the soil conditions Static |  |  | 1 |  | Open
Tbea | RM | Other infrastructure | Auxiliary systems | Design factors to be provided | 1.25.1 | One administration and office building with car port for 10 vehicles shall be provided, with sufficient space for operating personal, control room, security office, regular office rooms for permanent and visiting staff, meeting room, kitchen sanitary systems (toilet, showers separate for male and female), first aid, control room, electrical rooms, etc. The building shall have windows for office rooms and air conditioning system (split units) for all office rooms. | 1 |  |  |  | 1 |  |  | Priority to be discussed |  |  |  | 1 |  | Open
Tbea | RM | Other infrastructure | Auxiliary systems | Design factors to be provided | 1.25.1 | Warehouse for spare parts and workshop for minor mechanical/electrical works. | 1 |  |  |  | 1 | [6 empty] | 1 |  | Open
Tbea | RM | Other infrastructure | Auxiliary systems | Design factors to be provided | 1.25.1 | Water storage facility for drinking water, sanitary water (sufficient for 1 week) | 1 |  |  |  | 1 | [6 empty] | 1 |  | Open
Tbea | RM | Other infrastructure | Auxiliary systems | Design factors to be provided | 1.25.1 | Service water system sufficiently sized for cleaning cycle of modules | 1 |  |  |  | 1 | [6 empty] | 1 |  | Open
Tbea | RM | Other infrastructure | Auxiliary systems | Design factors to be provided | 1.25.1 | Sewage system including sewage disposal for Construction and O&M phase | 1 |  |  |  | 1 | [6 empty] | 1 |  | Open
Tbea | RM | Other infrastructure | Auxiliary systems | Guarantees | 1.25.4 | All buildings should be designed in accordance with the requirements of the Pakistan Building Code (available at www.pec.org.pk/buildingcode.aspx) and latest Seismic Provisions 2007. | 1 |  |  |  | 1 |  |  | Link to code |  |  |  | 1 |  | Open
Tbea | RM | Other infrastructure | Auxiliary systems | Security Surveillance System | 1.25.5 | The system shall comply with insurance requirements | 1 |  |  |  | 1 | [6 empty] | 1 |  | Open
Tbea | RM | Other infrastructure | Auxiliary systems | Security Surveillance System | 1.25.5 | The Bidder shall provide security personnel for 24 h / 7 days a week for the whole year | 1 |  |  |  | 1 | [6 empty] | 1 |  | Open
Tbea | RM | Other infrastructure | Auxiliary systems | DC Backup System / uninterrupted power supply (UPS) | 1.25.6 | IEC-60051 and IEC-60439 standards apply | 1 |  |  |  | 1 |  | Wording in Bid is still "IEC-51and IEC-439" insted of 60051 / 60439 | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  |  |  | 1 |  | Open
Tbea | MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Bills of Materials, BoMs: (glass, encapsulant, backsheet, ribbon, adhesives, cable, junction box, connector) | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Tbea | MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Maximum rated power | 1 | page 840 | 1 | [8 empty] | 1 |  | Pass
Tbea | MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Rated power tolerance | 1 | page 840 | 1 | [8 empty] | 1 |  | Pass
Tbea | MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Minimum efficiency at 200 W/m² (25°, AM 1.5) | 1 | page 840 | 1 | [8 empty] | 1 |  | Pass
Tbea | MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Materials and workmanship warranty of a minimum of 10 years | 1 | page 840 | 1 | [8 empty] | 1 |  | Pass
Tbea | MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Power warranty/performance guarantee of a minimum of 25 years: the power output should not fall below 90% within 10 years, and below 80% within 25 years; linear warranty mandatory | 1 | page 840 | 1 | [8 empty] | 1 |  | Pass
Tbea | MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Type of cells comprising the module, and number of cells in series | 1 | page 840 | 1 | [5 empty] | manufacturer |  |  | 1 |  | Pass
Tbea | MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Voltage at the maximum power point | 1 | page 840 | 1 | [8 empty] | 1 |  | Pass
Tbea | MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Current at the maximum current point | 1 | page 840 | 1 | [8 empty] | 1 |  | Pass
Tbea | MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Open-circuit voltage | 1 | page 840 | 1 | [8 empty] | 1 |  | Pass
Tbea | MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Short-circuit current | 1 | page 840 | 1 | [8 empty] | 1 |  | Pass
Tbea | MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Maximum system voltage | 1 | page 840 | 1 | [5 empty] | … at SK-II safety class |  |  | 1 |  | Pass
Tbea | MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Operating temperature range and nominal operating cell temperature NOCT | 1 | page 840 | 1 |  |  |  |  | What range is acceptable | There is as small range anyway Will result in the PR losses |  |  | 1 |  | Pass
Tbea | MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Tolerance to wind (maximum load) impact (mechanical load) | 1 | page 840 | 1 | [5 empty] | minimum 2400 Pa |  |  | 1 |  | Pass
Tbea | MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Manufacturers installation guidelines | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Tbea | MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Manufacturers confirmation for the suitability of module for specific weather conditions and the high UV-radiation | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  | especially reliability at high UV irridiance / Product warranty | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Tbea | MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Provide guarantees and data sheets (to be transferred to Employer upon COD) | 1 | page 840 | 1 | [8 empty] | 1 |  | Pass
Tbea | MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Specify number of modules and total MWp to be provided | 1 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Degradation Curve from Manufacturer | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Tbea | MAW | Modules | Modules | Standards (as applicable to crystalline silicion or thin-film) | 1.14.3 | IEC 61215 | 1 |  | 1 |  |  |  |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? | no, just a statement of compliance |  |  | 1 |  | Pass
Tbea | MAW | Modules | Modules | Standards (as applicable to crystalline silicion or thin-film) | 1.14.3 | IEC 61416 | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? | not existing | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Tbea | MAW | Modules | Modules | Standards (as applicable to crystalline silicion or thin-film) | 1.14.3 | IEC 61646 | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? | no, just a statement of compliance | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Tbea | MAW | Modules | Modules | Standards (as applicable to crystalline silicion or thin-film) | 1.14.3 | IEC 61730 | 1 |  | 1 |  |  |  |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? | no, just a statement of compliance |  |  | 1 |  | Pass
Tbea | MAW | Modules | Modules | Standards (as applicable to crystalline silicion or thin-film) | 1.14.3 | IEC 60364-4-41 | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? | no, just a statement of compliance 'protection against electric shock | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Tbea | MAW | Modules | Modules | Standards (as applicable to crystalline silicion or thin-film) | 1.14.3 | IEC 61701 | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? | no, just a statement of compliance | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Tbea | MAW | Modules | Modules | Standards (as applicable to crystalline silicion or thin-film) | 1.14.3 | IEC 60904-1, IEC 60904-3 | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? | no, just a statement of compliance | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Tbea | MAW | Modules | Modules | Pre-shipment quality assurance | 1.14.4 | Pre-shipment flash tested data Quality assurance for PV modules on-site and in laboratory simulator must meet the class AAA requirements of IEC 60904-9. The sun simulator must be calibrated with a reference cell, which itself was calibrated by a member of the WPVS scheme, with a maximum uncertainty of Isc of 1%. unique barcode (SNr) and labelled performance headlines (P(mpp), I(sc), U(oc), I(mpp), U(mpp) maximum current, maximum voltage Positive power sorting | 1 | page 93 |  |  | 1 |  |  | Cannot be evaluated at this stage. | compliance necessary | C |  | 1 |  | Open
Tbea | MAW | Modules | Modules | Pre-shipment quality assurance | 1.14.4 | All modules must undergo Electroluminiscense (EL) inspection with a resolution of minimum 4 MPixel prior to shipment. | 1 | page 93 |  |  | 1 |  |  | Cannot be evaluated at this stage. | compliance necessary | C |  | 1 |  | Open
Tbea | MAW | Modules | Modules | Pre-shipment quality assurance | 1.14.4 | A sufficient EVA cross linking has to be verified per production line through a gel content test supervised by an accredited (IEC 17025 or national pendant) independent certified module testing agency. | 1 | page 93 |  |  | 1 |  |  | Cannot be evaluated at this stage. | compliance necessary | C |  | 1 |  | Open
Tbea | MAW | Modules | Modules | Quality assurance on site | 1.14.5 | The modules shall undergo an incoming inspection at arrival on construction site. | 1 | page 93 |  |  | 1 |  |  | Cannot be evaluated at this stage. | stated and accepted | C |  | 1 |  | Open
Tbea | MAW | Modules | Due Diligence | Quality Assurance | 1.14.6 | The bidder will bear the cost of the Quality assurance for PV modules on-site and in laboratory to be carried out by the Employer through an independent technical consultant up to 150,000 USD. | 1 | page 93 | 1 | [8 empty] | 1 |  | Pass
Tbea | MAW | Modules | Modules | Pre-shipment quality assurance | 1.14.7 | Warranties and evidence shall be given by the bidder that their selected modules have been tested for susceptibility to Potential Induced Degradation (PID). | 1 | page 93 |  |  | 1 | Unclear: We do not understand your proposal, please detail your proposal. Especially confirm that you are compliant with our requested criteria. |  |  |  | C |  | 1 |  | Open
Tbea | MAW | Modules | Credentials | Project references | 1.14.8 | To show the proven technology a minimum of 500MW of proposed product type series must be in operation and reference projects shall be named. | 1 | page 458 |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | many plants with 10-50MWp were realized, but with same proven technology? | Related to project references |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Tbea | MAW | DC Cables | DC Cables | Specific Requirements | 1.15.1 | Are Ohmic losses less than 1% at full power? | 1 | page 858 |  |  | 1 |  |  |  | DC+AC losses < 2% | C |  | 1 |  | Open
Tbea | MAW | DC Cables | DC Cables | Design factors to be provided | 1.15.2 | String cable shall be of the following type: single conductor type, copper, 1000 V / Class II (according to protection class II / 1000V, IEC 61140, single core cable, tinned copper conductor, XLPE Insulation, double EVA jacket (resistant to heat and cold, resistant to ozone, UV, oil and chemicals), Temperature: 90 º C (Temperature Max. Allowable: 120 º C), Halogen free | 1 |  |  |  | 1 |  |  | It should be in accordance with the inverter values. | possibly 1500V for such system design | C |  | 1 |  | Open
Tbea | MAW | DC Cables | DC Cables | Design factors to be provided | 1.15.2 | Connectors of Modules and string cables shall be connected of self-locking type, have IP65 rating and shall be from same manufacturer and type | 1 |  |  |  | 1 | Unclear: We do not understand your proposal, please detail your proposal. Especially confirm that you are compliant with our requested criteria. |  |  |  | C |  | 1 |  | Open
Tbea | MAW | DC Cables | DC Cables | Design factors to be provided | 1.15.2 | The DC main (downstream of combiner box) wiring harness shall have the quality: Aluminum / Copper / 1000 V / Class II | 1 |  |  |  | 1 |  |  | It should be in accordance with the inverter values. | possibly 1500V for such system design | C |  | 1 |  | Open
Tbea | MAW | DC Cables | DC Cables | Design factors to be provided | 1.15.2 | Balance of electrical potential | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Need to be disscussed | equipotential bonding earthing mesh | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Tbea | MAW | DC Cables | DC Cables | Design factors to be provided | 1.15.2 | Installation to be verified by measurement-protocols | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Cannot be evaluated at this stage. | blanc protocol | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Tbea | MAW | DC Cables | DC Cables | Design factors to be provided | 1.15.2 | Clear and systematic labelling required | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Tbea | MAW | DC Cables | DC Cables | Design factors to be provided | 1.15.2 | Lifetime of 30 years is assured | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | What proof is required. | Life time test of nonmetal materials IEC 60811-408:2012 / (DIN EN 60811-408; VDE 0473-811-408:2012-12) 30 y assurance never seen until today | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Tbea | MAW | DC Cables | DC Cables | Design factors to be provided | 1.15.2 | Sizing of cables shall be specified according to the number of modules and strings per array | 1 |  | 1 | [5 empty] | voltage drop calculation |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | 1 |  | Pass
Tbea | MAW | DC Cables | DC Cables | Standards | 1.15.3 | IEC 60364-1 | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | 1 |  | Open
Tbea | MAW | DC Connectors | DC Connectors | Standards | 1.16.2 | EN 50521 | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? | PV Connectors no, just a statement of compliance |  |  | 1 |  | Open
Tbea | MAW | DC Connectors | DC Connectors | Standards | 1.16.2 | IEC 60512 | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? | Connectors E-Systems no, just a statement of compliance |  |  | 1 |  | Open
Tbea | MAW | DC Junction Box | DC Junction Box | Design factors to be provided | 1.17.1 | At least IP54 | 1 |  | 1 |  |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  | DC Junction box is applicable in what conditions? | depending on DC Design |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | 1 |  | Pass
Tbea | MAW | DC Junction Box | DC Junction Box | Design factors to be provided | 1.17.1 | DC fuses shall permit up to maximum 1000 V (or 1500V if designed). String box design, including all operating elements shall satisfy safety requirements | 1 |  | 1 |  |  |  |  | Will inverter voltage(1500V) effect the maximum voltage(1000V)? | depends on spec of inverter. |  |  | 1 |  | Pass
Tbea | MAW | DC Junction Box | DC Junction Box | Design factors to be provided | 1.17.1 | Monitored input-couples | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | Monitoring on string level? |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Tbea | MAW | DC Junction Box | DC Junction Box | Design factors to be provided | 1.17.1 | Class 2 DC surge arrestor | 1 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | MAW | DC Junction Box | DC Junction Box | Design factors to be provided | 1.17.1 | Dust and heat protection | 1 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | MAW | DC Junction Box | DC Junction Box | Specifications | 1.17.2 | Current monitoring | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | Monitoring on string level? |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Tbea | MAW | DC Junction Box | DC Junction Box | Specifications | 1.17.2 | Touch-safe protective cover | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Tbea | MAW | DC Junction Box | DC Junction Box | Specifications | 1.17.2, 1.17.1 | Monitoring interface for SCADA | 1 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | MAW | DC Junction Box | DC Junction Box | Standards | 1.17.3 | EN 61000-6 | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? | EMV no, just a statement of compliance |  |  | 1 |  | Open
Tbea | MAW | DC Junction Box | DC Junction Box | Standards | 1.17.3 | EN 60439-1 | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? | arcing fault / Störlichtbogen Verhalten no, just a statement of compliance |  |  | 1 |  | Open
Tbea | MAW | DC Junction Box | DC Junction Box | Standards | 1.17.3 | EN 50178 | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? | High currat devices no, just a statement of compliance |  |  | 1 |  | Open
Tbea | MAW | Inverters | Warranty | Warranty option | 1.18.1 | The Bidder shall arrange a full-service package for the selected inverters for a product warranty period of 5 years, with an option to cover additional 20 years including provisions for any necessary replacements including O&M service plan guaranteeing 99% availability. | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | Klaus? |  |  |  | Unclear: We do not understand your proposal, please detail your proposal. Especially confirm that you are compliant with our requested criteria. | 1 |  | Open
Tbea | MAW | Inverters | Inverters | Strategic Reason for Inverter Selection | 1.18.2 | Balance of System (BOS) costs of inverter and labour | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  | financial bid | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Tbea | MAW | Inverters | Inverters | Strategic Reason for Inverter Selection | 1.18.2 | Dust and heat protection | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  | derating? | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Tbea | MAW | Inverters | Inverters | Strategic Reason for Inverter Selection | 1.18.2 | Timely and effective monitoring at a granular/zoomed-in level | 1 |  |  |  | 1 |  |  |  |  | C | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | 1 |  | Open
Tbea | MAW | Inverters | Inverters | Strategic Reason for Inverter Selection | 1.18.2 | Available uptime | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us | [5 empty] | 1 |  | Open
Tbea | MAW | Inverters | Inverters | Strategic Reason for Inverter Selection | 1.18.2 | Concept of protection against overload, short-circuit, grid-failure, internal failure, over-temperature (de-rating), surge protection | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Its too general, needs to be reviewed. | failure codes and consquences (automatic/manual restart, throw away safety devices) | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Tbea | MAW | Inverters | O&M | Guarantees | 1.18.2 | For central inverters concept: the bidder shall ensure with an undertaking from the manufacturer that the concerned skilled staff will be made available at the site within 24 hours of reporting the defect to the manufacturer. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | Klaus? |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Tbea | MAW | Inverters | Inverters | Functionalities | 1.18.3 | Maximum Power Point Tracking (MPPT) and string/sub-array management | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Tbea | MAW | Inverters | Inverters | Functionalities | 1.18.3 | Matching grid voltage and frequency at point-of-coupling | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Tbea | MAW | Inverters | Inverters | Functionalities | 1.18.3 | Anti-islanding protection | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Tbea | MAW | Inverters | Inverters | Functionalities | 1.18.3 | Voltage regulation through reactive power support: remotely set point control for voltage stability | 1 |  | 1 |  |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  | 8.2 needs to ensure these questions are answered in the bids. |  |  |  | 1 |  | Pass
Tbea | MAW | Inverters | Inverters | Functionalities | 1.18.3 | Frequency regulation | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | 8.2 needs to ensure these questions are answered in the bids. |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Tbea | MAW | Inverters | Inverters | Functionalities | 1.18.3 | Voltage and frequency fault ride-through: no disconnection of the connection through voltage dip and change of active power generation, feed-in of reactive power during the fault for voltage stabilisation | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | 8.2 needs to ensure these questions are answered in the bids. |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Tbea | MAW | Inverters | Inverters | Functionalities | 1.18.3 | Limitation of voltage fluctuation due to switching operations and long-term flicker | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | 8.2 needs to ensure these questions are answered in the bids. |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Tbea | MAW | Inverters | Inverters | Functionalities | 1.18.3 | Limitation of short-circuit current | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | 8.2 needs to ensure these questions are answered in the bids. |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Tbea | MAW | Inverters | Inverters | Functionalities | 1.18.3 | Limitation of steady-stage voltage changes to 2% of the nominal value | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Tbea | MAW | Inverters | Inverters | Functionalities | 1.18.3 | Limitation of current harmonics and higher frequency components up to 9 kHz | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Tbea | MAW | Inverters | Inverters | Functionalities | 1.18.3 | Active power control reduction: remotely set point of control in case of network congestions or risk of system collapse, if deemed necessary | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | 8.2 needs to ensure these questions are answered in the bids. |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Tbea | MAW | Inverters | Monitoring | Functionalities | 1.18.3 | Advanced communication, with intelligent alerts/warnings, to the SCADA server | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Tbea | MAW | Inverters | Inverters | Specific Requirements | 1.18.6 | Specifications of table in Schedule C shall be met | 1 |  | 1 |  |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  | Link to table |  |  |  | 1 |  | Pass
Tbea | MAW | Inverters | Inverters | Design factors to be provided | 1.18.7 | Input voltage range (The voltage window for MPP tracking shall accommodate the expected degradation of the modules.) | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Tbea | MAW | Inverters | Inverters | Design factors to be provided | 1.18.7 | PV array configuration options: positive ground, negative ground | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Tbea | MAW | Inverters | Inverters | Design factors to be provided | 1.18.7 | Integrated transformer/transformerless / Outside Dry Type Transformer | 1 |  | 1 |  |  |  | transformerless |  |  |  |  | 1 |  | Pass
Tbea | MAW | Inverters | Inverters | Design factors to be provided | 1.18.7 | Peak efficiency/ Weighted efficiency | 1 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | MAW | Inverters | Inverters | Design factors to be provided | 1.18.7 | Nominal power | 1 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | MAW | Inverters | Inverters | Design factors to be provided | 1.18.7 | Nominal output voltage | 1 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | MAW | Inverters | Inverters | Design factors to be provided | 1.18.7 | Output voltage range | 1 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | MAW | Inverters | Inverters | Design factors to be provided | 1.18.7 | Maximum output current | 1 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | MAW | Inverters | Inverters | Design factors to be provided | 1.18.7 | Nominal output frequency, 3-phase | 1 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | MAW | Inverters | Inverters | Design factors to be provided | 1.18.7 | Operating temperature range | 1 |  | 1 |  |  |  |  | What is the acceptable range? | 60°C Derating? |  |  | 1 |  | Pass
Tbea | MAW | Inverters | Inverters | Design factors to be provided | 1.18.7 | Cooling method | 1 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | MAW | Inverters | Inverters | Design factors to be provided | 1.18.7 | Detection of insulation faults | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | [5 empty] | 1 |  | Open
Tbea | MAW | Inverters | Inverters | Design factors to be provided | 1.18.7 | Protection rating: NEMA 3R, IP54/IP55/IP60 | 1 |  | 1 |  |  | Unclear: We do not understand your proposal, please detail your proposal. Especially confirm that you are compliant with our requested criteria. | IP54 |  |  |  |  | 1 |  | Pass
Tbea | MAW | Inverters | Inverters | Standards | 1.18.8 | IEEE 1547 | 1 |  | 1 |  |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? | no, just a statement of compliance Interconnecting Distributed Resources |  |  | 1 |  | Pass
Tbea | MAW | Inverters | Inverters | Standards | 1.18.8 | TUV, VDE, or equivalent certification of passing the relevant standards | 1 |  | 1 |  |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | [5 empty] | 1 |  | Pass
Tbea | MAW | Inverters | Inverters | Manufacturers confirmation | 1.18.9 | The Bidder shall deliver a manufacturer's confirmation in his Bid for the suitability of the inverter for the specific weather conditions applicable in Bahawalpur Pakistan. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Tbea | MAW | Inverters | Credentials | Project references | 1.18.10 | A minimum of 100 MWp of similar product/type must be in operation and reference projects shall be named. | 1 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | MAW | Inverters | Inverters | Quality Assurance | 1.18.11 | Check of protection against overload, short-circuit, grid-failure, internal failure, over-temperature (de-rating), surge protection, detection of insulation faults of AC Cables. Bidder shall firmly specify the manufacturer, types and length of cables to be installed | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | shall? | 8.2 needs to ensure these questions are answered in the bids. |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Tbea | MAW | Inverters | Inverters | Quality Assurance | 1.18.11 | Test run in the field for maximum and EU-efficiency of all Inverters | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | shall? | 8.2 needs to ensure these questions are answered in the bids. |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Tbea | MAW | Inverters | Inverters | Quality Assurance | 1.18.11 | Test run and check of MPP tracking of all inverters | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | shall? | 8.2 needs to ensure these questions are answered in the bids. |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Tbea | MAW | Inverters | Inverters | Quality Assurance | 1.18.11 | The Bidder shall deliver detailed protocols of performance test run (warm power test) for every single inverter | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | shall? | Cannot be evaluated at this stage |  | C |  | 1 |  | Open
Tbea | MAW | Inverters | Inverters | Quality Assurance | 1.18.11 | After commissioning, 1 of 10 inverters will be measured on site (power curve and efficiency) by an approved independent technical consultant on behalf of the Employer. The on-site measurements shall be accepted by the Bidder as average values for all inverters | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  | Cannot be evaluated at this stage | compliance! | C |  | 1 |  | Open
Tbea | MAW | Inverters | Due diligence | Quality Assurance | 1.18.12 | The Bidder accepts that the cost of the Quality assurance for Inverters to be carried by the Employer through an independent technical consultant shall be taken over by the successful bidder up to an amount of 100,000 USD. | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  |  |  | C |  | 1 |  | Open
Zte | MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Bills of Materials, BoMs: (glass, encapsulant, backsheet, ribbon, adhesives, cable, junction box, connector) | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Zte | MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Maximum rated power | 1 | \3-Response to Section 2\2-Schedules to Bid\Schedule F - Specific Operation Plant and Equipment Detail\3-Data Sheets, Instructions, Manuals\Module | 1 |  |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  |  |  |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | 1 |  | Pass
Zte | MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Rated power tolerance | 1 | \3-Response to Section 2\2-Schedules to Bid\Schedule F - Specific Operation Plant and Equipment Detail\3-Data Sheets, Instructions, Manuals\Module | 1 |  |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  |  |  |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | 1 |  | Pass
Zte | MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Minimum efficiency at 200 W/m² (25°, AM 1.5) | 1 | \3-Response to Section 2\2-Schedules to Bid\Schedule F - Specific Operation Plant and Equipment Detail\3-Data Sheets, Instructions, Manuals\Module | 1 |  |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | [5 empty] | 1 |  | Pass
Zte | MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Materials and workmanship warranty of a minimum of 10 years | 1 | \3-Response to Section 2\2-Schedules to Bid\Schedule F - Specific Operation Plant and Equipment Detail\3-Data Sheets, Instructions, Manuals\Module | 1 |  |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | [5 empty] | 1 |  | Pass
Zte | MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Power warranty/performance guarantee of a minimum of 25 years: the power output should not fall below 90% within 10 years, and below 80% within 25 years; linear warranty mandatory | 1 | \3-Response to Section 2\2-Schedules to Bid\Schedule F - Specific Operation Plant and Equipment Detail\3-Data Sheets, Instructions, Manuals\Module | 1 |  |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | [5 empty] | 1 |  | Pass
Zte | MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Type of cells comprising the module, and number of cells in series | 1 | \3-Response to Section 2\2-Schedules to Bid\Schedule F - Specific Operation Plant and Equipment Detail\3-Data Sheets, Instructions, Manuals\Module | 1 |  |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  |  | manufacturer |  |  | 1 |  | Pass
Zte | MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Voltage at the maximum power point | 1 | \3-Response to Section 2\2-Schedules to Bid\Schedule F - Specific Operation Plant and Equipment Detail\3-Data Sheets, Instructions, Manuals\Module | 1 |  |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | [5 empty] | 1 |  | Pass
Zte | MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Current at the maximum current point | 1 | \3-Response to Section 2\2-Schedules to Bid\Schedule F - Specific Operation Plant and Equipment Detail\3-Data Sheets, Instructions, Manuals\Module | 1 |  |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | [5 empty] | 1 |  | Pass
Zte | MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Open-circuit voltage | 1 | \3-Response to Section 2\2-Schedules to Bid\Schedule F - Specific Operation Plant and Equipment Detail\3-Data Sheets, Instructions, Manuals\Module | 1 |  |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | [5 empty] | 1 |  | Pass
Zte | MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Short-circuit current | 1 | \3-Response to Section 2\2-Schedules to Bid\Schedule F - Specific Operation Plant and Equipment Detail\3-Data Sheets, Instructions, Manuals\Module | 1 |  |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | [5 empty] | 1 |  | Pass
Zte | MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Maximum system voltage | 1 | \3-Response to Section 2\2-Schedules to Bid\Schedule F - Specific Operation Plant and Equipment Detail\3-Data Sheets, Instructions, Manuals\Module | 1 | [5 empty] | … at SK-II safety class |  |  | 1 |  | Pass
Zte | MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Operating temperature range and nominal operating cell temperature NOCT | 1 | \3-Response to Section 2\2-Schedules to Bid\Schedule F - Specific Operation Plant and Equipment Detail\3-Data Sheets, Instructions, Manuals\Module | 1 |  |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  | What range is acceptable | There is as small range anyway Will result in the PR losses |  |  | 1 |  | Pass
Zte | MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Tolerance to wind (maximum load) impact (mechanical load) | 1 | \3-Response to Section 2\2-Schedules to Bid\Schedule F - Specific Operation Plant and Equipment Detail\3-Data Sheets, Instructions, Manuals\Module | 1 |  |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  |  | minimum 2400 Pa |  |  | 1 |  | Pass
Zte | MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Manufacturers installation guidelines | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | only LDK, not Suntech |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Zte | MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Manufacturers confirmation for the suitability of module for specific weather conditions and the high UV-radiation | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  | especially reliability at high UV irridiance / Product warranty | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Zte | MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Provide guarantees and data sheets (to be transferred to Employer upon COD) | 1 | \3-Response to Section 2\2-Schedules to Bid\Schedule F - Specific Operation Plant and Equipment Detail\3-Data Sheets, Instructions, Manuals\Module | 1 | [8 empty] | 1 |  | Pass
Zte | MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Specify number of modules and total MWp to be provided | 1 |  | 1 | [8 empty] | 1 |  | Pass
Zte | MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Degradation Curve from Manufacturer | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Zte | MAW | Modules | Modules | Standards (as applicable to crystalline silicion or thin-film) | 1.14.3 | IEC 61215 | 1 | \3-Response to Section 2\2-Schedules to Bid\Schedule F - Specific Operation Plant and Equipment Detail\3-Data Sheets, Instructions, Manuals\Module |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | Suntech: ok, LDK: missing | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? | no, just a statement of compliance | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Zte | MAW | Modules | Modules | Standards (as applicable to crystalline silicion or thin-film) | 1.14.3 | IEC 61416 | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? | not existing | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Zte | MAW | Modules | Modules | Standards (as applicable to crystalline silicion or thin-film) | 1.14.3 | IEC 61646 | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? | no, just a statement of compliance | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Zte | MAW | Modules | Modules | Standards (as applicable to crystalline silicion or thin-film) | 1.14.3 | IEC 61730 | 1 |  | 1 |  |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? | no, just a statement of compliance |  |  | 1 |  | Pass
Zte | MAW | Modules | Modules | Standards (as applicable to crystalline silicion or thin-film) | 1.14.3 | IEC 60364-4-41 | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? | no, just a statement of compliance 'protection against electric shock | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Zte | MAW | Modules | Modules | Standards (as applicable to crystalline silicion or thin-film) | 1.14.3 | IEC 61701 | 1 | \3-Response to Section 2\2-Schedules to Bid\Schedule F - Specific Operation Plant and Equipment Detail\3-Data Sheets, Instructions, Manuals\Module | 1 |  |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? | no, just a statement of compliance |  |  | 1 |  | Pass
Zte | MAW | Modules | Modules | Standards (as applicable to crystalline silicion or thin-film) | 1.14.3 | IEC 60904-1, IEC 60904-3 | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? | no, just a statement of compliance | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Zte | MAW | Modules | Modules | Pre-shipment quality assurance | 1.14.4 | Pre-shipment flash tested data Quality assurance for PV modules on-site and in laboratory simulator must meet the class AAA requirements of IEC 60904-9. The sun simulator must be calibrated with a reference cell, which itself was calibrated by a member of the WPVS scheme, with a maximum uncertainty of Isc of 1%. unique barcode (SNr) and labelled performance headlines (P(mpp), I(sc), U(oc), I(mpp), U(mpp) maximum current, maximum voltage Positive power sorting | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Cannot be evaluated at this stage. | compliance necessary | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Zte | MAW | Modules | Modules | Pre-shipment quality assurance | 1.14.4 | All modules must undergo Electroluminiscense (EL) inspection with a resolution of minimum 4 MPixel prior to shipment. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Cannot be evaluated at this stage. | compliance necessary | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Zte | MAW | Modules | Modules | Pre-shipment quality assurance | 1.14.4 | A sufficient EVA cross linking has to be verified per production line through a gel content test supervised by an accredited (IEC 17025 or national pendant) independent certified module testing agency. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Cannot be evaluated at this stage. | compliance necessary | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Zte | MAW | Modules | Modules | Quality assurance on site | 1.14.5 | The modules shall undergo an incoming inspection at arrival on construction site. | 1 |  |  |  | 1 |  |  | Cannot be evaluated at this stage. | stated and accepted | C |  | 1 |  | Open
Zte | MAW | Modules | Due Diligence | Quality Assurance | 1.14.6 | The bidder will bear the cost of the Quality assurance for PV modules on-site and in laboratory to be carried out by the Employer through an independent technical consultant up to 150,000 USD. | 1 |  |  |  | 1 |  |  |  |  | C |  | 1 |  | Open
Zte | MAW | Modules | Modules | Pre-shipment quality assurance | 1.14.7 | Warranties and evidence shall be given by the bidder that their selected modules have been tested for susceptibility to Potential Induced Degradation (PID). | 1 |  | 1 |  |  |  | LDK and Suntech |  |  |  |  | 1 |  | Pass
Zte | MAW | Modules | Credentials | Project references | 1.14.8 | To show the proven technology a minimum of 500MW of proposed product type series must be in operation and reference projects shall be named. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Related to project references |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Zte | MAW | DC Cables | DC Cables | Specific Requirements | 1.15.1 | Are Ohmic losses less than 1% at full power? | 1 |  | 1 | [5 empty] | DC+AC losses < 2% |  |  | 1 |  | Pass
Zte | MAW | DC Cables | DC Cables | Design factors to be provided | 1.15.2 | String cable shall be of the following type: single conductor type, copper, 1000 V / Class II (according to protection class II / 1000V, IEC 61140, single core cable, tinned copper conductor, XLPE Insulation, double EVA jacket (resistant to heat and cold, resistant to ozone, UV, oil and chemicals), Temperature: 90 º C (Temperature Max. Allowable: 120 º C), Halogen free | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | It should be in accordance with the inverter values. | possibly 1500V for such system design | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Zte | MAW | DC Cables | DC Cables | Design factors to be provided | 1.15.2 | Connectors of Modules and string cables shall be connected of self-locking type, have IP65 rating and shall be from same manufacturer and type | 1 |  | 1 |  |  |  | MC4 |  |  |  |  | 1 |  | Pass
Zte | MAW | DC Cables | DC Cables | Design factors to be provided | 1.15.2 | The DC main (downstream of combiner box) wiring harness shall have the quality: Aluminum / Copper / 1000 V / Class II | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | It should be in accordance with the inverter values. | possibly 1500V for such system design | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Zte | MAW | DC Cables | DC Cables | Design factors to be provided | 1.15.2 | Balance of electrical potential | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Need to be disscussed | equipotential bonding earthing mesh | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Zte | MAW | DC Cables | DC Cables | Design factors to be provided | 1.15.2 | Installation to be verified by measurement-protocols | 1 |  |  |  | 1 |  |  | Cannot be evaluated at this stage. | blanc protocol | C |  | 1 |  | Open
Zte | MAW | DC Cables | DC Cables | Design factors to be provided | 1.15.2 | Clear and systematic labelling required | 1 |  |  |  | 1 |  |  |  |  | C |  | 1 |  | Open
Zte | MAW | DC Cables | DC Cables | Design factors to be provided | 1.15.2 | Lifetime of 30 years is assured | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | What proof is required. | Life time test of nonmetal materials IEC 60811-408:2012 / (DIN EN 60811-408; VDE 0473-811-408:2012-12) 30 y assurance never seen until today | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Zte | MAW | DC Cables | DC Cables | Design factors to be provided | 1.15.2 | Sizing of cables shall be specified according to the number of modules and strings per array | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  | voltage drop calculation | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Zte | MAW | DC Cables | DC Cables | Standards | 1.15.3 | IEC 60364-1 | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Zte | MAW | DC Connectors | DC Connectors | Standards | 1.16.2 | EN 50521 | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? | PV Connectors no, just a statement of compliance | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Zte | MAW | DC Connectors | DC Connectors | Standards | 1.16.2 | IEC 60512 | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? | Connectors E-Systems no, just a statement of compliance | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Zte | MAW | DC Junction Box | DC Junction Box | Design factors to be provided | 1.17.1 | At least IP54 | 1 | \3-Response to Section 2\2-Schedules to Bid\Schedule A - Specific Works Data\1. Technical Proposal | 1 |  |  |  | IP65 | DC Junction box is applicable in what conditions? | depending on DC Design |  |  | 1 |  | Pass
Zte | MAW | DC Junction Box | DC Junction Box | Design factors to be provided | 1.17.1 | DC fuses shall permit up to maximum 1000 V (or 1500V if designed). String box design, including all operating elements shall satisfy safety requirements | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | equipotential connection? | Will inverter voltage(1500V) effect the maximum voltage(1000V)? | depends on spec of inverter. | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Zte | MAW | DC Junction Box | DC Junction Box | Design factors to be provided | 1.17.1 | Monitored input-couples | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Zte | MAW | DC Junction Box | DC Junction Box | Design factors to be provided | 1.17.1 | Class 2 DC surge arrestor | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Zte | MAW | DC Junction Box | DC Junction Box | Design factors to be provided | 1.17.1 | Dust and heat protection | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Zte | MAW | DC Junction Box | DC Junction Box | Specifications | 1.17.2 | Current monitoring | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Zte | MAW | DC Junction Box | DC Junction Box | Specifications | 1.17.2 | Touch-safe protective cover | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | no cover, just small boxes |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Zte | MAW | DC Junction Box | DC Junction Box | Specifications | 1.17.2, 1.17.1 | Monitoring interface for SCADA | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Zte | MAW | DC Junction Box | DC Junction Box | Standards | 1.17.3 | EN 61000-6 | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? | EMV no, just a statement of compliance | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Zte | MAW | DC Junction Box | DC Junction Box | Standards | 1.17.3 | EN 60439-1 | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? | arcing fault / Störlichtbogen Verhalten no, just a statement of compliance | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Zte | MAW | DC Junction Box | DC Junction Box | Standards | 1.17.3 | EN 50178 | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? | High currat devices no, just a statement of compliance | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Zte | MAW | Inverters | Warranty | Warranty option | 1.18.1 | The Bidder shall arrange a full-service package for the selected inverters for a product warranty period of 5 years, with an option to cover additional 20 years including provisions for any necessary replacements including O&M service plan guaranteeing 99% availability. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Zte | MAW | Inverters | Inverters | Strategic Reason for Inverter Selection | 1.18.2 | Balance of System (BOS) costs of inverter and labour | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  | financial bid | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Zte | MAW | Inverters | Inverters | Strategic Reason for Inverter Selection | 1.18.2 | Dust and heat protection | 1 | \3-Response to Section 2\2-Schedules to Bid\Schedule F - Specific Operation Plant and Equipment Detail\3-Data Sheets, Instructions, Manuals\Inverter\Datasheet |  |  | 1 |  |  |  | derating? |  |  | 1 |  | Open
Zte | MAW | Inverters | Inverters | Strategic Reason for Inverter Selection | 1.18.2 | Timely and effective monitoring at a granular/zoomed-in level | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Zte | MAW | Inverters | Inverters | Strategic Reason for Inverter Selection | 1.18.2 | Available uptime | 1 | \3-Response to Section 2\2-Schedules to Bid\Schedule F - Specific Operation Plant and Equipment Detail\3-Data Sheets, Instructions, Manuals\Inverter\Datasheet |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Zte | MAW | Inverters | Inverters | Strategic Reason for Inverter Selection | 1.18.2 | Concept of protection against overload, short-circuit, grid-failure, internal failure, over-temperature (de-rating), surge protection | 1 | \3-Response to Section 2\2-Schedules to Bid\Schedule F - Specific Operation Plant and Equipment Detail\3-Data Sheets, Instructions, Manuals\Inverter\Datasheet |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | partly confirmed | Its too general, needs to be reviewed. | failure codes and consquences (automatic/manual restart, throw away safety devices) | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Zte | MAW | Inverters | O&M | Guarantees | 1.18.2 | For central inverters concept: the bidder shall ensure with an undertaking from the manufacturer that the concerned skilled staff will be made available at the site within 24 hours of reporting the defect to the manufacturer. | 1 | \3-Response to Section 2\2-Schedules to Bid\Schedule F - Specific Operation Plant and Equipment Detail\3-Data Sheets, Instructions, Manuals\Inverter\Datasheet |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Zte | MAW | Inverters | Inverters | Functionalities | 1.18.3 | Maximum Power Point Tracking (MPPT) and string/sub-array management | 1 | \3-Response to Section 2\2-Schedules to Bid\Schedule F - Specific Operation Plant and Equipment Detail\3-Data Sheets, Instructions, Manuals\Inverter\Datasheet |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Zte | MAW | Inverters | Inverters | Functionalities | 1.18.3 | Matching grid voltage and frequency at point-of-coupling | 1 | \3-Response to Section 2\2-Schedules to Bid\Schedule F - Specific Operation Plant and Equipment Detail\3-Data Sheets, Instructions, Manuals\Inverter\Datasheet |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Zte | MAW | Inverters | Inverters | Functionalities | 1.18.3 | Anti-islanding protection | 1 | \3-Response to Section 2\2-Schedules to Bid\Schedule F - Specific Operation Plant and Equipment Detail\3-Data Sheets, Instructions, Manuals\Inverter\Datasheet | 1 | [8 empty] | 1 |  | Pass
Zte | MAW | Inverters | Inverters | Functionalities | 1.18.3 | Voltage regulation through reactive power support: remotely set point control for voltage stability | 1 | \3-Response to Section 2\2-Schedules to Bid\Schedule F - Specific Operation Plant and Equipment Detail\3-Data Sheets, Instructions, Manuals\Inverter\Datasheet | 1 |  |  |  |  | 8.2 needs to ensure these questions are answered in the bids. |  |  |  | 1 |  | Pass
Zte | MAW | Inverters | Inverters | Functionalities | 1.18.3 | Frequency regulation | 1 | \3-Response to Section 2\2-Schedules to Bid\Schedule F - Specific Operation Plant and Equipment Detail\3-Data Sheets, Instructions, Manuals\Inverter\Datasheet |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | 8.2 needs to ensure these questions are answered in the bids. |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Zte | MAW | Inverters | Inverters | Functionalities | 1.18.3 | Voltage and frequency fault ride-through: no disconnection of the connection through voltage dip and change of active power generation, feed-in of reactive power during the fault for voltage stabilisation | 1 | \3-Response to Section 2\2-Schedules to Bid\Schedule F - Specific Operation Plant and Equipment Detail\3-Data Sheets, Instructions, Manuals\Inverter\Datasheet | 1 |  |  |  |  | 8.2 needs to ensure these questions are answered in the bids. |  |  |  | 1 |  | Pass
Zte | MAW | Inverters | Inverters | Functionalities | 1.18.3 | Limitation of voltage fluctuation due to switching operations and long-term flicker | 1 | \3-Response to Section 2\2-Schedules to Bid\Schedule F - Specific Operation Plant and Equipment Detail\3-Data Sheets, Instructions, Manuals\Inverter\Datasheet |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | 8.2 needs to ensure these questions are answered in the bids. |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Zte | MAW | Inverters | Inverters | Functionalities | 1.18.3 | Limitation of short-circuit current | 1 | \3-Response to Section 2\2-Schedules to Bid\Schedule F - Specific Operation Plant and Equipment Detail\3-Data Sheets, Instructions, Manuals\Inverter\Datasheet |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | 8.2 needs to ensure these questions are answered in the bids. |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Zte | MAW | Inverters | Inverters | Functionalities | 1.18.3 | Limitation of steady-stage voltage changes to 2% of the nominal value | 1 | \3-Response to Section 2\2-Schedules to Bid\Schedule F - Specific Operation Plant and Equipment Detail\3-Data Sheets, Instructions, Manuals\Inverter\Datasheet |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Zte | MAW | Inverters | Inverters | Functionalities | 1.18.3 | Limitation of current harmonics and higher frequency components up to 9 kHz | 1 | \3-Response to Section 2\2-Schedules to Bid\Schedule F - Specific Operation Plant and Equipment Detail\3-Data Sheets, Instructions, Manuals\Inverter\Datasheet |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Zte | MAW | Inverters | Inverters | Functionalities | 1.18.3 | Active power control reduction: remotely set point of control in case of network congestions or risk of system collapse, if deemed necessary | 1 | \3-Response to Section 2\2-Schedules to Bid\Schedule F - Specific Operation Plant and Equipment Detail\3-Data Sheets, Instructions, Manuals\Inverter\Datasheet |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | 8.2 needs to ensure these questions are answered in the bids. |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Zte | MAW | Inverters | Monitoring | Functionalities | 1.18.3 | Advanced communication, with intelligent alerts/warnings, to the SCADA server | 1 | \3-Response to Section 2\2-Schedules to Bid\Schedule F - Specific Operation Plant and Equipment Detail\3-Data Sheets, Instructions, Manuals\Inverter\Datasheet |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Zte | MAW | Inverters | Inverters | Specific Requirements | 1.18.6 | Specifications of table in Schedule C shall be met | 1 | \3-Response to Section 2\2-Schedules to Bid\Schedule F - Specific Operation Plant and Equipment Detail\3-Data Sheets, Instructions, Manuals\Inverter\Datasheet | 1 |  |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  | Link to table |  |  |  | 1 |  | Pass
Zte | MAW | Inverters | Inverters | Design factors to be provided | 1.18.7 | Input voltage range (The voltage window for MPP tracking shall accommodate the expected degradation of the modules.) | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Zte | MAW | Inverters | Inverters | Design factors to be provided | 1.18.7 | PV array configuration options: positive ground, negative ground | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Zte | MAW | Inverters | Inverters | Design factors to be provided | 1.18.7 | Integrated transformer/transformerless / Outside Dry Type Transformer | 1 |  | 1 |  |  |  | no transformer |  |  |  |  | 1 |  | Pass
Zte | MAW | Inverters | Inverters | Design factors to be provided | 1.18.7 | Peak efficiency/ Weighted efficiency | 1 |  | 1 | [8 empty] | 1 |  | Pass
Zte | MAW | Inverters | Inverters | Design factors to be provided | 1.18.7 | Nominal power | 1 |  | 1 | [8 empty] | 1 |  | Pass
Zte | MAW | Inverters | Inverters | Design factors to be provided | 1.18.7 | Nominal output voltage | 1 |  | 1 | [8 empty] | 1 |  | Pass
Zte | MAW | Inverters | Inverters | Design factors to be provided | 1.18.7 | Output voltage range | 1 |  | 1 | [8 empty] | 1 |  | Pass
Zte | MAW | Inverters | Inverters | Design factors to be provided | 1.18.7 | Maximum output current | 1 |  | 1 | [8 empty] | 1 |  | Pass
Zte | MAW | Inverters | Inverters | Design factors to be provided | 1.18.7 | Nominal output frequency, 3-phase | 1 |  | 1 | [8 empty] | 1 |  | Pass
Zte | MAW | Inverters | Inverters | Design factors to be provided | 1.18.7 | Operating temperature range | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | -25℃~+55℃(>45℃derating) | What is the acceptable range? | 60°C Derating? | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Zte | MAW | Inverters | Inverters | Design factors to be provided | 1.18.7 | Cooling method | 1 |  | 1 |  |  | Unclear: We do not understand your proposal, please detail your proposal. Especially confirm that you are compliant with our requested criteria. | [5 empty] | 1 |  | Pass
Zte | MAW | Inverters | Inverters | Design factors to be provided | 1.18.7 | Detection of insulation faults | 1 |  | 1 |  |  | Unclear: We do not understand your proposal, please detail your proposal. Especially confirm that you are compliant with our requested criteria. | [5 empty] | 1 |  | Pass
Zte | MAW | Inverters | Inverters | Design factors to be provided | 1.18.7 | Protection rating: NEMA 3R, IP54/IP55/IP60 | 1 |  | 1 |  |  | Unclear: We do not understand your proposal, please detail your proposal. Especially confirm that you are compliant with our requested criteria. | IP54 |  |  |  |  | 1 |  | Pass
Zte | MAW | Inverters | Inverters | Standards | 1.18.8 | IEEE 1547 | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? | no, just a statement of compliance Interconnecting Distributed Resources | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Zte | MAW | Inverters | Inverters | Standards | 1.18.8 | TUV, VDE, or equivalent certification of passing the relevant standards | 1 | \3-Response to Section 2\2-Schedules to Bid\Schedule F - Specific Operation Plant and Equipment Detail\3-Data Sheets, Instructions, Manuals\Inverter\Datasheet | 1 | [7 empty] | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | 1 |  | Pass
Zte | MAW | Inverters | Inverters | Manufacturers confirmation | 1.18.9 | The Bidder shall deliver a manufacturer's confirmation in his Bid for the suitability of the inverter for the specific weather conditions applicable in Bahawalpur Pakistan. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Zte | MAW | Inverters | Credentials | Project references | 1.18.10 | A minimum of 100 MWp of similar product/type must be in operation and reference projects shall be named. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Zte | MAW | Inverters | Inverters | Quality Assurance | 1.18.11 | Check of protection against overload, short-circuit, grid-failure, internal failure, over-temperature (de-rating), surge protection, detection of insulation faults of AC Cables. Bidder shall firmly specify the manufacturer, types and length of cables to be installed | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | 8.2 needs to ensure these questions are answered in the bids. |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Zte | MAW | Inverters | Inverters | Quality Assurance | 1.18.11 | Test run in the field for maximum and EU-efficiency of all Inverters | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | 8.2 needs to ensure these questions are answered in the bids. |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Zte | MAW | Inverters | Inverters | Quality Assurance | 1.18.11 | Test run and check of MPP tracking of all inverters | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | 8.2 needs to ensure these questions are answered in the bids. |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Zte | MAW | Inverters | Inverters | Quality Assurance | 1.18.11 | The Bidder shall deliver detailed protocols of performance test run (warm power test) for every single inverter | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Cannot be evaluated at this stage |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Zte | MAW | Inverters | Inverters | Quality Assurance | 1.18.11 | After commissioning, 1 of 10 inverters will be measured on site (power curve and efficiency) by an approved independent technical consultant on behalf of the Employer. The on-site measurements shall be accepted by the Bidder as average values for all inverters | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Cannot be evaluated at this stage | compliance! | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Zte | MAW | Inverters | Due diligence | Quality Assurance | 1.18.12 | The Bidder accepts that the cost of the Quality assurance for Inverters to be carried by the Employer through an independent technical consultant shall be taken over by the successful bidder up to an amount of 100,000 USD. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Juwi | MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Bills of Materials, BoMs: (glass, encapsulant, backsheet, ribbon, adhesives, cable, junction box, connector) | 1 |  | 1 | [7 empty] | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | 1 |  | Pass
Juwi | MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Maximum rated power | 1 | page 59 | 1 | [8 empty] | 1 |  | Pass
Juwi | MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Rated power tolerance | 1 | page 59 | 1 | [8 empty] | 1 |  | Pass
Juwi | MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Minimum efficiency at 200 W/m² (25°, AM 1.5) | 1 | page 59 | 1 | [8 empty] | 1 |  | Pass
Juwi | MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Materials and workmanship warranty of a minimum of 10 years | 1 | page 59 | 1 |  |  |  | 12 years |  |  |  |  | 1 |  | Pass
Juwi | MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Power warranty/performance guarantee of a minimum of 25 years: the power output should not fall below 90% within 10 years, and below 80% within 25 years; linear warranty mandatory | 1 | page 59 | 1 | [7 empty] | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | 1 |  | Pass
Juwi | MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Type of cells comprising the module, and number of cells in series | 1 | page 59 | 1 | [5 empty] | manufacturer |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | 1 |  | Pass
Juwi | MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Voltage at the maximum power point | 1 | page 59 | 1 | [7 empty] | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | 1 |  | Pass
Juwi | MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Current at the maximum current point | 1 | page 59 | 1 | [8 empty] | 1 |  | Pass
Juwi | MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Open-circuit voltage | 1 | page 59 | 1 | [7 empty] | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | 1 |  | Pass
Juwi | MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Short-circuit current | 1 | page 59 | 1 | [7 empty] | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | 1 |  | Pass
Juwi | MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Maximum system voltage | 1 | page 59 | 1 | [5 empty] | … at SK-II safety class |  |  | 1 |  | Pass
Juwi | MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Operating temperature range and nominal operating cell temperature NOCT | 1 | page 59 | 1 |  |  |  |  | What range is acceptable | There is as small range anyway Will result in the PR losses |  |  | 1 |  | Pass
Juwi | MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Tolerance to wind (maximum load) impact (mechanical load) | 1 | page 59 | 1 | [5 empty] | minimum 2400 Pa |  |  | 1 |  | Pass
Juwi | MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Manufacturers installation guidelines | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Juwi | MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Manufacturers confirmation for the suitability of module for specific weather conditions and the high UV-radiation | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  | especially reliability at high UV irridiance / Product warranty | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Juwi | MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Provide guarantees and data sheets (to be transferred to Employer upon COD) | 1 |  | 1 | [8 empty] | 1 |  | Pass
Juwi | MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Specify number of modules and total MWp to be provided | 1 | page 392 | 1 | [8 empty] | 1 |  | Pass
Juwi | MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Degradation Curve from Manufacturer | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Juwi | MAW | Modules | Modules | Standards (as applicable to crystalline silicion or thin-film) | 1.14.3 | IEC 61215 | 1 | page 59 | 1 |  |  |  |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? | no, just a statement of compliance |  |  | 1 |  | Pass
Juwi | MAW | Modules | Modules | Standards (as applicable to crystalline silicion or thin-film) | 1.14.3 | IEC 61416 | 1 | page 59 |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? | not existing | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Juwi | MAW | Modules | Modules | Standards (as applicable to crystalline silicion or thin-film) | 1.14.3 | IEC 61646 | 1 | page 59 |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? | no, just a statement of compliance | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Juwi | MAW | Modules | Modules | Standards (as applicable to crystalline silicion or thin-film) | 1.14.3 | IEC 61730 | 1 | page 59 | 1 |  |  |  |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? | no, just a statement of compliance |  |  | 1 |  | Pass
Juwi | MAW | Modules | Modules | Standards (as applicable to crystalline silicion or thin-film) | 1.14.3 | IEC 60364-4-41 | 1 | page 59 |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? | no, just a statement of compliance 'protection against electric shock | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Juwi | MAW | Modules | Modules | Standards (as applicable to crystalline silicion or thin-film) | 1.14.3 | IEC 61701 | 1 | page 59 |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? | no, just a statement of compliance | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Juwi | MAW | Modules | Modules | Standards (as applicable to crystalline silicion or thin-film) | 1.14.3 | IEC 60904-1, IEC 60904-3 | 1 | page 59 |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? | no, just a statement of compliance | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Juwi | MAW | Modules | Modules | Pre-shipment quality assurance | 1.14.4 | Pre-shipment flash tested data Quality assurance for PV modules on-site and in laboratory simulator must meet the class AAA requirements of IEC 60904-9. The sun simulator must be calibrated with a reference cell, which itself was calibrated by a member of the WPVS scheme, with a maximum uncertainty of Isc of 1%. unique barcode (SNr) and labelled performance headlines (P(mpp), I(sc), U(oc), I(mpp), U(mpp) maximum current, maximum voltage Positive power sorting | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Cannot be evaluated at this stage. | compliance necessary | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Juwi | MAW | Modules | Modules | Pre-shipment quality assurance | 1.14.4 | All modules must undergo Electroluminiscense (EL) inspection with a resolution of minimum 4 MPixel prior to shipment. | 1 | page 89 | 1 |  |  |  |  | Cannot be evaluated at this stage. | compliance necessary |  |  | 1 |  | Pass
Juwi | MAW | Modules | Modules | Pre-shipment quality assurance | 1.14.4 | A sufficient EVA cross linking has to be verified per production line through a gel content test supervised by an accredited (IEC 17025 or national pendant) independent certified module testing agency. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Cannot be evaluated at this stage. | compliance necessary | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Juwi | MAW | Modules | Modules | Quality assurance on site | 1.14.5 | The modules shall undergo an incoming inspection at arrival on construction site. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Cannot be evaluated at this stage. | stated and accepted | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Juwi | MAW | Modules | Due Diligence | Quality Assurance | 1.14.6 | The bidder will bear the cost of the Quality assurance for PV modules on-site and in laboratory to be carried out by the Employer through an independent technical consultant up to 150,000 USD. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Juwi | MAW | Modules | Modules | Pre-shipment quality assurance | 1.14.7 | Warranties and evidence shall be given by the bidder that their selected modules have been tested for susceptibility to Potential Induced Degradation (PID). | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | Additional Tests available |  |  | C |  | 1 |  | Open
Juwi | MAW | Modules | Credentials | Project references | 1.14.8 | To show the proven technology a minimum of 500MW of proposed product type series must be in operation and reference projects shall be named. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Related to project references |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Juwi | MAW | DC Connectors | DC Connectors | Standards | 1.16.2 | EN 50521 | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? | PV Connectors no, just a statement of compliance | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Juwi | MAW | DC Connectors | DC Connectors | Standards | 1.16.2 | IEC 60512 | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? | Connectors E-Systems no, just a statement of compliance | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Juwi | MAW | Inverters | Warranty | Warranty option | 1.18.1 | The Bidder shall arrange a full-service package for the selected inverters for a product warranty period of 5 years, with an option to cover additional 20 years including provisions for any necessary replacements including O&M service plan guaranteeing 99% availability. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Juwi | MAW | Inverters | Inverters | Strategic Reason for Inverter Selection | 1.18.2 | Balance of System (BOS) costs of inverter and labour | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  | financial bid | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Juwi | MAW | Inverters | Inverters | Strategic Reason for Inverter Selection | 1.18.2 | Dust and heat protection | 1 |  | 1 | [5 empty] | derating? |  |  | 1 |  | Pass
Juwi | MAW | Inverters | Inverters | Strategic Reason for Inverter Selection | 1.18.2 | Timely and effective monitoring at a granular/zoomed-in level | 1 |  | 1 | [8 empty] | 1 |  | Pass
Juwi | MAW | Inverters | Inverters | Strategic Reason for Inverter Selection | 1.18.2 | Available uptime | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Juwi | MAW | Inverters | Inverters | Strategic Reason for Inverter Selection | 1.18.2 | Concept of protection against overload, short-circuit, grid-failure, internal failure, over-temperature (de-rating), surge protection | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Its too general, needs to be reviewed. | failure codes and consquences (automatic/manual restart, throw away safety devices) | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Juwi | MAW | Inverters | O&M | Guarantees | 1.18.2 | For central inverters concept: the bidder shall ensure with an undertaking from the manufacturer that the concerned skilled staff will be made available at the site within 24 hours of reporting the defect to the manufacturer. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Juwi | MAW | Inverters | Inverters | Functionalities | 1.18.3 | Maximum Power Point Tracking (MPPT) and string/sub-array management | 1 | page 291 | 1 | [8 empty] | 1 |  | Pass
Juwi | MAW | Inverters | Inverters | Functionalities | 1.18.3 | Matching grid voltage and frequency at point-of-coupling | 1 | page 291 | 1 | [8 empty] | 1 |  | Pass
Juwi | MAW | Inverters | Inverters | Functionalities | 1.18.3 | Anti-islanding protection | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Juwi | MAW | Inverters | Inverters | Functionalities | 1.18.3 | Voltage regulation through reactive power support: remotely set point control for voltage stability | 1 | page 291 | 1 |  |  |  |  | 8.2 needs to ensure these questions are answered in the bids. |  |  |  | 1 |  | Pass
Juwi | MAW | Inverters | Inverters | Functionalities | 1.18.3 | Frequency regulation | 1 | page 291 | 1 |  |  |  |  | 8.2 needs to ensure these questions are answered in the bids. |  |  |  | 1 |  | Pass
Juwi | MAW | Inverters | Inverters | Functionalities | 1.18.3 | Voltage and frequency fault ride-through: no disconnection of the connection through voltage dip and change of active power generation, feed-in of reactive power during the fault for voltage stabilisation | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | 8.2 needs to ensure these questions are answered in the bids. |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Juwi | MAW | Inverters | Inverters | Functionalities | 1.18.3 | Limitation of voltage fluctuation due to switching operations and long-term flicker | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | 8.2 needs to ensure these questions are answered in the bids. |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Juwi | MAW | Inverters | Inverters | Functionalities | 1.18.3 | Limitation of short-circuit current | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | 8.2 needs to ensure these questions are answered in the bids. |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Juwi | MAW | Inverters | Inverters | Functionalities | 1.18.3 | Limitation of steady-stage voltage changes to 2% of the nominal value | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Juwi | MAW | Inverters | Inverters | Functionalities | 1.18.3 | Limitation of current harmonics and higher frequency components up to 9 kHz | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Juwi | MAW | Inverters | Inverters | Functionalities | 1.18.3 | Active power control reduction: remotely set point of control in case of network congestions or risk of system collapse, if deemed necessary | 1 | page 291 | 1 |  |  |  |  | 8.2 needs to ensure these questions are answered in the bids. |  |  |  | 1 |  | Pass
Juwi | MAW | Inverters | Monitoring | Functionalities | 1.18.3 | Advanced communication, with intelligent alerts/warnings, to the SCADA server | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Juwi | MAW | Inverters | Inverters | Specific Requirements | 1.18.6 | Specifications of table in Schedule C shall be met | 1 | page 291 | 1 |  |  |  |  | Link to table |  |  |  | 1 |  | Pass
Juwi | MAW | Inverters | Inverters | Design factors to be provided | 1.18.7 | Input voltage range (The voltage window for MPP tracking shall accommodate the expected degradation of the modules.) | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Juwi | MAW | Inverters | Inverters | Design factors to be provided | 1.18.7 | PV array configuration options: positive ground, negative ground | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Juwi | MAW | Inverters | Inverters | Design factors to be provided | 1.18.7 | Integrated transformer/transformerless / Outside Dry Type Transformer | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Juwi | MAW | Inverters | Inverters | Design factors to be provided | 1.18.7 | Peak efficiency/ Weighted efficiency | 1 | page 291 | 1 | [8 empty] | 1 |  | Pass
Juwi | MAW | Inverters | Inverters | Design factors to be provided | 1.18.7 | Nominal power | 1 | page 291 | 1 | [8 empty] | 1 |  | Pass
Juwi | MAW | Inverters | Inverters | Design factors to be provided | 1.18.7 | Nominal output voltage | 1 | page 291 | 1 | [8 empty] | 1 |  | Pass
Juwi | MAW | Inverters | Inverters | Design factors to be provided | 1.18.7 | Output voltage range | 1 | page 291 | 1 | [8 empty] | 1 |  | Pass
Juwi | MAW | Inverters | Inverters | Design factors to be provided | 1.18.7 | Maximum output current | 1 | page 291 | 1 | [8 empty] | 1 |  | Pass
Juwi | MAW | Inverters | Inverters | Design factors to be provided | 1.18.7 | Nominal output frequency, 3-phase | 1 | page 291 | 1 | [8 empty] | 1 |  | Pass
Juwi | MAW | Inverters | Inverters | Design factors to be provided | 1.18.7 | Operating temperature range | 1 | page 291 | 1 |  |  |  |  | What is the acceptable range? | 60°C Derating? |  |  | 1 |  | Pass
Juwi | MAW | Inverters | Inverters | Design factors to be provided | 1.18.7 | Cooling method | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Juwi | MAW | Inverters | Inverters | Design factors to be provided | 1.18.7 | Detection of insulation faults | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Juwi | MAW | Inverters | Inverters | Design factors to be provided | 1.18.7 | Protection rating: NEMA 3R, IP54/IP55/IP60 | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Juwi | MAW | Inverters | Inverters | Standards | 1.18.8 | IEEE 1547 | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? | no, just a statement of compliance Interconnecting Distributed Resources | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Juwi | MAW | Inverters | Inverters | Standards | 1.18.8 | TUV, VDE, or equivalent certification of passing the relevant standards | 1 | page 291 | 1 | [8 empty] | 1 |  | Pass
Juwi | MAW | Inverters | Inverters | Manufacturers confirmation | 1.18.9 | The Bidder shall deliver a manufacturer's confirmation in his Bid for the suitability of the inverter for the specific weather conditions applicable in Bahawalpur Pakistan. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Juwi | MAW | Inverters | Credentials | Project references | 1.18.10 | A minimum of 100 MWp of similar product/type must be in operation and reference projects shall be named. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Juwi | MAW | Inverters | Inverters | Quality Assurance | 1.18.11 | Check of protection against overload, short-circuit, grid-failure, internal failure, over-temperature (de-rating), surge protection, detection of insulation faults of AC Cables. Bidder shall firmly specify the manufacturer, types and length of cables to be installed | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | 8.2 needs to ensure these questions are answered in the bids. |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Juwi | MAW | Inverters | Inverters | Quality Assurance | 1.18.11 | Test run in the field for maximum and EU-efficiency of all Inverters | 1 |  |  |  | 1 |  |  | 8.2 needs to ensure these questions are answered in the bids. |  | C |  | 1 |  | Open
Juwi | MAW | Inverters | Inverters | Quality Assurance | 1.18.11 | Test run and check of MPP tracking of all inverters | 1 |  |  |  | 1 |  |  | 8.2 needs to ensure these questions are answered in the bids. |  | C |  | 1 |  | Open
Juwi | MAW | Inverters | Inverters | Quality Assurance | 1.18.11 | The Bidder shall deliver detailed protocols of performance test run (warm power test) for every single inverter | 1 |  |  |  | 1 |  |  | Cannot be evaluated at this stage |  | C |  | 1 |  | Open
Juwi | MAW | Inverters | Inverters | Quality Assurance | 1.18.11 | After commissioning, 1 of 10 inverters will be measured on site (power curve and efficiency) by an approved independent technical consultant on behalf of the Employer. The on-site measurements shall be accepted by the Bidder as average values for all inverters | 1 |  |  |  | 1 |  |  | Cannot be evaluated at this stage | compliance! | C |  | 1 |  | Open
Juwi | MAW | Inverters | Due diligence | Quality Assurance | 1.18.12 | The Bidder accepts that the cost of the Quality assurance for Inverters to be carried by the Employer through an independent technical consultant shall be taken over by the successful bidder up to an amount of 100,000 USD. | 1 |  |  |  | 1 |  |  |  |  | C |  | 1 |  | Open
Juwi | JBU MAW | DC Cables | DC Cables | Specific Requirements | 1.15.1 | Are Ohmic losses less than 1% at full power? Fail | 1 |  |  | 1 |  | Are Ohmic losses less than 1% at full power? | page 392, 2%; page 395, 1,4% |  | DC+AC losses < 2% | U |  | 1 |  | Fail
Juwi | JBU MAW | DC Cables | DC Cables | Design factors to be provided | 1.15.2 | String cable shall be of the following type: single conductor type, copper, 1000 V / Class II (according to protection class II / 1000V, IEC 61140, single core cable, tinned copper conductor, XLPE Insulation, double EVA jacket (resistant to heat and cold, resistant to ozone, UV, oil and chemicals), Temperature: 90 º C (Temperature Max. Allowable: 120 º C), Halogen free | 1 |  | 1 |  |  |  |  | It should be in accordance with the inverter values. | possibly 1500V for such system design |  |  | 1 |  | Pass
Juwi | JBU MAW | DC Cables | DC Cables | Design factors to be provided | 1.15.2 | Connectors of Modules and string cables shall be connected of self-locking type, have IP65 rating and shall be from same manufacturer and type | 1 |  | 1 | [8 empty] | 1 |  | Pass
Juwi | JBU MAW | DC Cables | DC Cables | Design factors to be provided | 1.15.2 | The DC main (downstream of combiner box) wiring harness shall have the quality: Aluminum / Copper / 1000 V / Class II | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | It should be in accordance with the inverter values. | possibly 1500V for such system design | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Juwi | JBU MAW | DC Cables | DC Cables | Design factors to be provided | 1.15.2 | Balance of electrical potential | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Need to be disscussed | equipotential bonding earthing mesh | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Juwi | JBU MAW | DC Cables | DC Cables | Design factors to be provided | 1.15.2 | Installation to be verified by measurement-protocols | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Cannot be evaluated at this stage. | blanc protocol | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Juwi | JBU MAW | DC Cables | DC Cables | Design factors to be provided | 1.15.2 | Clear and systematic labelling required | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Juwi | JBU MAW | DC Cables | DC Cables | Design factors to be provided | 1.15.2 | Lifetime of 30 years is assured | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | What proof is required. | Life time test of nonmetal materials IEC 60811-408:2012 / (DIN EN 60811-408; VDE 0473-811-408:2012-12) 30 y assurance never seen until today | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Juwi | JBU MAW | DC Cables | DC Cables | Design factors to be provided | 1.15.2 | Sizing of cables shall be specified according to the number of modules and strings per array | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  | voltage drop calculation | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Juwi | JBU MAW | DC Cables | DC Cables | Standards | 1.15.3 | IEC 60364-1 | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Juwi | JBU MAW | DC Junction Box | DC Junction Box | Design factors to be provided | 1.17.1 | At least IP54 | 1 |  | 1 |  |  |  |  | DC Junction box is applicable in what conditions? | depending on DC Design |  |  | 1 |  | Pass
Juwi | JBU MAW | DC Junction Box | DC Junction Box | Design factors to be provided | 1.17.1 | DC fuses shall permit up to maximum 1000 V (or 1500V if designed). String box design, including all operating elements shall satisfy safety requirements | 1 |  | 1 |  |  |  |  | Will inverter voltage(1500V) effect the maximum voltage(1000V)? | depends on spec of inverter. |  |  | 1 |  | Pass
Juwi | JBU MAW | DC Junction Box | DC Junction Box | Design factors to be provided | 1.17.1 | Monitored input-couples | 1 |  | 1 | [8 empty] | 1 |  | Pass
Juwi | JBU MAW | DC Junction Box | DC Junction Box | Design factors to be provided | 1.17.1 | Class 2 DC surge arrestor | 1 |  | 1 | [8 empty] | 1 |  | Pass
Juwi | JBU MAW | DC Junction Box | DC Junction Box | Design factors to be provided | 1.17.1 | Dust and heat protection | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Juwi | JBU MAW | DC Junction Box | DC Junction Box | Specifications | 1.17.2 | Current monitoring | 1 |  | 1 | [8 empty] | 1 |  | Pass
Juwi | JBU MAW | DC Junction Box | DC Junction Box | Specifications | 1.17.2 | Touch-safe protective cover | 1 |  |  |  | 1 |  |  |  |  | C |  | 1 |  | Open
Juwi | JBU MAW | DC Junction Box | DC Junction Box | Specifications | 1.17.2, 1.17.1 | Monitoring interface for SCADA | 1 |  | 1 | [8 empty] | 1 |  | Pass
Juwi | JBU MAW | DC Junction Box | DC Junction Box | Standards | 1.17.3 | EN 61000-6 | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? | EMV no, just a statement of compliance | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Juwi | JBU MAW | DC Junction Box | DC Junction Box | Standards | 1.17.3 | EN 60439-1 | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? | arcing fault / Störlichtbogen Verhalten no, just a statement of compliance | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Juwi | JBU MAW | DC Junction Box | DC Junction Box | Standards | 1.17.3 | EN 50178 | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? | High currat devices no, just a statement of compliance | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Chint | MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Bills of Materials, BoMs: (glass, encapsulant, backsheet, ribbon, adhesives, cable, junction box, connector) | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Chint | MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Maximum rated power | 1 | Doc 3&4 page 109 | 1 | [8 empty] | 1 |  | Pass
Chint | MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Rated power tolerance | 1 | Doc 3&4 page 109 | 1 | [8 empty] | 1 |  | Pass
Chint | MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Minimum efficiency at 200 W/m² (25°, AM 1.5) | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Chint | MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Materials and workmanship warranty of a minimum of 10 years | 1 | Doc 3&4 page 109 |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | Extended product warranty --> materials and workmanship? |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Chint | MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Power warranty/performance guarantee of a minimum of 25 years: the power output should not fall below 90% within 10 years, and below 80% within 25 years; linear warranty mandatory | 1 | Doc 3&4 page 109 | 1 | [8 empty] | 1 |  | Pass
Chint | MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Type of cells comprising the module, and number of cells in series | 1 | Doc 3&4 page 109 | 1 | [5 empty] | manufacturer |  |  | 1 |  | Pass
Chint | MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Voltage at the maximum power point | 1 | Doc 3&4 page 109 | 1 | [8 empty] | 1 |  | Pass
Chint | MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Current at the maximum current point | 1 | Doc 3&4 page 109 | 1 | [8 empty] | 1 |  | Pass
Chint | MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Open-circuit voltage | 1 | Doc 3&4 page 109 | 1 | [8 empty] | 1 |  | Pass
Chint | MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Short-circuit current | 1 | Doc 3&4 page 109 | 1 | [8 empty] | 1 |  | Pass
Chint | MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Maximum system voltage | 1 | Doc 3&4 page 109 | 1 | [5 empty] | … at SK-II safety class |  |  | 1 |  | Pass
Chint | MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Operating temperature range and nominal operating cell temperature NOCT | 1 | Doc 3&4 page 109 | 1 |  |  |  |  | What range is acceptable | There is as small range anyway Will result in the PR losses |  |  | 1 |  | Pass
Chint | MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Tolerance to wind (maximum load) impact (mechanical load) | 1 | Doc 3&4 page 109 | 1 | [5 empty] | minimum 2400 Pa |  |  | 1 |  | Pass
Chint | MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Manufacturers installation guidelines | 1 |  |  |  | 1 |  |  |  |  | C |  | 1 |  | Open
Chint | MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Manufacturers confirmation for the suitability of module for specific weather conditions and the high UV-radiation | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  | especially reliability at high UV irridiance / Product warranty | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Chint | MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Provide guarantees and data sheets (to be transferred to Employer upon COD) | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Chint | MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Specify number of modules and total MWp to be provided | 1 | Doc 3&4 page 447 |  |  | 1 |  | Pvsyst: 100MWp + 800kWp (403200 modules) |  |  | U |  | 1 |  | Open
Chint | MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Degradation Curve from Manufacturer | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Chint | MAW | Modules | Modules | Standards (as applicable to crystalline silicion or thin-film) | 1.14.3 | IEC 61215 | 1 | doc 1&2 page 198, 209 | 1 |  |  |  |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? | no, just a statement of compliance |  |  | 1 |  | Pass
Chint | MAW | Modules | Modules | Standards (as applicable to crystalline silicion or thin-film) | 1.14.3 | IEC 61416 | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? | not existing | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Chint | MAW | Modules | Modules | Standards (as applicable to crystalline silicion or thin-film) | 1.14.3 | IEC 61646 | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? | no, just a statement of compliance | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Chint | MAW | Modules | Modules | Standards (as applicable to crystalline silicion or thin-film) | 1.14.3 | IEC 61730 | 1 |  | 1 |  |  |  |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? | no, just a statement of compliance |  |  | 1 |  | Pass
Chint | MAW | Modules | Modules | Standards (as applicable to crystalline silicion or thin-film) | 1.14.3 | IEC 60364-4-41 | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? | no, just a statement of compliance 'protection against electric shock | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Chint | MAW | Modules | Modules | Standards (as applicable to crystalline silicion or thin-film) | 1.14.3 | IEC 61701 | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? | no, just a statement of compliance | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Chint | MAW | Modules | Modules | Standards (as applicable to crystalline silicion or thin-film) | 1.14.3 | IEC 60904-1, IEC 60904-3 | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? | no, just a statement of compliance | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Chint | MAW | Modules | Modules | Pre-shipment quality assurance | 1.14.4 | Pre-shipment flash tested data Quality assurance for PV modules on-site and in laboratory simulator must meet the class AAA requirements of IEC 60904-9. The sun simulator must be calibrated with a reference cell, which itself was calibrated by a member of the WPVS scheme, with a maximum uncertainty of Isc of 1%. unique barcode (SNr) and labelled performance headlines (P(mpp), I(sc), U(oc), I(mpp), U(mpp) maximum current, maximum voltage Positive power sorting | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Cannot be evaluated at this stage. | compliance necessary | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Chint | MAW | Modules | Modules | Pre-shipment quality assurance | 1.14.4 | All modules must undergo Electroluminiscense (EL) inspection with a resolution of minimum 4 MPixel prior to shipment. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Cannot be evaluated at this stage. | compliance necessary | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Chint | MAW | Modules | Modules | Pre-shipment quality assurance | 1.14.4 | A sufficient EVA cross linking has to be verified per production line through a gel content test supervised by an accredited (IEC 17025 or national pendant) independent certified module testing agency. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Cannot be evaluated at this stage. | compliance necessary | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Chint | MAW | Modules | Modules | Quality assurance on site | 1.14.5 | The modules shall undergo an incoming inspection at arrival on construction site. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Cannot be evaluated at this stage. | stated and accepted | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Chint | MAW | Modules | Due Diligence | Quality Assurance | 1.14.6 | The bidder will bear the cost of the Quality assurance for PV modules on-site and in laboratory to be carried out by the Employer through an independent technical consultant up to 150,000 USD. | 1 |  |  |  | 1 |  |  |  |  | C |  | 1 |  | Open
Chint | MAW | Modules | Modules | Pre-shipment quality assurance | 1.14.7 | Warranties and evidence shall be given by the bidder that their selected modules have been tested for susceptibility to Potential Induced Degradation (PID). | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Chint | MAW | Modules | Credentials | Project references | 1.14.8 | To show the proven technology a minimum of 500MW of proposed product type series must be in operation and reference projects shall be named. | 1 | Doc 1&2 page 417, doc 3&4 page 105 |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | approx. 450 MWp named | Related to project references |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Chint | MAW | DC Cables | DC Cables | Specific Requirements | 1.15.1 | Are Ohmic losses less than 1% at full power? | 1 |  |  |  | 1 |  | Pvsyst: DC losses at 0.9%, AC losses not considered? |  | DC+AC losses < 2% | U |  | 1 |  | Open
Chint | MAW | DC Cables | DC Cables | Design factors to be provided | 1.15.2 | String cable shall be of the following type: single conductor type, copper, 1000 V / Class II (according to protection class II / 1000V, IEC 61140, single core cable, tinned copper conductor, XLPE Insulation, double EVA jacket (resistant to heat and cold, resistant to ozone, UV, oil and chemicals), Temperature: 90 º C (Temperature Max. Allowable: 120 º C), Halogen free | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | PV1-F 1*4 | It should be in accordance with the inverter values. | possibly 1500V for such system design | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Chint | MAW | DC Cables | DC Cables | Design factors to be provided | 1.15.2 | Connectors of Modules and string cables shall be connected of self-locking type, have IP65 rating and shall be from same manufacturer and type | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Chint | MAW | DC Cables | DC Cables | Design factors to be provided | 1.15.2 | The DC main (downstream of combiner box) wiring harness shall have the quality: Aluminum / Copper / 1000 V / Class II | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | It should be in accordance with the inverter values. | possibly 1500V for such system design | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Chint | MAW | DC Cables | DC Cables | Design factors to be provided | 1.15.2 | Balance of electrical potential | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Need to be disscussed | equipotential bonding earthing mesh | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Chint | MAW | DC Cables | DC Cables | Design factors to be provided | 1.15.2 | Installation to be verified by measurement-protocols | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Cannot be evaluated at this stage. | blanc protocol | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Chint | MAW | DC Cables | DC Cables | Design factors to be provided | 1.15.2 | Clear and systematic labelling required | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Chint | MAW | DC Cables | DC Cables | Design factors to be provided | 1.15.2 | Lifetime of 30 years is assured | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | What proof is required. | Life time test of nonmetal materials IEC 60811-408:2012 / (DIN EN 60811-408; VDE 0473-811-408:2012-12) 30 y assurance never seen until today | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Chint | MAW | DC Cables | DC Cables | Design factors to be provided | 1.15.2 | Sizing of cables shall be specified according to the number of modules and strings per array | 1 | doc 1&2 page 454 | 1 | [5 empty] | voltage drop calculation |  |  | 1 |  | Pass
Chint | MAW | DC Cables | DC Cables | Standards | 1.15.3 | IEC 60364-1 | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Chint | MAW | DC Connectors | DC Connectors | Standards | 1.16.2 | EN 50521 | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? | PV Connectors no, just a statement of compliance | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Chint | MAW | DC Connectors | DC Connectors | Standards | 1.16.2 | IEC 60512 | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? | Connectors E-Systems no, just a statement of compliance | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Chint | MAW | DC Junction Box | DC Junction Box | Design factors to be provided | 1.17.1 | At least IP54 | 1 | Doc 1&2 page 19 | 1 |  |  |  |  | DC Junction box is applicable in what conditions? | depending on DC Design |  |  | 1 |  | Pass
Chint | MAW | DC Junction Box | DC Junction Box | Design factors to be provided | 1.17.1 | DC fuses shall permit up to maximum 1000 V (or 1500V if designed). String box design, including all operating elements shall satisfy safety requirements | 1 | Doc 3&4 page 84 | 1 |  |  |  |  | Will inverter voltage(1500V) effect the maximum voltage(1000V)? | depends on spec of inverter. |  |  | 1 |  | Pass
Chint | MAW | DC Junction Box | DC Junction Box | Design factors to be provided | 1.17.1 | Monitored input-couples | 1 | Doc 1&2 page 19 | 1 | [8 empty] | 1 |  | Pass
Chint | MAW | DC Junction Box | DC Junction Box | Design factors to be provided | 1.17.1 | Class 2 DC surge arrestor | 1 | Doc 1&2 page 19 | 1 | [8 empty] | 1 |  | Pass
Chint | MAW | DC Junction Box | DC Junction Box | Design factors to be provided | 1.17.1 | Dust and heat protection | 1 | Doc 1&2 page 19 | 1 | [8 empty] | 1 |  | Pass
Chint | MAW | DC Junction Box | DC Junction Box | Specifications | 1.17.2 | Current monitoring | 1 | Doc 3&4 page 84 | 1 | [8 empty] | 1 |  | Pass
Chint | MAW | DC Junction Box | DC Junction Box | Specifications | 1.17.2 | Touch-safe protective cover | 1 | Doc 3&4 page 83 | 1 |  |  |  | transparent cover |  |  |  |  | 1 |  | Pass
Chint | MAW | DC Junction Box | DC Junction Box | Specifications | 1.17.2, 1.17.1 | Monitoring interface for SCADA | 1 | Doc 1&2 page 19 | 1 | [8 empty] | 1 |  | Pass
Chint | MAW | DC Junction Box | DC Junction Box | Standards | 1.17.3 | EN 61000-6 | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? | EMV no, just a statement of compliance | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Chint | MAW | DC Junction Box | DC Junction Box | Standards | 1.17.3 | EN 60439-1 | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? | arcing fault / Störlichtbogen Verhalten no, just a statement of compliance | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Chint | MAW | DC Junction Box | DC Junction Box | Standards | 1.17.3 | EN 50178 | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? | High currat devices no, just a statement of compliance | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Chint | MAW | Inverters | Warranty | Warranty option | 1.18.1 | The Bidder shall arrange a full-service package for the selected inverters for a product warranty period of 5 years, with an option to cover additional 20 years including provisions for any necessary replacements including O&M service plan guaranteeing 99% availability. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 5 years standard warranty; optional up to 20 years |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Chint | MAW | Inverters | Inverters | Strategic Reason for Inverter Selection | 1.18.2 | Balance of System (BOS) costs of inverter and labour | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  | financial bid | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Chint | MAW | Inverters | Inverters | Strategic Reason for Inverter Selection | 1.18.2 | Dust and heat protection | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  | derating? | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Chint | MAW | Inverters | Inverters | Strategic Reason for Inverter Selection | 1.18.2 | Timely and effective monitoring at a granular/zoomed-in level | 1 |  | 1 | [8 empty] | 1 |  | Pass
Chint | MAW | Inverters | Inverters | Strategic Reason for Inverter Selection | 1.18.2 | Available uptime | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Chint | MAW | Inverters | Inverters | Strategic Reason for Inverter Selection | 1.18.2 | Concept of protection against overload, short-circuit, grid-failure, internal failure, over-temperature (de-rating), surge protection | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Its too general, needs to be reviewed. | failure codes and consquences (automatic/manual restart, throw away safety devices) | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Chint | MAW | Inverters | O&M | Guarantees | 1.18.2 | For central inverters concept: the bidder shall ensure with an undertaking from the manufacturer that the concerned skilled staff will be made available at the site within 24 hours of reporting the defect to the manufacturer. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Chint | MAW | Inverters | Inverters | Functionalities | 1.18.3 | Maximum Power Point Tracking (MPPT) and string/sub-array management | 1 | Doc 3&4 page 53 | 1 | [8 empty] | 1 |  | Pass
Chint | MAW | Inverters | Inverters | Functionalities | 1.18.3 | Matching grid voltage and frequency at point-of-coupling | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Chint | MAW | Inverters | Inverters | Functionalities | 1.18.3 | Anti-islanding protection | 1 | doc 3&4 page 6 | 1 | [8 empty] | 1 |  | Pass
Chint | MAW | Inverters | Inverters | Functionalities | 1.18.3 | Voltage regulation through reactive power support: remotely set point control for voltage stability | 1 | Doc 3&4 page 53 | 1 |  |  |  | Reactive power adjustable and the power factor range from -0.8 to +0.8, Reactive power compensation at night | 8.2 needs to ensure these questions are answered in the bids. |  |  |  | 1 |  | Pass
Chint | MAW | Inverters | Inverters | Functionalities | 1.18.3 | Frequency regulation | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | 8.2 needs to ensure these questions are answered in the bids. |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Chint | MAW | Inverters | Inverters | Functionalities | 1.18.3 | Voltage and frequency fault ride-through: no disconnection of the connection through voltage dip and change of active power generation, feed-in of reactive power during the fault for voltage stabilisation | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | 8.2 needs to ensure these questions are answered in the bids. |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Chint | MAW | Inverters | Inverters | Functionalities | 1.18.3 | Limitation of voltage fluctuation due to switching operations and long-term flicker | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | 8.2 needs to ensure these questions are answered in the bids. |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Chint | MAW | Inverters | Inverters | Functionalities | 1.18.3 | Limitation of short-circuit current | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | 8.2 needs to ensure these questions are answered in the bids. |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Chint | MAW | Inverters | Inverters | Functionalities | 1.18.3 | Limitation of steady-stage voltage changes to 2% of the nominal value | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Chint | MAW | Inverters | Inverters | Functionalities | 1.18.3 | Limitation of current harmonics and higher frequency components up to 9 kHz | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Chint | MAW | Inverters | Inverters | Functionalities | 1.18.3 | Active power control reduction: remotely set point of control in case of network congestions or risk of system collapse, if deemed necessary | 1 | Doc 3&4 page 53 | 1 |  |  |  | Active power continuously adjustable | 8.2 needs to ensure these questions are answered in the bids. |  |  |  | 1 |  | Pass
Chint | MAW | Inverters | Monitoring | Functionalities | 1.18.3 | Advanced communication, with intelligent alerts/warnings, to the SCADA server | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Chint | MAW | Inverters | Inverters | Specific Requirements | 1.18.6 | Specifications of table in Schedule C shall be met | 1 |  | 1 |  |  |  |  | Link to table |  |  |  | 1 |  | Pass
Chint | MAW | Inverters | Inverters | Design factors to be provided | 1.18.7 | Input voltage range (The voltage window for MPP tracking shall accommodate the expected degradation of the modules.) | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Chint | MAW | Inverters | Inverters | Design factors to be provided | 1.18.7 | PV array configuration options: positive ground, negative ground | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Chint | MAW | Inverters | Inverters | Design factors to be provided | 1.18.7 | Integrated transformer/transformerless / Outside Dry Type Transformer | 1 | Doc 3&4 page 53 | 1 |  |  |  | transformerless |  |  |  |  | 1 |  | Pass
Chint | MAW | Inverters | Inverters | Design factors to be provided | 1.18.7 | Peak efficiency/ Weighted efficiency | 1 | Doc 3&4 page 53 | 1 | [8 empty] | 1 |  | Pass
Chint | MAW | Inverters | Inverters | Design factors to be provided | 1.18.7 | Nominal power | 1 | Doc 3&4 page 53 | 1 | [8 empty] | 1 |  | Pass
Chint | MAW | Inverters | Inverters | Design factors to be provided | 1.18.7 | Nominal output voltage | 1 | Doc 3&4 page 53 | 1 | [8 empty] | 1 |  | Pass
Chint | MAW | Inverters | Inverters | Design factors to be provided | 1.18.7 | Output voltage range | 1 | Doc 3&4 page 53 | 1 | [8 empty] | 1 |  | Pass
Chint | MAW | Inverters | Inverters | Design factors to be provided | 1.18.7 | Maximum output current | 1 | Doc 3&4 page 53 | 1 | [8 empty] | 1 |  | Pass
Chint | MAW | Inverters | Inverters | Design factors to be provided | 1.18.7 | Nominal output frequency, 3-phase | 1 | Doc 3&4 page 53 | 1 | [8 empty] | 1 |  | Pass
Chint | MAW | Inverters | Inverters | Design factors to be provided | 1.18.7 | Operating temperature range | 1 | Doc 3&4 page 53 | 1 |  |  |  |  | What is the acceptable range? | 60°C Derating? |  |  | 1 |  | Pass
Chint | MAW | Inverters | Inverters | Design factors to be provided | 1.18.7 | Cooling method | 1 | Doc 3&4 page 53 | 1 |  |  |  | Variable speed cooling fans |  |  |  |  | 1 |  | Pass
Chint | MAW | Inverters | Inverters | Design factors to be provided | 1.18.7 | Detection of insulation faults | 1 | Doc 3&4 page 53 |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Chint | MAW | Inverters | Inverters | Design factors to be provided | 1.18.7 | Protection rating: NEMA 3R, IP54/IP55/IP60 | 1 |  | 1 |  |  |  | IP20 indoor, installed in a station |  |  |  |  | 1 |  | Pass
Chint | MAW | Inverters | Inverters | Standards | 1.18.8 | IEEE 1547 | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? | no, just a statement of compliance Interconnecting Distributed Resources | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Chint | MAW | Inverters | Inverters | Standards | 1.18.8 | TUV, VDE, or equivalent certification of passing the relevant standards | 1 | Doc 3&4 page 4 | 1 | [8 empty] | 1 |  | Pass
Chint | MAW | Inverters | Inverters | Manufacturers confirmation | 1.18.9 | The Bidder shall deliver a manufacturer's confirmation in his Bid for the suitability of the inverter for the specific weather conditions applicable in Bahawalpur Pakistan. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Chint | MAW | Inverters | Credentials | Project references | 1.18.10 | A minimum of 100 MWp of similar product/type must be in operation and reference projects shall be named. | 1 | Doc 3&4 page 26 | 1 | [8 empty] | 1 |  | Pass
Chint | MAW | Inverters | Inverters | Quality Assurance | 1.18.11 | Check of protection against overload, short-circuit, grid-failure, internal failure, over-temperature (de-rating), surge protection, detection of insulation faults of AC Cables. Bidder shall firmly specify the manufacturer, types and length of cables to be installed | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | 8.2 needs to ensure these questions are answered in the bids. |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Chint | MAW | Inverters | Inverters | Quality Assurance | 1.18.11 | Test run in the field for maximum and EU-efficiency of all Inverters | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | 8.2 needs to ensure these questions are answered in the bids. |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Chint | MAW | Inverters | Inverters | Quality Assurance | 1.18.11 | Test run and check of MPP tracking of all inverters | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | 8.2 needs to ensure these questions are answered in the bids. |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Chint | MAW | Inverters | Inverters | Quality Assurance | 1.18.11 | The Bidder shall deliver detailed protocols of performance test run (warm power test) for every single inverter | 1 |  |  |  | 1 |  |  | Cannot be evaluated at this stage |  | C |  | 1 |  | Open
Chint | MAW | Inverters | Inverters | Quality Assurance | 1.18.11 | After commissioning, 1 of 10 inverters will be measured on site (power curve and efficiency) by an approved independent technical consultant on behalf of the Employer. The on-site measurements shall be accepted by the Bidder as average values for all inverters | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Cannot be evaluated at this stage | compliance! | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Chint | MAW | Inverters | Due diligence | Quality Assurance | 1.18.12 | The Bidder accepts that the cost of the Quality assurance for Inverters to be carried by the Employer through an independent technical consultant shall be taken over by the successful bidder up to an amount of 100,000 USD. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Zte | JUE | Scope of the Bid | O&M | General Requirements | 2.1.2 | Responsibility to keep Performance Ratio and Availability at highest levels | 1 |  | 1 | [8 empty] | 1 |  | Pass
Zte | JUE | Scope of the Bid | O&M | General Requirements | 2.1.2 | Preventive maintenance | 2 |  | 1 | [8 empty] | 1 |  | Pass
Zte | JUE | Scope of the Bid | O&M | General Requirements | 2.1.2 | Provision and Installation of spare parts, keeping of spare parts stock (refill of used spares). Reporting of status and consumption to be continuously updated | 2 |  |  |  | 1 | Unclear: We do not understand your proposal, please detail your proposal. Especially confirm that you are compliant with our requested criteria. | not completely described |  |  |  |  | 1 |  | Open
Zte | JUE | Scope of the Bid | O&M | General Requirements | 2.1.2 | Corrective maintenance with guaranteed response times | 1 |  |  |  | 1 | Unclear: We do not understand your proposal, please detail your proposal. Especially confirm that you are compliant with our requested criteria. | not correct described |  |  |  |  | 1 |  | Open
Zte | JUE | Scope of the Bid | O&M | General Requirements | 2.1.2 | Daily, monthly and yearly performance and production reporting | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | no reporting is described |  |  |  |  | 1 |  | Open
Zte | JUE | Scope of the Bid | O&M | General Requirements | 2.1.2 | Operation of the Plant (including 24/7 presence of O&M and security staff on the project site). | 1 |  | 1 | [8 empty] | 1 |  | Pass
Zte | JUE | Scope of the Bid | O&M | General Requirements | 2.1.2 | Cleaning of the Plant, preventive and corrective maintenance of the civil works and the fences. | 1 |  |  |  | 1 | Unclear: We do not understand your proposal, please detail your proposal. Especially confirm that you are compliant with our requested criteria. | not correct described |  |  |  |  | 1 |  | Open
Zte | JUE | Scope of the Bid | O&M | General Requirements | 2.1.2 | Cleaning of Modules and irradiation sensors to prevent dust accumulation to undesirable level. | 1 |  |  |  | 1 | Unclear: We do not understand your proposal, please detail your proposal. Especially confirm that you are compliant with our requested criteria. | not correct described |  |  |  |  | 1 |  | Open
Zte | JUE | Scope of the Bid | O&M | General Requirements | 2.1.2 | Ordinary road and land maintenance to the extent required for proper maintenance of the Plant. | 3 |  |  |  | 1 | Unclear: We do not understand your proposal, please detail your proposal. Especially confirm that you are compliant with our requested criteria. | not described |  |  |  |  | 1 |  | Open
Zte | JUE | Scope of the Bid | O&M | General Requirements | 2.1.2 | Smooth functioning of all interconnections and data communications of the system performance | 2 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing |  |  |  |  | 1 |  | Open
Zte | JUE | Scope of the Bid | O&M | General Requirements | 2.1.2 | Optimal level of SCADA monitoring | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us | [5 empty] | 1 |  | Open
Zte | JUE | Scope of the Bid | O&M | General Requirements | 2.1.2 | Coordination and compliance with NTDC requirements | 1 |  | 1 | [8 empty] | 1 |  | Pass
Zte | JUE | Scope of the Bid | O&M | General Requirements | 2.1.2 | Maintaining a customer support hotline for the Employer/NTDC | 3 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing |  |  |  |  | 1 |  | Open
Zte | JUE | Scope of the Bid | O&M | General Requirements | 2.1.2 | Providing regular reports of repairs, maintenance, and tests | 3 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing |  |  |  |  | 1 |  | Open
Zte | JUE | Scope of the Bid | O&M | General Requirements | 2.1.2 | Performance variance analysis of the module strings and inverters | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing |  |  |  |  | 1 |  | Open
Zte | JUE | Scope of the Bid | O&M | General Requirements | 2.1.2 | Periodic maintenance of inverter, transformer, combiner boxes etc., according manufacturer's requirements | 1 |  |  |  | 1 | Unclear: We do not understand your proposal, please detail your proposal. Especially confirm that you are compliant with our requested criteria. | no period is described |  |  |  |  | 1 |  | Open
Zte | JUE | Scope of the Bid | O&M | General Requirements | 2.1.2 | Scheduled maintenance routines: e.g., inspections of modules with polarized sunglasses to check for discolouration, the first signs of de-lamination, loose wires in the electronics, corrosion of mounting structures, erosion | 1 |  | 1 | [8 empty] | 1 |  | Pass
Zte | JUE | Scope of the Bid | O&M | General Requirements | 2.1.2 | Track chronic negative deviations in the module string output, i.e., power tolerances consistently in the negative | 3 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing |  |  |  |  | 1 |  | Open
Zte | JUE | Scope of the Bid | O&M | General Requirements | 2.1.2 | Negotiating a warranty reserve for replacements with the suppliers | 3 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing |  |  |  |  | 1 |  | Open
Zte | JUE | Scope of the Bid | O&M | General Requirements | 2.1.2 | Maintaining adequate reserves for timely replacement | 2 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing |  |  |  |  | 1 |  | Open
Zte | JUE | Scope of the Bid | O&M | General Requirements | 2.1.2 | Insuring products at different levels but for sensible costs; the insurance policy shall not become expensive compared to the replacement cost of the item | 3 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing |  |  |  |  | 1 |  | Open
Zte | JUE | Scope of the Bid | O&M | General Requirements | 2.1.2 | Warranties and insurance policies should be assignable/transferrable to the Employer in case it decides to take over the O&M | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing |  |  |  |  | 1 |  | Open
Zte | JUE | Scope of the Bid | O&M | General Requirements | 2.1.2 | Reporting the monitoring and surveillance system. | 3 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing |  |  |  |  | 1 |  | Open
Zte | JUE | Scope of the Bid | O&M | General Requirements | 2.1.2 | Technical report elaboration. | 3 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing |  |  |  |  | 1 |  | Open
Zte | JUE | Scope of the Bid | O&M | General Requirements | 2.1.2 | On site Security services. | 3 |  |  |  | 1 | Unclear: We do not understand your proposal, please detail your proposal. Especially confirm that you are compliant with our requested criteria. | not completely described |  |  |  |  | 1 |  | Open
Zte | JUE | Scope of the Bid | O&M | General Requirements | 2.1.2 | Provide all O&M Staff, trained and certified as far as applicable. For security reasons, a 24 h/ 7 days a week staffing of security and maintenance shall be provided. The staffing concept and selected key employees shall be presented to the Employer for approval. | 1 | 2. Operation & Maintenance Services Proposal_v1.0_20140218.pdf 3.1 Page 13 |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 3 3.1 Inspection personnel should be trained and get certificate. |  |  |  |  | 1 |  | Open
Zte | JUE | Initial Inspection | O&M | General Requirements | 2.2.1 | familiarize himself with the specific plant equipment and specific maintenance requirements / training of staff | 1 | 3. Operation & Maintenance Services Proposal_v1.0_20140218.pdf 3.1 Page 13 |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 3 3.1 Inspection personnel should be trained and get certificate. |  |  |  |  | 1 |  | Open
Zte | JUE | Initial Inspection | O&M | General Requirements | 2.2.2 | Maintenance routines, inspection check-lists, working files, | 1 |  |  |  | 1 | Unclear: We do not understand your proposal, please detail your proposal. Especially confirm that you are compliant with our requested criteria. | not completely described |  |  |  |  | 1 |  | Open
Zte | JUE | Initial Inspection | O&M | General Requirements | 2.2.3 | coordinate with the Employer and keep him updated regarding his progress of preparation, status of construction, pending issues of Construction, Commissioning and testing. | 2 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | Cannot be evaluated at this stage |  |  |  |  | 1 |  | Open
Zte | JUE | Bi-annual inspection | O&M | PV Generator | 2.3.1 | 100% visual inspection of modules regarding damage in spring | 1 |  |  |  | 1 | Unclear: We do not understand your proposal, please detail your proposal. Especially confirm that you are compliant with our requested criteria. | not completely described |  |  |  |  | 1 |  | Open
Zte | JUE | Bi-annual inspection | O&M | PV Generator | 2.3.1 | Random visual inspection of modules regarding damage in autumn | 2 |  |  |  | 1 |  | Cannot be evaluated at this stage |  |  |  |  | 1 |  | Open
Zte | JUE | Bi-annual inspection | O&M | PV Generator | 2.3.1 | Random check of module clip with respect to loosening; if necessary replacement of clips (min. 10%, documentation of location, during 5 years inspection of whole PV plant) | 2 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | Cannot be evaluated at this stage missing |  |  |  |  | 1 |  | Open
Zte | JUE | Bi-annual inspection | O&M | PV Generator | 2.3.1 | Random testing of the steadiness of the mounting foundation/system and random inspection regarding corrosion at substructure (min. 10%, documentation of location, during 10 years inspection of whole PV plant) | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing |  |  |  |  | 1 |  | Open
Zte | JUE | Bi-annual inspection | O&M | PV Generator | 2.3.1 | Documentation of wear and tear of moving components, monitoring of dust intrusion and corrosion. | 2 |  | 1 | [8 empty] | 1 |  | Pass
Zte | JUE | Bi-annual inspection | O&M | PV Generator | 2.3.1 | Cleaning of sensors and switches | 1 |  |  |  |  | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | sensors shall be done by independent Meteo Station Operator |  |  |  |  | 0 |  | Open
Zte | JUE | Bi-annual inspection | O&M | PV Generator | 2.3.1 | Cleaning of all modules | 1 |  | 1 | [8 empty] | 1 |  | Pass
Zte | JUE | Bi-annual inspection | O&M | Inverter (100%) | 2.3.2 | Functional check of ventilator system of inverter station | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing |  |  |  |  | 1 |  | Open
Zte | JUE | Bi-annual inspection | O&M | Inverter (100%) | 2.3.2 | Cleaning of the filter mats in the air leaks | 2 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing |  |  |  |  | 1 |  | Open
Zte | JUE | Bi-annual inspection | O&M | Inverter (100%) | 2.3.2 | Replacement of dirty filter mats | 2 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing |  |  |  |  | 1 |  | Open
Zte | JUE | Bi-annual inspection | O&M | Inverter (100%) | 2.3.2 | Inspection of the interior of the electrical cabinet regarding dust deposit, dirtiness, humidity, water penetration from outside. If necessary the cabinet has to be cleaned. | 1 |  | 1 | [8 empty] | 1 |  | Pass
Zte | JUE | Bi-annual inspection | O&M | Inverter (100%) | 2.3.2 | Testing of inverter features according to maintenance schedule of manufacturer. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing |  |  |  |  | 1 |  | Open
Zte | JUE | Bi-annual inspection | O&M | Inverter (100%) | 2.3.2 | Maintenance of inverters according to manufacturer's instruction. | 1 |  |  |  |  | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing |  |  |  |  | 0 |  | Open
Zte | JUE | Bi-annual inspection | O&M | Monitoring | 2.3.3 | Functionality testing of the monitoring system | 3 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing |  |  |  |  | 1 |  | Open
Zte | JUE | Bi-annual inspection | O&M | Maintenance | 2.3.3 | Maintenance of all Power plant components according to manufacturer's instructions | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing |  |  |  |  | 1 |  | Open
Zte | JUE | Main Annual Inspection | O&M | PV Generator | 2.4.1 | Visual inspection of all accessible cable trenches and cable trays regarding damage | 1 |  | 1 | [8 empty] | 1 |  | Pass
Zte | JUE | Main Annual Inspection | O&M | PV Generator | 2.4.1 | Visual inspection and random testing of string connector (min. 10% with Documentation of location , during 10 years testing of whole PV plant) | 1 |  | 1 | [8 empty] | 1 |  | Pass
Zte | JUE | Main Annual Inspection | O&M | PV Generator | 2.4.1 | Inspection of DC distribution box: Visual inspection of all clamps and degree of pollution. Testing of over-voltage protection | 1 |  | 1 | [8 empty] | 1 |  | Pass
Zte | JUE | Main Annual Inspection | O&M | PV Generator | 2.4.1 | Maintenance of sensors based on manufacturer’s instructions | 1 |  |  |  | 1 | [6 empty] | 1 |  | Open
Zte | JUE | Main Annual Inspection | O&M | Inverter (100%) | 2.4.2 | Test of the internal miniature circuit breakers and power switch, test of emergency shut-off | 1 |  | 1 | [8 empty] | 1 |  | Pass
Zte | JUE | Main Annual Inspection | O&M | Inverter (100%) | 2.4.2 | Visual inspection of all fuses | 1 |  |  |  | 1 | Unclear: We do not understand your proposal, please detail your proposal. Especially confirm that you are compliant with our requested criteria. | not completely described |  |  |  |  | 1 |  | Open
Zte | JUE | Main Annual Inspection | O&M | Inverter (100%) | 2.4.2 | Inspection of over-voltage protection and upstream fuses regarding external damage | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing |  |  |  |  | 1 |  | Open
Zte | JUE | Main Annual Inspection | O&M | Inverter (100%) | 2.4.2 | Functional check of internal and external over- and under-voltage monitoring through operation of test terminal | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing |  |  |  |  | 1 |  | Open
Zte | JUE | Main Annual Inspection | O&M | Inverter (100%) | 2.4.2 | Functional check of insulation monitoring | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing |  |  |  |  | 1 |  | Open
Zte | JUE | Main Annual Inspection | O&M | Inverter (100%) | 2.4.2 | Check of control and auxiliary voltages | 2 |  | 1 | [8 empty] | 1 |  | Pass
Zte | JUE | Main Annual Inspection | O&M | Inverter (100%) | 2.4.2 | Check of the safety circuit for the interruption of the AC-grid protection in the case of failure (emergency shut-off, over-/ under-voltage, over temperature, etc.) based on the local conditions | 1 |  | 1 | [8 empty] | 1 |  | Pass
Zte | JUE | Main Annual Inspection | O&M | Inverter (100%) | 2.4.2 | Visual inspection of AC and DC clamps regarding tightness and colouring, tightening of clamps | 1 |  | 1 | [8 empty] | 1 |  | Pass
Zte | JUE | Main Annual Inspection | O&M | Inverter (100%) | 2.4.2 | Maintenance of inverters according to manufacturer instruction | 1 |  |  |  | 1 | Unclear: We do not understand your proposal, please detail your proposal. Especially confirm that you are compliant with our requested criteria. | not completely described |  |  |  |  | 1 |  | Open
Zte | JUE | Main Annual Inspection | O&M | Roads | 2.4.3 | Visual inspection of roads within the PV plant shall be carried out to ascertain that these are maintained in good condition for the intended purpose. | 2 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing |  |  |  |  | 1 |  | Open
Zte | JUE | Main Annual Inspection | O&M | Substation and Transmission Line | 2.4.4 | Visual inspection of transformer and switchboard rooms and cleaning if necessary | 1 |  |  |  | 1 | Unclear: We do not understand your proposal, please detail your proposal. Especially confirm that you are compliant with our requested criteria. | not completely described |  |  |  |  | 1 |  | Open
Zte | JUE | Main Annual Inspection | O&M | Substation and Transmission Line | 2.4.4 | Visual inspection of Transmission Line and report of damage to the grid operator | 2 |  |  |  | 1 | Unclear: We do not understand your proposal, please detail your proposal. Especially confirm that you are compliant with our requested criteria. | not completely described |  |  |  |  | 1 |  | Open
Zte | JUE | Main Annual Inspection | O&M | Substation and Transmission Line | 2.4.4 | Maintenance of substation and transmission line according to manufacturer instruction | 1 |  |  |  | 1 | Unclear: We do not understand your proposal, please detail your proposal. Especially confirm that you are compliant with our requested criteria. | not completely described |  |  |  |  | 1 |  | Open
Zte | JUE | Main Annual Inspection | O&M | Auxiliary system | 2.4.5 | Inspection of security system inclusive fence, all gates, all cameras etc. Random test of the fence fastening, if necessary retightening of the screws | 2 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing |  |  |  |  | 1 |  | Open
Zte | JUE | Main Annual Inspection | O&M | Auxiliary system | 2.4.5 | If existing: inspection of requirements out of the building permit | 2 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing |  |  |  |  | 1 |  | Open
Zte | JUE | Main Annual Inspection | O&M | Auxiliary system | 2.4.5 | Maintenance of all components according to manufacturer instruction | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing |  |  |  |  | 1 |  | Open
Zte | JUE | Special inspection (every 4 years) | O&M | Specific Requirements | 2.5.1 | Measurement of inverters and generators according to recognized international standards and according to results from commissioning certificates (insulation, loop resistance, earthing, DC-open circuit voltage) | 2 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing |  |  |  |  | 1 |  | Open
Zte | JUE | Special inspection (every 4 years) | O&M | Specific Requirements | 2.5.1 | Protection systems of medium voltage switching panels of the stations | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing |  |  |  |  | 1 |  | Open
Zte | JUE | Special inspection (every 4 years) | O&M | Specific Requirements | 2.5.1 | Oil check of transformers | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing |  |  |  |  | 1 |  | Open
Zte | JUE | Special inspection (every 4 years) | O&M | Specific Requirements | 2.5.1 | Control of station equipment | 2 |  | 1 | [8 empty] | 1 |  | Pass
Zte | JUE | Deactivation | O&M | Allowed deactivation periods | 2.6.1 | Times with irradiation level < 300 W/m² | 2 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing |  |  |  |  | 1 |  | Open
Zte | JUE | Deactivation | O&M | Allowed deactivation periods | 2.6.1 | Approved by The Employer to ensure consideration of Employer's obligations | 2 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing |  |  |  |  | 1 |  | Open
Zte | JUE | Deactivation | O&M | Allowed deactivation periods | 2.6.1 | Approved from grid operator | 2 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing |  |  |  |  | 1 |  | Open
Zte | JUE | Deactivation | O&M | Specific Requirements | 2.6.2 | All deactivations during maintenance works shall be completely documented. | 2 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing |  |  |  |  | 1 |  | Open
Zte | JUE | Deactivation | O&M | Specific Requirements | 2.6.3 | Deactivation shall not be considered as permitted downtime. | 2 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing |  |  |  |  | 1 |  | Open
Zte | JUE | Change of Inspection and Maintenance Work procedures | O&M | Specific Requirements | 2.7 | work in accordance with all applicable laws | 2 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing |  |  |  |  | 1 |  | Open
Zte | JUE | Performance of maintenance and repair works | O&M | Specific Requirements | 2.8.1 | Corresponding regulations of the respective component manufacturer shall have to be followed during maintenance works | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing |  |  |  |  | 1 |  | Open
Zte | JUE | Performance of maintenance and repair works | O&M | Specific Requirements | 2.8.2 | Report document for maintenance works (blanc sample requiered for bid) | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing |  |  |  |  | 1 |  | Open
Zte | JUE | Performance of maintenance and repair works | O&M | Specific Requirements | 2.8.3 | Observe and respect the maintenance and operation specifications of the manufacturer of the components | 3 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing |  |  |  |  | 1 |  | Open
Zte | JUE | Performance of maintenance and repair works | O&M | Specific Requirements | 2.8.4 | Observe and respect the local law, regulations and international PV standards. | 3 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing |  |  |  |  | 1 |  | Open
Zte | JUE | Performance of maintenance and repair works | O&M | Specific Requirements | 2.8.5 | During his work the Bidder shall be held responsible for the public safety of the PV plant | 2 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing |  |  |  |  | 1 |  | Open
Zte | JUE | On-site monitoring | O&M | Specific Requirements | 2.9.1 | Permanent (24/7) staffing of the Power Plant, consisting of security and O&M personnel. | 1 |  | 1 | [8 empty] | 1 |  | Pass
Zte | JUE | On-site monitoring | O&M | Specific Requirements | 2.9.2 | Bidder shall arrange service contracts with specialized sub-contractors | 2 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing |  |  |  |  | 1 |  | Open
Zte | JUE | On-site monitoring | O&M | Specific Requirements | 2.9.3 | All operational data shall be logged on-site in parallel to the remote data storage | 2 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing |  |  |  |  | 1 |  | Open
Zte | JUE | On-site monitoring | O&M | Specific Requirements | 2.9.4 | The data of irradiation sensors shall be monitored by an independent expert on a continuous basis | 2 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing |  |  |  |  | 1 |  | Open
Zte | JUE | Remote Supervision | O&M | Specific Requirements | 2.10.1 | On-call service provided for the Employer for availability outside business hours and during weekends (24/7). | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing |  |  |  |  | 1 |  | Open
Zte | JUE | Remote Supervision | O&M | Specific Requirements | 2.10.2 | Any reductions in performance shall have to be logged. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing |  |  |  |  | 1 |  | Open
Zte | JUE | Remote Supervision | O&M | Specific Requirements | 2.10.3 | The data will comprise, apart from electrical parameters of the PV plant: currents, voltages, irradiation values, kind and period of reductions in performance such as curtailment by the grid operator | 2 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing |  |  |  |  | 1 |  | Open
Zte | JUE | Remote Supervision | O&M | Specific Requirements | 2.10.4 | The data shall present the status of the plant such as the performance ratio annual overview and the current feed-in power | 2 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing |  |  |  |  | 1 |  | Open
Zte | JUE | Remote Supervision | O&M | Specific Requirements | 2.10.5 | The remote supervision shall also control the operation of the PV plant. | 2 |  |  |  | 1 | Unclear: We do not understand your proposal, please detail your proposal. Especially confirm that you are compliant with our requested criteria. | not completely described |  |  |  |  | 1 |  | Open
Zte | JUE | Remote Supervision | O&M | Specific Requirements | 2.10.6 | The remote supervision shall also include the taking of measures for removal of faults. | 2 |  |  |  | 1 | Unclear: We do not understand your proposal, please detail your proposal. Especially confirm that you are compliant with our requested criteria. | not completely described |  |  |  |  | 1 |  | Open
Zte | JUE | Remote Supervision | O&M | Specific Requirements | 2.10.7 | The Bidder shall provide to the Employer permanent online access to the power plant control system for parallel monitoring | 1 |  |  |  | 1 | [6 empty] | 1 |  | Open
Zte | JUE | Remote Supervision | O&M | Specific Requirements | 2.10.8 | Monthly / quarterly and annual reports based on the data of the remote supervision provided to the Employer 4 weeks after the last period of reporting at the latest. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing |  |  |  |  | 1 |  | Open
Zte | JUE | Remote Supervision | O&M | Specific Requirements | 2.10.9 | The fees for telephone connection and/or data transfer services are included in the annual remuneration. | 2 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing |  |  |  |  | 1 |  | Open
Zte | JUE | Reaction to Fault Messages / Response Times | O&M | Specific Requirements | 2.11.1 | Every fault message has to be registered in the monitoring software. According to the fault message, the Bidder shall issue a fault diagnosis within a response time of 2 hours (24/7) | 1 |  |  |  | 1 | Unclear: We do not understand your proposal, please detail your proposal. Especially confirm that you are compliant with our requested criteria. | not completely described |  |  |  |  | 1 |  | Open
Zte | JUE | Reaction to Fault Messages / Response Times | O&M | Specific Requirements | 2.11.2 | profit relevant Fault Events: Downtime registration/ reasons/ repair/ in monthly report (blanc of monthly report?) | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing |  |  |  |  | 1 |  | Open
Zte | JUE | Fault Management / Warranty defects | O&M | Specific Requirements | 2.12.1 | Fault Management: all handling and communication | 2 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing |  |  |  |  | 1 |  | Open
Zte | JUE | Fault Management / Warranty defects | O&M | Specific Requirements | 2.12.2 | Fault Management: Handling / correspondence with third parties | 2 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing |  |  |  |  | 1 |  | Open
Zte | JUE | Fault Management / Warranty defects | O&M | Specific Requirements | 2.12.3 | Fault Management = without repair works | 3 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing |  |  |  |  | 1 |  | Open
Zte | JUE | Fault Management / Warranty defects | O&M | Specific Requirements | 2.12.4 | Product warranties in favour of contractor / Bidder (responsible) to claim all warranties for at least 5 years | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing |  |  |  |  | 1 |  | Open
Zte | JUE | Fault Management / Warranty defects | O&M | Specific Requirements | 2.12.5 | Operational defects, which are not considered as warranty defects - see repair works section below | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing |  |  |  |  | 1 |  | Open
Zte | JUE | Fault Management / Warranty defects | O&M | Specific Requirements | 2.12.6 | All defects shall be documented within the same day of detection, | 2 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing |  |  |  |  | 1 |  | Open
Zte | JUE | Fault Calls | O&M | Specific Requirements | 2.13.1 | The scope of service shall include any working times for all fault calls including travelling times and costs. | 1 |  |  |  | 1 | Unclear: We do not understand your proposal, please detail your proposal. Especially confirm that you are compliant with our requested criteria. | not completely described |  |  |  |  | 1 |  | Open
Zte | JUE | Fault Calls | O&M | Specific Requirements | 2.13.2 | The minimum response time in case of failure must meet the EPA requirements | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing |  |  |  |  | 1 |  | Open
Zte | JUE | Fault Calls | O&M | Specific Requirements | 2.13.2 | --> Time Model: Response Times for Priorities 1-3 (12h / 24h / 1 week) | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing |  |  |  |  | 1 |  | Open
Zte | JUE | Fault Calls | O&M | Specific Requirements | 2.13.3 | failure time response does not match the response time of EPA >> failure time response does not match the response time of EPA | 3 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing |  |  |  |  | 1 |  | Open
Zte | JUE | Fault Calls | O&M | Specific Requirements | 2.13.4 | The fault call shall include the fault diagnosis on site as well as an immediate error correction if possible. The fault shall have to be corrected within the response time and, failing this, a diagnosis of the fault has to be effect indicating further measures. | 2 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing |  |  |  |  | 1 |  | Open
Zte | JUE | Fault Calls | O&M | Specific Requirements | 2.13.5 | Fault calls can be performed without prior consent of the Employer. | 3 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing |  |  |  |  | 1 |  | Open
Zte | JUE | Fault Calls | O&M | Specific Requirements | 2.13.6 | If the elimination of faults is not possible within the response time / and additional travelling, this is Repair Work | 3 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing |  |  |  |  | 1 |  | Open
Zte | JUE | Spare Parts and Tools | O&M | Specific Requirements | 2.14 | provide the necessary set of spare parts and maintenance tools as required to perform the services | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing |  |  |  |  | 1 |  | Open
Zte | JUE | Spare Parts and Tools | O&M | Specific Requirements | 2.14.1 | cover all cost for supply and re-stocking of spare parts from his annual remuneration. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing |  |  |  |  | 1 |  | Open
Zte | JUE | Spare Parts and Tools | O&M | Specific Requirements | 2.14.2 | refill spare parts immediately after consumption | 2 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing |  |  |  |  | 1 |  | Open
Zte | JUE | Reduced Output of the Plant | O&M | Specific Requirements | 2.15 | Monthly comparison of the specific performance of all measuring channels among each other. 5% reduced output results in general check of all the channels and shall be documented. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing |  |  |  |  | 1 |  | Open
Zte | JUE | Reduced Output of the Plant | O&M | Specific Requirements | 2.15.1 | Identified reduced output shall be justified. Reduced output shall be recovered and liquidated damages determined. | 1 |  |  |  | 1 |  | missing liquidated --> means --> performance |  |  |  |  | 1 |  | Open
Zte | JUE | Repair time and cost | O&M | Specific Requirements | 2.16 | Repair times are considered as part of the availability guaranty of the Bidder. All cost of repair shall be part of the Bidders annual remuneration. For the avoidance of doubt that includes any repairs due to lightening, theft and vandalism. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing |  |  |  |  | 1 |  | Open
Zte | JUE | Working Time | O&M | Specific Requirements | 2.17 | All working times of Bidders personnel shall be included in the Bidders annual remuneration. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing |  |  |  |  | 1 |  | Open
Zte | JUE | Approval | O&M | Specific Requirements | 2.18 | Extensive repairs have to be approved by the Employer. | 2 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing |  |  |  |  | 1 |  | Open
Zte | JUE | Documentation | O&M | Specific Requirements | 2.19 | All repair works and compensations shall have to be documented and to be submitted to the Employer within two weeks. | 2 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing |  |  |  |  | 1 |  | Open
Zte | JUE | Inspection of Repair Works | O&M | Specific Requirements | 2.20 | The Employer can inspect the repair works within one month (30 days) after receiving the documentation | 2 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing |  |  |  |  | 1 |  | Open
Zte | JUE | Ground Maintenance | O&M | Specific Requirements | 2.21 | Ground maintenance shall include all procedures that are necessary to avoid module shading and an incorrect operation of the trackers. This shall include the levelling of sand drifts. Necessary switching operations shall be coordinated by the Bidder with responsible authorities | 2 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing |  |  |  |  | 1 |  | Open
Zte | JUE | Person in Control of PV plant | O&M | Specific Requirements | 2.22 | The Bidder shall propose an organigram for the O& M personnel with one main responsible | 2 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing |  |  |  |  | 1 |  | Open
Zte | JUE | Reporting | O&M | Specific Requirements | 2.23 | The Bidder shall deliver to the Employer regular reports on monthly, quarterly and annual basis. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing |  |  |  |  | 1 |  | Open
Tbea | JUE | Scope of the Bid | O&M | General Requirements | 2.1.2 | Responsibility to keep Performance Ratio and Availability at highest levels | 1 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | JUE | Scope of the Bid | O&M | General Requirements | 2.1.2 | Preventive maintenance | 2 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | JUE | Scope of the Bid | O&M | General Requirements | 2.1.2 | Provision and Installation of spare parts, keeping of spare parts stock (refill of used spares). Reporting of status and consumption to be continuously updated | 2 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | JUE | Scope of the Bid | O&M | General Requirements | 2.1.2 | Corrective maintenance with guaranteed response times | 1 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | JUE | Scope of the Bid | O&M | General Requirements | 2.1.2 | Daily, monthly and yearly performance and production reporting | 1 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | JUE | Scope of the Bid | O&M | General Requirements | 2.1.2 | Operation of the Plant (including 24/7 presence of O&M and security staff on the project site). | 1 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | JUE | Scope of the Bid | O&M | General Requirements | 2.1.2 | Cleaning of the Plant, preventive and corrective maintenance of the civil works and the fences. | 1 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | JUE | Scope of the Bid | O&M | General Requirements | 2.1.2 | Cleaning of Modules and irradiation sensors to prevent dust accumulation to undesirable level. | 1 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | JUE | Scope of the Bid | O&M | General Requirements | 2.1.2 | Ordinary road and land maintenance to the extent required for proper maintenance of the Plant. | 3 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | JUE | Scope of the Bid | O&M | General Requirements | 2.1.2 | Smooth functioning of all interconnections and data communications of the system performance | 2 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | JUE | Scope of the Bid | O&M | General Requirements | 2.1.2 | Optimal level of SCADA monitoring | 1 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | JUE | Scope of the Bid | O&M | General Requirements | 2.1.2 | Coordination and compliance with NTDC requirements | 1 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | JUE | Scope of the Bid | O&M | General Requirements | 2.1.2 | Maintaining a customer support hotline for the Employer/NTDC | 3 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | JUE | Scope of the Bid | O&M | General Requirements | 2.1.2 | Providing regular reports of repairs, maintenance, and tests | 3 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | JUE | Scope of the Bid | O&M | General Requirements | 2.1.2 | Performance variance analysis of the module strings and inverters | 1 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | JUE | Scope of the Bid | O&M | General Requirements | 2.1.2 | Periodic maintenance of inverter, transformer, combiner boxes etc., according manufacturer's requirements | 1 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | JUE | Scope of the Bid | O&M | General Requirements | 2.1.2 | Scheduled maintenance routines: e.g., inspections of modules with polarized sunglasses to check for discolouration, the first signs of de-lamination, loose wires in the electronics, corrosion of mounting structures, erosion | 1 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | JUE | Scope of the Bid | O&M | General Requirements | 2.1.2 | Track chronic negative deviations in the module string output, i.e., power tolerances consistently in the negative | 3 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | JUE | Scope of the Bid | O&M | General Requirements | 2.1.2 | Negotiating a warranty reserve for replacements with the suppliers | 3 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | JUE | Scope of the Bid | O&M | General Requirements | 2.1.2 | Maintaining adequate reserves for timely replacement | 2 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | JUE | Scope of the Bid | O&M | General Requirements | 2.1.2 | Insuring products at different levels but for sensible costs; the insurance policy shall not become expensive compared to the replacement cost of the item | 3 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | JUE | Scope of the Bid | O&M | General Requirements | 2.1.2 | Warranties and insurance policies should be assignable/transferrable to the Employer in case it decides to take over the O&M | 1 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | JUE | Scope of the Bid | O&M | General Requirements | 2.1.2 | Reporting the monitoring and surveillance system. | 3 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | JUE | Scope of the Bid | O&M | General Requirements | 2.1.2 | Technical report elaboration. | 3 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | JUE | Scope of the Bid | O&M | General Requirements | 2.1.2 | On site Security services. | 3 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | JUE | Scope of the Bid | O&M | General Requirements | 2.1.2 | Provide all O&M Staff, trained and certified as far as applicable. For security reasons, a 24 h/ 7 days a week staffing of security and maintenance shall be provided. The staffing concept and selected key employees shall be presented to the Employer for approval. | 1 |  |  |  | 1 | Second criteria / sentence is missing. | [5 empty] | 1 |  | Open
Tbea | JUE | Initial Inspection | O&M | General Requirements | 2.2.1 | familiarize himself with the specific plant equipment and specific maintenance requirements / training of staff | 1 |  |  |  | 1 | first criteria / sentence is missing. | [5 empty] | 1 |  | Open
Tbea | JUE | Initial Inspection | O&M | General Requirements | 2.2.2 | Maintenance routines, inspection check-lists, working files, | 1 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | JUE | Initial Inspection | O&M | General Requirements | 2.2.3 | coordinate with the Employer and keep him updated regarding his progress of preparation, status of construction, pending issues of Construction, Commissioning and testing. | 2 |  | 1 |  |  |  | Cannot be evaluated at this stage |  |  |  |  | 1 |  | Pass
Tbea | JUE | Bi-annual inspection | O&M | PV Generator | 2.3.1 | 100% visual inspection of modules regarding damage in spring | 1 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | JUE | Bi-annual inspection | O&M | PV Generator | 2.3.1 | Random visual inspection of modules regarding damage in autumn | 2 |  | 1 |  |  |  | Cannot be evaluated at this stage |  |  |  |  | 1 |  | Pass
Tbea | JUE | Bi-annual inspection | O&M | PV Generator | 2.3.1 | Random check of module clip with respect to loosening; if necessary replacement of clips (min. 10%, documentation of location, during 5 years inspection of whole PV plant) | 2 |  | 1 |  |  |  | Cannot be evaluated at this stage |  |  |  |  | 1 |  | Pass
Tbea | JUE | Bi-annual inspection | O&M | PV Generator | 2.3.1 | Random testing of the steadiness of the mounting foundation/system and random inspection regarding corrosion at substructure (min. 10%, documentation of location, during 10 years inspection of whole PV plant) | 1 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | JUE | Bi-annual inspection | O&M | PV Generator | 2.3.1 | Documentation of wear and tear of moving components, monitoring of dust intrusion and corrosion. | 2 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | JUE | Bi-annual inspection | O&M | PV Generator | 2.3.1 | Cleaning of sensors and switches | 1 |  | 1 |  |  |  | sensors shall be done by independent Meteo Station Operator |  |  |  |  | 1 |  | Pass
Tbea | JUE | Bi-annual inspection | O&M | PV Generator | 2.3.1 | Cleaning of all modules | 1 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | JUE | Bi-annual inspection | O&M | Inverter (100%) | 2.3.2 | Functional check of ventilator system of inverter station | 1 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | JUE | Bi-annual inspection | O&M | Inverter (100%) | 2.3.2 | Cleaning of the filter mats in the air leaks | 2 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | JUE | Bi-annual inspection | O&M | Inverter (100%) | 2.3.2 | Replacement of dirty filter mats | 2 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | JUE | Bi-annual inspection | O&M | Inverter (100%) | 2.3.2 | Inspection of the interior of the electrical cabinet regarding dust deposit, dirtiness, humidity, water penetration from outside. If necessary the cabinet has to be cleaned. | 1 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | JUE | Bi-annual inspection | O&M | Inverter (100%) | 2.3.2 | Testing of inverter features according to maintenance schedule of manufacturer. | 1 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | JUE | Bi-annual inspection | O&M | Inverter (100%) | 2.3.2 | Maintenance of inverters according to manufacturer's instruction. | 1 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | JUE | Bi-annual inspection | O&M | Monitoring | 2.3.3 | Functionality testing of the monitoring system | 3 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | JUE | Bi-annual inspection | O&M | Maintenance | 2.3.3 | Maintenance of all Power plant components according to manufacturer's instructions | 1 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | JUE | Main Annual Inspection | O&M | PV Generator | 2.4.1 | Visual inspection of all accessible cable trenches and cable trays regarding damage | 1 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | JUE | Main Annual Inspection | O&M | PV Generator | 2.4.1 | Visual inspection and random testing of string connector (min. 10% with Documentation of location , during 10 years testing of whole PV plant) | 1 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | JUE | Main Annual Inspection | O&M | PV Generator | 2.4.1 | Inspection of DC distribution box: Visual inspection of all clamps and degree of pollution. Testing of over-voltage protection | 1 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | JUE | Main Annual Inspection | O&M | PV Generator | 2.4.1 | Maintenance of sensors based on manufacturer’s instructions | 1 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | JUE | Main Annual Inspection | O&M | Inverter (100%) | 2.4.2 | Test of the internal miniature circuit breakers and power switch, test of emergency shut-off | 1 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | JUE | Main Annual Inspection | O&M | Inverter (100%) | 2.4.2 | Visual inspection of all fuses | 1 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | JUE | Main Annual Inspection | O&M | Inverter (100%) | 2.4.2 | Inspection of over-voltage protection and upstream fuses regarding external damage | 1 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | JUE | Main Annual Inspection | O&M | Inverter (100%) | 2.4.2 | Functional check of internal and external over- and under-voltage monitoring through operation of test terminal | 1 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | JUE | Main Annual Inspection | O&M | Inverter (100%) | 2.4.2 | Functional check of insulation monitoring | 1 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | JUE | Main Annual Inspection | O&M | Inverter (100%) | 2.4.2 | Check of control and auxiliary voltages | 2 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | JUE | Main Annual Inspection | O&M | Inverter (100%) | 2.4.2 | Check of the safety circuit for the interruption of the AC-grid protection in the case of failure (emergency shut-off, over-/ under-voltage, over temperature, etc.) based on the local conditions | 1 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | JUE | Main Annual Inspection | O&M | Inverter (100%) | 2.4.2 | Visual inspection of AC and DC clamps regarding tightness and colouring, tightening of clamps | 1 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | JUE | Main Annual Inspection | O&M | Inverter (100%) | 2.4.2 | Maintenance of inverters according to manufacturer instruction | 1 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | JUE | Main Annual Inspection | O&M | Roads | 2.4.3 | Visual inspection of roads within the PV plant shall be carried out to ascertain that these are maintained in good condition for the intended purpose. | 2 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | JUE | Main Annual Inspection | O&M | Substation and Transmission Line | 2.4.4 | Visual inspection of transformer and switchboard rooms and cleaning if necessary | 1 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | JUE | Main Annual Inspection | O&M | Substation and Transmission Line | 2.4.4 | Visual inspection of Transmission Line and report of damage to the grid operator | 2 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | JUE | Main Annual Inspection | O&M | Substation and Transmission Line | 2.4.4 | Maintenance of substation and transmission line according to manufacturer instruction | 1 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | JUE | Main Annual Inspection | O&M | Auxiliary system | 2.4.5 | Inspection of security system inclusive fence, all gates, all cameras etc. Random test of the fence fastening, if necessary retightening of the screws | 2 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | JUE | Main Annual Inspection | O&M | Auxiliary system | 2.4.5 | If existing: inspection of requirements out of the building permit | 2 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | JUE | Main Annual Inspection | O&M | Auxiliary system | 2.4.5 | Maintenance of all components according to manufacturer instruction | 1 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | JUE | Special inspection (every 4 years) | O&M | Specific Requirements | 2.5.1 | Measurement of inverters and generators according to recognized international standards and according to results from commissioning certificates (insulation, loop resistance, earthing, DC-open circuit voltage) | 2 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | JUE | Special inspection (every 4 years) | O&M | Specific Requirements | 2.5.1 | Protection systems of medium voltage switching panels of the stations | 1 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | JUE | Special inspection (every 4 years) | O&M | Specific Requirements | 2.5.1 | Oil check of transformers | 1 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | JUE | Special inspection (every 4 years) | O&M | Specific Requirements | 2.5.1 | Control of station equipment | 2 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | JUE | Deactivation | O&M | Allowed deactivation periods | 2.6.1 | Times with irradiation level < 300 W/m² | 2 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | JUE | Deactivation | O&M | Allowed deactivation periods | 2.6.1 | Approved by The Employer to ensure consideration of Employer's obligations | 2 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | JUE | Deactivation | O&M | Allowed deactivation periods | 2.6.1 | Approved from grid operator | 2 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | JUE | Deactivation | O&M | Specific Requirements | 2.6.2 | All deactivations during maintenance works shall be completely documented. | 2 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | JUE | Deactivation | O&M | Specific Requirements | 2.6.3 | Deactivation shall not be considered as permitted downtime. | 2 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | JUE | Change of Inspection and Maintenance Work procedures | O&M | Specific Requirements | 2.7 | work in accordance with all applicable laws | 2 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | JUE | Performance of maintenance and repair works | O&M | Specific Requirements | 2.8.1 | Corresponding regulations of the respective component manufacturer shall have to be followed during maintenance works | 1 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | JUE | Performance of maintenance and repair works | O&M | Specific Requirements | 2.8.2 | Report document for maintenance works (blanc sample requiered for bid) | 1 |  |  |  | 1 | blanc sample is missing | [5 empty] | 1 |  | Open
Tbea | JUE | Performance of maintenance and repair works | O&M | Specific Requirements | 2.8.3 | Observe and respect the maintenance and operation specifications of the manufacturer of the components | 3 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | JUE | Performance of maintenance and repair works | O&M | Specific Requirements | 2.8.4 | Observe and respect the local law, regulations and international PV standards. | 3 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | JUE | Performance of maintenance and repair works | O&M | Specific Requirements | 2.8.5 | During his work the Bidder shall be held responsible for the public safety of the PV plant | 2 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | JUE | On-site monitoring | O&M | Specific Requirements | 2.9.1 | Permanent (24/7) staffing of the Power Plant, consisting of security and O&M personnel. | 1 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | JUE | On-site monitoring | O&M | Specific Requirements | 2.9.2 | Bidder shall arrange service contracts with specialized sub-contractors | 2 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | JUE | On-site monitoring | O&M | Specific Requirements | 2.9.3 | All operational data shall be logged on-site in parallel to the remote data storage | 2 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | JUE | On-site monitoring | O&M | Specific Requirements | 2.9.4 | The data of irradiation sensors shall be monitored by an independent expert on a continuous basis | 2 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | JUE | Remote Supervision | O&M | Specific Requirements | 2.10.1 | On-call service provided for the Employer for availability outside business hours and during weekends (24/7). | 1 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | JUE | Remote Supervision | O&M | Specific Requirements | 2.10.2 | Any reductions in performance shall have to be logged. | 1 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | JUE | Remote Supervision | O&M | Specific Requirements | 2.10.3 | The data will comprise, apart from electrical parameters of the PV plant: currents, voltages, irradiation values, kind and period of reductions in performance such as curtailment by the grid operator | 2 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | JUE | Remote Supervision | O&M | Specific Requirements | 2.10.4 | The data shall present the status of the plant such as the performance ratio annual overview and the current feed-in power | 2 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | JUE | Remote Supervision | O&M | Specific Requirements | 2.10.5 | The remote supervision shall also control the operation of the PV plant. | 2 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | JUE | Remote Supervision | O&M | Specific Requirements | 2.10.6 | The remote supervision shall also include the taking of measures for removal of faults. | 2 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | JUE | Remote Supervision | O&M | Specific Requirements | 2.10.7 | The Bidder shall provide to the Employer permanent online access to the power plant control system for parallel monitoring | 1 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | JUE | Remote Supervision | O&M | Specific Requirements | 2.10.8 | Monthly / quarterly and annual reports based on the data of the remote supervision provided to the Employer 4 weeks after the last period of reporting at the latest. | 1 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | JUE | Remote Supervision | O&M | Specific Requirements | 2.10.9 | The fees for telephone connection and/or data transfer services are included in the annual remuneration. | 2 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | JUE | Reaction to Fault Messages / Response Times | O&M | Specific Requirements | 2.11.1 | Every fault message has to be registered in the monitoring software. According to the fault message, the Bidder shall issue a fault diagnosis within a response time of 2 hours (24/7) | 1 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | JUE | Reaction to Fault Messages / Response Times | O&M | Specific Requirements | 2.11.2 | profit relevant Fault Events: Downtime registration/ reasons/ repair/ in monthly report (blanc of monthly report?) | 1 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | JUE | Fault Management / Warranty defects | O&M | Specific Requirements | 2.12.1 | Fault Management: all handling and communication | 2 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | JUE | Fault Management / Warranty defects | O&M | Specific Requirements | 2.12.2 | Fault Management: Handling / correspondence with third parties | 2 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | JUE | Fault Management / Warranty defects | O&M | Specific Requirements | 2.12.3 | Fault Management = without repair works | 3 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | JUE | Fault Management / Warranty defects | O&M | Specific Requirements | 2.12.4 | Product warranties in favour of contractor / Bidder (responsible) to claim all warranties for at least 5 years | 1 |  |  |  | 1 | we cant find the first criteria. please explaine. | the first criteria is missing, please explaine. |  |  |  |  | 1 |  | Open
Tbea | JUE | Fault Management / Warranty defects | O&M | Specific Requirements | 2.12.5 | Operational defects, which are not considered as warranty defects - see repair works section below | 1 |  |  |  | 1 | rectified at the soonest occasion by TBEA? | Failure Response Time Model not not accepted |  |  |  |  | 1 |  | Open
Tbea | JUE | Fault Management / Warranty defects | O&M | Specific Requirements | 2.12.6 | All defects shall be documented within the same day of detection, | 2 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | JUE | Fault Calls | O&M | Specific Requirements | 2.13.1 | The scope of service shall include any working times for all fault calls including travelling times and costs. | 1 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | JUE | Fault Calls | O&M | Specific Requirements | 2.13.2 | The minimum response time in case of failure must meet the EPA requirements | 1 |  | 1 |  |  |  | EPA has to accept |  |  |  |  | 1 |  | Pass
Tbea | JUE | Fault Calls | O&M | Specific Requirements | 2.13.2 | --> Time Model: Response Times for Priorities 1-3 (12h / 24h / 1 week) | 1 |  |  |  | 1 | Please clarify compliance with rfp: rectified at the soonest occasion by TBEA? look at 2.12.5 | look at 2.12.5 |  |  |  |  | 1 |  | Open
Tbea | JUE | Fault Calls | O&M | Specific Requirements | 2.13.3 | failure time response does not match the response time of EPA >> failure time response does not match the response time of EPA | 3 |  | 1 |  |  |  | EPA has to accept |  |  |  |  | 1 |  | Pass
Tbea | JUE | Fault Calls | O&M | Specific Requirements | 2.13.4 | The fault call shall include the fault diagnosis on site as well as an immediate error correction if possible. The fault shall have to be corrected within the response time and, failing this, a diagnosis of the fault has to be effect indicating further measures. | 2 |  | 1 |  |  | General understanding: expressions like "shall", "shall be supplied with", "has to be", "must be" have the meaning of "will be delivered"? Please confirm. | (shall) have to --> or --> will be corrected? |  |  |  |  | 1 |  | Pass
Tbea | JUE | Fault Calls | O&M | Specific Requirements | 2.13.5 | Fault calls can be performed without prior consent of the Employer. | 3 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | JUE | Fault Calls | O&M | Specific Requirements | 2.13.6 | If the elimination of faults is not possible within the response time / and additional travelling, this is Repair Work | 3 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | JUE | Spare Parts and Tools | O&M | Specific Requirements | 2.14 | provide the necessary set of spare parts and maintenance tools as required to perform the services | 1 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | JUE | Spare Parts and Tools | O&M | Specific Requirements | 2.14.1 | cover all cost for supply and re-stocking of spare parts from his annual remuneration. | 1 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | JUE | Spare Parts and Tools | O&M | Specific Requirements | 2.14.2 | refill spare parts immediately after consumption | 2 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | JUE | Reduced Output of the Plant | O&M | Specific Requirements | 2.15 | Monthly comparison of the specific performance of all measuring channels among each other. 5% reduced output results in general check of all the channels and shall be documented. | 1 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | JUE | Reduced Output of the Plant | O&M | Specific Requirements | 2.15.1 | Identified reduced output shall be justified. Reduced output shall be recovered and liquidated damages determined. | 1 |  | 1 |  |  |  | liquidated --> means --> performance |  |  |  |  | 1 |  | Pass
Tbea | JUE | Repair time and cost | O&M | Specific Requirements | 2.16 | Repair times are considered as part of the availability guaranty of the Bidder. All cost of repair shall be part of the Bidders annual remuneration. For the avoidance of doubt that includes any repairs due to lightening, theft and vandalism. | 1 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | JUE | Working Time | O&M | Specific Requirements | 2.17 | All working times of Bidders personnel shall be included in the Bidders annual remuneration. | 1 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | JUE | Approval | O&M | Specific Requirements | 2.18 | Extensive repairs have to be approved by the Employer. | 2 |  |  |  | 1 | please confirm: No exemptions are allowed | [5 empty] | 1 |  | Open
Tbea | JUE | Documentation | O&M | Specific Requirements | 2.19 | All repair works and compensations shall have to be documented and to be submitted to the Employer within two weeks. | 2 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | JUE | Inspection of Repair Works | O&M | Specific Requirements | 2.20 | The Employer can inspect the repair works within one month (30 days) after receiving the documentation | 2 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | JUE | Ground Maintenance | O&M | Specific Requirements | 2.21 | Ground maintenance shall include all procedures that are necessary to avoid module shading and an incorrect operation of the trackers. This shall include the levelling of sand drifts. Necessary switching operations shall be coordinated by the Bidder with responsible authorities | 2 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | JUE | Person in Control of PV plant | O&M | Specific Requirements | 2.22 | The Bidder shall propose an organigram for the O& M personnel with one main responsible | 2 |  |  |  | 1 | "and shall be approved by the Employer. Any replacement or substitute of this person shall be subject to approval by the Employer." we can not find. Please confirm. | [5 empty] | 1 |  | Open
Tbea | JUE | Reporting | O&M | Specific Requirements | 2.23 | The Bidder shall deliver to the Employer regular reports on monthly, quarterly and annual basis. | 1 |  | 1 | [8 empty] | 1 |  | Pass
Juwi | JUE | Scope of the Bid | O&M | General Requirements | 2.1.2 | Responsibility to keep Performance Ratio and Availability at highest levels | 1 |  |  |  | 1 | L | missing |  |  |  |  | 1 |  | Open
Juwi | JUE | Scope of the Bid | O&M | General Requirements | 2.1.2 | Corrective maintenance with guaranteed response times | 1 |  | 1 | [8 empty] | 1 |  | Pass
Juwi | JUE | Scope of the Bid | O&M | General Requirements | 2.1.2 | Daily, monthly and yearly performance and production reporting | 1 |  |  |  | 1 | L | not completely described |  |  |  |  | 1 |  | Open
Juwi | JUE | Scope of the Bid | O&M | General Requirements | 2.1.2 | Operation of the Plant (including 24/7 presence of O&M and security staff on the project site). | 1 |  |  |  | 1 |  | only day time |  |  |  |  | 1 |  | Open
Juwi | JUE | Scope of the Bid | O&M | General Requirements | 2.1.2 | Cleaning of the Plant, preventive and corrective maintenance of the civil works and the fences. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing |  |  |  |  | 1 |  | Open
Juwi | JUE | Scope of the Bid | O&M | General Requirements | 2.1.2 | Cleaning of Modules and irradiation sensors to prevent dust accumulation to undesirable level. | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | additional bid for cleaning can be issued is required!! |  |  |  |  | 1 |  | Open
Juwi | JUE | Scope of the Bid | O&M | General Requirements | 2.1.2 | Optimal level of SCADA monitoring | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing |  |  |  |  | 1 |  | Open
Juwi | JUE | Scope of the Bid | O&M | General Requirements | 2.1.2 | Coordination and compliance with NTDC requirements | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing |  |  |  |  | 1 |  | Open
Juwi | JUE | Scope of the Bid | O&M | General Requirements | 2.1.2 | Performance variance analysis of the module strings and inverters | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing |  |  |  |  | 1 |  | Open
Juwi | JUE | Scope of the Bid | O&M | General Requirements | 2.1.2 | Periodic maintenance of inverter, transformer, combiner boxes etc., according manufacturer's requirements | 1 |  |  |  | 1 | according manufacturer's requirements is confirmable | missing |  |  |  |  | 1 |  | Open
Juwi | JUE | Scope of the Bid | O&M | General Requirements | 2.1.2 | Scheduled maintenance routines: e.g., inspections of modules with polarized sunglasses to check for discolouration, the first signs of de-lamination, loose wires in the electronics, corrosion of mounting structures, erosion | 1 |  | 1 | [8 empty] | 1 |  | Pass
Juwi | JUE | Scope of the Bid | O&M | General Requirements | 2.1.2 | Warranties and insurance policies should be assignable/transferrable to the Employer in case it decides to take over the O&M | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing |  |  |  |  | 1 |  | Open
Juwi | JUE | Scope of the Bid | O&M | General Requirements | 2.1.2 | Provide all O&M Staff, trained and certified as far as applicable. For security reasons, a 24 h/ 7 days a week staffing of security and maintenance shall be provided. The staffing concept and selected key employees shall be presented to the Employer for approval. | 1 | Schedule F 1.1 |  |  | 1 | 5 days or 24/7 ? | additional |  |  |  |  | 1 |  | Open
Juwi | JUE | Initial Inspection | O&M | General Requirements | 2.2.1 | familiarize himself with the specific plant equipment and specific maintenance requirements / training of staff | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing |  |  |  |  | 1 |  | Open
Juwi | JUE | Initial Inspection | O&M | General Requirements | 2.2.2 | Maintenance routines, inspection check-lists, working files, | 1 |  | 1 | [8 empty] | 1 |  | Pass
Juwi | JUE | Bi-annual inspection | O&M | PV Generator | 2.3.1 | 100% visual inspection of modules regarding damage in spring | 1 |  |  |  | 1 | 100% visual inspection of modules regarding damage in spring is confirmable | [5 empty] | 1 |  | Open
Juwi | JUE | Bi-annual inspection | O&M | PV Generator | 2.3.1 | Random testing of the steadiness of the mounting foundation/system and random inspection regarding corrosion at substructure (min. 10%, documentation of location, during 10 years inspection of whole PV plant) | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing |  |  |  |  | 1 |  | Open
Juwi | JUE | Bi-annual inspection | O&M | PV Generator | 2.3.1 | Cleaning of sensors and switches | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | sensors shall be done by independent Meteo Station Operator |  |  |  |  | 1 |  | Open
Juwi | JUE | Bi-annual inspection | O&M | PV Generator | 2.3.1 | Cleaning of all modules | 1 |  |  |  | 1 | additional bid for cleaning can be issued is required!! | additional bid for cleaning can be issued |  |  |  |  | 1 |  | Open
Juwi | JUE | Bi-annual inspection | O&M | Inverter (100%) | 2.3.2 | Functional check of ventilator system of inverter station | 1 |  | 1 | [8 empty] | 1 |  | Pass
Juwi | JUE | Bi-annual inspection | O&M | Inverter (100%) | 2.3.2 | Inspection of the interior of the electrical cabinet regarding dust deposit, dirtiness, humidity, water penetration from outside. If necessary the cabinet has to be cleaned. | 1 |  | 1 | [8 empty] | 1 |  | Pass
Juwi | JUE | Bi-annual inspection | O&M | Inverter (100%) | 2.3.2 | Testing of inverter features according to maintenance schedule of manufacturer. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | L according manufacturer's instruction is confirmable |  |  |  |  | 1 |  | Open
Juwi | JUE | Bi-annual inspection | O&M | Inverter (100%) | 2.3.2 | Maintenance of inverters according to manufacturer's instruction. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | L according manufacturer's instruction is confirmable |  |  |  |  | 1 |  | Open
Juwi | JUE | Bi-annual inspection | O&M | Maintenance | 2.3.3 | Maintenance of all Power plant components according to manufacturer's instructions | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | L according manufacturer's instruction is confirmable |  |  |  |  | 1 |  | Open
Juwi | JUE | Main Annual Inspection | O&M | PV Generator | 2.4.1 | Visual inspection of all accessible cable trenches and cable trays regarding damage | 1 |  | 1 | [8 empty] | 1 |  | Pass
Juwi | JUE | Main Annual Inspection | O&M | PV Generator | 2.4.1 | Visual inspection and random testing of string connector (min. 10% with Documentation of location , during 10 years testing of whole PV plant) | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | not completely described |  |  |  |  | 1 |  | Open
Juwi | JUE | Main Annual Inspection | O&M | PV Generator | 2.4.1 | Inspection of DC distribution box: Visual inspection of all clamps and degree of pollution. Testing of over-voltage protection | 1 |  | 1 | [8 empty] | 1 |  | Pass
Juwi | JUE | Main Annual Inspection | O&M | PV Generator | 2.4.1 | Maintenance of sensors based on manufacturer’s instructions | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | L according manufacturer's instruction is confirmable |  |  |  |  | 1 |  | Open
Juwi | JUE | Main Annual Inspection | O&M | Inverter (100%) | 2.4.2 | Test of the internal miniature circuit breakers and power switch, test of emergency shut-off | 1 |  | 1 | [8 empty] | 1 |  | Pass
Juwi | JUE | Main Annual Inspection | O&M | Inverter (100%) | 2.4.2 | Visual inspection of all fuses | 1 |  |  |  | 1 |  | missing |  |  |  |  | 1 |  | Open
Juwi | JUE | Main Annual Inspection | O&M | Inverter (100%) | 2.4.2 | Inspection of over-voltage protection and upstream fuses regarding external damage | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | not completely described |  |  |  |  | 1 |  | Open
Juwi | JUE | Main Annual Inspection | O&M | Inverter (100%) | 2.4.2 | Functional check of internal and external over- and under-voltage monitoring through operation of test terminal | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | not completely described |  |  |  |  | 1 |  | Open
Juwi | JUE | Main Annual Inspection | O&M | Inverter (100%) | 2.4.2 | Functional check of insulation monitoring | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | not completely described |  |  |  |  | 1 |  | Open
Juwi | JUE | Main Annual Inspection | O&M | Inverter (100%) | 2.4.2 | Check of the safety circuit for the interruption of the AC-grid protection in the case of failure (emergency shut-off, over-/ under-voltage, over temperature, etc.) based on the local conditions | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | not completely described |  |  |  |  | 1 |  | Open
Juwi | JUE | Main Annual Inspection | O&M | Inverter (100%) | 2.4.2 | Visual inspection of AC and DC clamps regarding tightness and colouring, tightening of clamps | 1 |  | 1 |  |  | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | [5 empty] | 1 |  | Pass
Juwi | JUE | Main Annual Inspection | O&M | Inverter (100%) | 2.4.2 | Maintenance of inverters according to manufacturer instruction | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing |  |  |  |  | 1 |  | Open
Juwi | JUE | Main Annual Inspection | O&M | Substation and Transmission Line | 2.4.4 | Visual inspection of transformer and switchboard rooms and cleaning if necessary | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing |  |  |  |  | 1 |  | Open
Juwi | JUE | Main Annual Inspection | O&M | Substation and Transmission Line | 2.4.4 | Maintenance of substation and transmission line according to manufacturer instruction | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing |  |  |  |  | 1 |  | Open
Juwi | JUE | Main Annual Inspection | O&M | Auxiliary system | 2.4.5 | Maintenance of all components according to manufacturer instruction | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing |  |  |  |  | 1 |  | Open
Juwi | JUE | Special inspection (every 4 years) | O&M | Specific Requirements | 2.5.1 | Protection systems of medium voltage switching panels of the stations | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing |  |  |  |  | 1 |  | Open
Juwi | JUE | Special inspection (every 4 years) | O&M | Specific Requirements | 2.5.1 | Oil check of transformers | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing |  |  |  |  | 1 |  | Open
Juwi | JUE | Performance of maintenance and repair works | O&M | Specific Requirements | 2.8.1 | Corresponding regulations of the respective component manufacturer shall have to be followed during maintenance works | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing |  |  |  |  | 1 |  | Open
Juwi | JUE | Performance of maintenance and repair works | O&M | Specific Requirements | 2.8.2 | Report document for maintenance works (blanc sample requiered for bid) | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | Report document for maintenance works is missing |  |  |  |  | 1 |  | Open
Juwi | JUE | On-site monitoring | O&M | Specific Requirements | 2.9.1 | Permanent (24/7) staffing of the Power Plant, consisting of security and O&M personnel. | 1 |  |  |  | 1 | Unclear: We do not understand your proposal, please detail your proposal. Especially confirm that you are compliant with our requested criteria. | [5 empty] | 1 |  | Open
Juwi | JUE | Remote Supervision | O&M | Specific Requirements | 2.10.1 | On-call service provided for the Employer for availability outside business hours and during weekends (24/7). | 1 |  |  |  | 1 | Unclear: We do not understand your proposal, please detail your proposal. Especially confirm that you are compliant with our requested criteria. | [5 empty] | 1 |  | Open
Juwi | JUE | Remote Supervision | O&M | Specific Requirements | 2.10.2 | Any reductions in performance shall have to be logged. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing |  |  |  |  | 1 |  | Open
Juwi | JUE | Remote Supervision | O&M | Specific Requirements | 2.10.7 | The Bidder shall provide to the Employer permanent online access to the power plant control system for parallel monitoring | 1 |  | 1 | [8 empty] | 1 |  | Pass
Juwi | JUE | Remote Supervision | O&M | Specific Requirements | 2.10.8 | Monthly / quarterly and annual reports based on the data of the remote supervision provided to the Employer 4 weeks after the last period of reporting at the latest. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing |  |  |  |  | 1 |  | Open
Juwi | JUE | Reaction to Fault Messages / Response Times | O&M | Specific Requirements | 2.11.1 | Every fault message has to be registered in the monitoring software. According to the fault message, the Bidder shall issue a fault diagnosis within a response time of 2 hours (24/7) | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing |  |  |  |  | 1 |  | Open
Juwi | JUE | Reaction to Fault Messages / Response Times | O&M | Specific Requirements | 2.11.2 | profit relevant Fault Events: Downtime registration/ reasons/ repair/ in monthly report (blanc of monthly report?) | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing |  |  |  |  | 1 |  | Open
Juwi | JUE | Fault Management / Warranty defects | O&M | Specific Requirements | 2.12.4 | Product warranties in favour of contractor / Bidder (responsible) to claim all warranties for at least 5 years | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing |  |  |  |  | 1 |  | Open
Juwi | JUE | Fault Management / Warranty defects | O&M | Specific Requirements | 2.12.5 | Operational defects, which are not considered as warranty defects - see repair works section below | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | Failure Response Time Model not not accepted |  |  |  |  | 1 |  | Open
Juwi | JUE | Fault Calls | O&M | Specific Requirements | 2.13.1 | The scope of service shall include any working times for all fault calls including travelling times and costs. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing |  |  |  |  | 1 |  | Open
Juwi | JUE | Fault Calls | O&M | Specific Requirements | 2.13.2 | The minimum response time in case of failure must meet the EPA requirements | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing |  |  |  |  | 1 |  | Open
Juwi | JUE | Fault Calls | O&M | Specific Requirements | 2.13.2 | --> Time Model: Response Times for Priorities 1-3 (12h / 24h / 1 week) | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | look at 2.12.5 |  |  |  |  | 1 |  | Open
Juwi | JUE | Spare Parts and Tools | O&M | Specific Requirements | 2.14 | provide the necessary set of spare parts and maintenance tools as required to perform the services | 1 |  | 1 | [8 empty] | 1 |  | Pass
Juwi | JUE | Spare Parts and Tools | O&M | Specific Requirements | 2.14.1 | cover all cost for supply and re-stocking of spare parts from his annual remuneration. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing |  |  |  |  | 1 |  | Open
Juwi | JUE | Reduced Output of the Plant | O&M | Specific Requirements | 2.15 | Monthly comparison of the specific performance of all measuring channels among each other. 5% reduced output results in general check of all the channels and shall be documented. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing |  |  |  |  | 1 |  | Open
Juwi | JUE | Reduced Output of the Plant | O&M | Specific Requirements | 2.15.1 | Identified reduced output shall be justified. Reduced output shall be recovered and liquidated damages determined. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing liquidated --> means --> performance |  |  |  |  | 1 |  | Open
Juwi | JUE | Repair time and cost | O&M | Specific Requirements | 2.16 | Repair times are considered as part of the availability guaranty of the Bidder. All cost of repair shall be part of the Bidders annual remuneration. For the avoidance of doubt that includes any repairs due to lightening, theft and vandalism. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing |  |  |  |  | 1 |  | Open
Juwi | JUE | Working Time | O&M | Specific Requirements | 2.17 | All working times of Bidders personnel shall be included in the Bidders annual remuneration. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing |  |  |  |  | 1 |  | Open
Juwi | JUE | Reporting | O&M | Specific Requirements | 2.23 | The Bidder shall deliver to the Employer regular reports on monthly, quarterly and annual basis. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing |  |  |  |  | 1 |  | Open
Tbea | JBU | AC Cabling | AC Cabling | Design factors to be provided | 1.19.1 | AC cable shall be of Copper. Rated voltage, nominal voltage between phase and neutral and nominal voltage between phases to be specified by the Bidder | 1 |  |  |  | 1 | General understanding: expressions like "shall", "shall be supplied with", "has to be", "must be" have the meaning of "will be delivered"? Please confirm. |  |  |  | G | General understanding: expressions like "shall", "shall be supplied with", "has to be", "must be" have the meaning of "will be delivered"? Please confirm. | 1 |  | Open
Tbea | JBU | AC Cabling | AC Cabling | Design factors to be provided | 1.19.1 | Appropriate sizing to minimise voltage drop and losses | 1 |  |  |  | 1 | General understanding: expressions like "shall", "shall be supplied with", "has to be", "must be" have the meaning of "will be delivered"? Please confirm. |  | What is the appropriate size? | leeway to allow MPP tracking when module voltage drops. At least 10%. Ralf, ist Vital kriterium. | G | General understanding: expressions like "shall", "shall be supplied with", "has to be", "must be" have the meaning of "will be delivered"? Please confirm. | 1 |  | Open
Tbea | JBU | AC Cabling | AC Cabling | Design factors to be provided | 1.19.1 | Lifetime longer than 25 years | 1 |  |  |  | 1 | General understanding: expressions like "shall", "shall be supplied with", "has to be", "must be" have the meaning of "will be delivered"? Please confirm. |  |  |  | G | General understanding: expressions like "shall", "shall be supplied with", "has to be", "must be" have the meaning of "will be delivered"? Please confirm. | 1 |  | Open
Tbea | JBU | AC Cabling | AC Cabling | Design factors to be provided | 1.19.1 | Rated voltage | 1 |  |  |  | 1 | General understanding: expressions like "shall", "shall be supplied with", "has to be", "must be" have the meaning of "will be delivered"? Please confirm. |  |  |  | G | General understanding: expressions like "shall", "shall be supplied with", "has to be", "must be" have the meaning of "will be delivered"? Please confirm. | 1 |  | Open
Tbea | JBU | AC Cabling | AC Cabling | Design factors to be provided | 1.19.1 | Bending radius | 1 |  |  |  | 1 | General understanding: expressions like "shall", "shall be supplied with", "has to be", "must be" have the meaning of "will be delivered"? Please confirm. |  |  |  | G | General understanding: expressions like "shall", "shall be supplied with", "has to be", "must be" have the meaning of "will be delivered"? Please confirm. | 1 |  | Open
Tbea | JBU | AC Cabling | AC Cabling | Design factors to be provided | 1.19.1 | Cables shall be suitable for the environmental conditions at the project site, including UV protection (The Bidder shall provide certification from manufacturer) | 1 |  |  |  | 1 | General understanding: expressions like "shall", "shall be supplied with", "has to be", "must be" have the meaning of "will be delivered"? Please confirm. |  |  |  | G | General understanding: expressions like "shall", "shall be supplied with", "has to be", "must be" have the meaning of "will be delivered"? Please confirm. | 1 |  | Open
Tbea | JBU | AC Cabling | AC Cabling | Design factors to be provided | 1.19.1 | Installation to be verified by measurement-protocols | 1 |  |  |  | 1 | General understanding: expressions like "shall", "shall be supplied with", "has to be", "must be" have the meaning of "will be delivered"? Please confirm. |  |  |  | G | General understanding: expressions like "shall", "shall be supplied with", "has to be", "must be" have the meaning of "will be delivered"? Please confirm. | 1 |  | Open
Tbea | JBU | AC Cabling | AC Cabling | Design factors to be provided | 1.19.1 | Cable installation shall ensure grounding and short-circuit protection | 1 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | JBU | AC Cabling | AC Cabling | Design factors to be provided | 1.19.1 | Sufficient and effective cable protection against attacks of rodents for any cabling underground or above is required | 1 |  |  |  | 1 | General understanding: expressions like "shall", "shall be supplied with", "has to be", "must be" have the meaning of "will be delivered"? Please confirm. |  |  |  | G | General understanding: expressions like "shall", "shall be supplied with", "has to be", "must be" have the meaning of "will be delivered"? Please confirm. | 1 |  | Open
Tbea | JBU | AC Cabling | AC Cabling | Standards | 1.19.2 | IEC 60502 | 1 |  |  |  | 1 | General understanding: expressions like "shall", "shall be supplied with", "has to be", "must be" have the meaning of "will be delivered"? Please confirm. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  | G | General understanding: expressions like "shall", "shall be supplied with", "has to be", "must be" have the meaning of "will be delivered"? Please confirm. | 1 |  | Open
Tbea | JBU | AC Cabling | AC Cabling | Standards | 1.19.2 | IEC 60364 | 1 |  |  |  | 1 | General understanding: expressions like "shall", "shall be supplied with", "has to be", "must be" have the meaning of "will be delivered"? Please confirm. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  | G | General understanding: expressions like "shall", "shall be supplied with", "has to be", "must be" have the meaning of "will be delivered"? Please confirm. | 1 |  | Open
Tbea | JBU | AC Cabling | AC Cabling | Standards | 1.19.2 | DIN-VDE-0276 | 1 |  |  |  | 1 | General understanding: expressions like "shall", "shall be supplied with", "has to be", "must be" have the meaning of "will be delivered"? Please confirm. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  | G | General understanding: expressions like "shall", "shall be supplied with", "has to be", "must be" have the meaning of "will be delivered"? Please confirm. | 1 |  | Open
Tbea | JBU | AC Cabling | AC Cabling | Standards | 1.19.2 | EN 60332-1-1 and EN 60332-2-1 | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Tbea | JBU | AC Cabling | AC Cabling | Specific Requirements | 1.19.3 | The runs of both the main DC and AC cables, in the System layout, should be adjusted to keep power losses below <1% at STC (Design calculations through cable loss simulation to be provided for review & comment). | 1 |  | 1 |  |  |  |  | Part of system design | Kategorie ? |  |  | 1 |  | Pass
Tbea | JBU | AC Combiner Box | AC Combiner Box | Design factors to be provided | 1.20.1 | Rated voltage | 1 |  | 1 |  |  |  | not applicable |  |  |  |  | 1 |  | Pass
Tbea | JBU | AC Combiner Box | AC Combiner Box | Design factors to be provided | 1.20.1 | Rated current | 1 |  | 1 |  |  |  | not applicable |  |  |  |  | 1 |  | Pass
Tbea | JBU | AC Combiner Box | AC Combiner Box | Design factors to be provided | 1.20.1 | Class 2 AC surge arrestor | 1 |  | 1 |  |  |  | not applicable |  |  |  |  | 1 |  | Pass
Tbea | JBU | AC Combiner Box | AC Combiner Box | Design factors to be provided | 1.20.1 | Load breaker switch of adequate size | 1 |  | 1 |  |  |  | not applicable |  |  |  |  | 1 |  | Pass
Tbea | JBU | AC Combiner Box | AC Combiner Box | Design factors to be provided | 1.20.1 | Flame test | 1 |  | 1 |  |  |  | not applicable |  |  |  |  | 1 |  | Pass
Tbea | JBU | AC Combiner Box | AC Combiner Box | Design factors to be provided | 1.20.1 | Waterproof test | 1 |  | 1 |  |  |  | not applicable |  |  |  |  | 1 |  | Pass
Tbea | JBU | AC Combiner Box | AC Combiner Box | Design factors to be provided | 1.20.1 | Operating temperature range | 1 |  | 1 |  |  |  | not applicable |  |  |  |  | 1 |  | Pass
Tbea | JBU | AC Combiner Box | AC Combiner Box | Design factors to be provided | 1.20.1 | Stripping length of the individual wire | 1 |  | 1 |  |  |  | not applicable |  |  |  |  | 1 |  | Pass
Tbea | JBU | AC Combiner Box | AC Combiner Box | Standards | 1.20.2 | IP 67 | 1 |  | 1 |  |  |  | not applicable |  |  |  |  | 1 |  | Pass
Tbea | JBU | AC Combiner Box | AC Combiner Box | Standards | 1.20.2 | EN 60529, DIN-VDE-0472 | 1 |  | 1 |  |  |  | not applicable | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  |  |  | 1 |  | Pass
Tbea | JBU | Step-up Transformers/MV Switchgear | Step-up Transformers/MV Switchgear | Guarantees | 1.21.1 | Compatibility with NTDC grid connection code must be ensured | 1 |  |  |  | 1 | General understanding: expressions like "shall", "shall be supplied with", "has to be", "must be" have the meaning of "will be delivered"? Please confirm. |  |  |  | G | General understanding: expressions like "shall", "shall be supplied with", "has to be", "must be" have the meaning of "will be delivered"? Please confirm. | 1 |  | Open
Tbea | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Design factors to be provided | 1.21.2 | 3-phase, double wound, continuously rated, oil-cooled, enclosed transformers, use of low loss core steel and close coupled copper windings | 1 | page 902 |  | 1 |  | Unclear: We do not understand your proposal, please detail your proposal. Especially confirm that you are compliant with our requested criteria. | dry type transformer according to datasheet |  |  | U |  | 1 | 1 | Fail
Tbea | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Design factors to be provided | 1.21.2 | Incoming terminals | 1 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Design factors to be provided | 1.21.2 | Outgoing terminals | 1 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Design factors to be provided | 1.21.2 | kVA rating | 1 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Design factors to be provided | 1.21.2 | Primary side voltage | 1 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Design factors to be provided | 1.21.2 | Secondary side voltage | 1 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Design factors to be provided | 1.21.2 | Insulation type | 1 |  |  |  | 1 | Unclear: We do not understand your proposal, please detail your proposal. Especially confirm that you are compliant with our requested criteria. | dry type transformer according to datasheet |  |  | U |  | 1 |  | Open
Tbea | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Design factors to be provided | 1.21.2 | Short-circuit impedance | 1 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Design factors to be provided | 1.21.2 | No-load losses | 1 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Design factors to be provided | 1.21.2 | Efficiency | 1 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Design factors to be provided | 1.21.2 | Operating temperature range | 1 | page 902 |  |  | 1 | Unclear: We do not understand your proposal, please detail your proposal. Especially confirm that you are compliant with our requested criteria. | -35°C up to +45°C |  |  | U |  | 1 |  | Open
Tbea | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Design factors to be provided | 1.21.2 | Maximum ambient temperature and altitude | 1 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Design factors to be provided | 1.21.2 | Humidity tolerance | 1 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Design factors to be provided | 1.21.2 | Cooling method | 1 | page 902 |  |  | 1 | Unclear: We do not understand your proposal, please detail your proposal. Especially confirm that you are compliant with our requested criteria. | dry type transformer according to datasheet |  |  | U |  | 1 |  | Open
Tbea | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Design factors to be provided | 1.21.2 | Protection system | 1 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Design factors to be provided | 1.21.2 | Operational data shall be logged in central operating system (e.g. oil temperature, oil level, pressure, Temperature probes (one per phase): Alarm and trip of cell etc.) | 1 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Standards | 1.21.3 | IEC 62446 | 1 |  | 1 |  |  |  |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  |  |  | 1 |  | Pass
Tbea | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Standards | 1.21.3 | IEC 60076 | 1 |  | 1 |  |  |  |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  |  |  | 1 |  | Pass
Tbea | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Standards | 1.21.3 | IEC 60085 | 1 |  | 1 |  |  |  |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  |  |  | 1 |  | Pass
Tbea | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Standards | 1.21.3 | IEC 60214 | 1 |  | 1 |  |  |  |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  |  |  | 1 |  | Pass
Tbea | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Standards | 1.21.3 | IEC 60137 | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  | C |  | 1 |  | Open
Tbea | JBU | Step-up Transformers/MV Switchgear | Due Diligence | Quality Assurance | 1.21.3 | Factory witness testing will be required for MV transformer and switchgear to be installed at this project. The cost of the due diligence to be carried by the Employer through an independent technical consultant will be taken over by the successful bidder up to an amount of 30,000 USD. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Tbea | JBU | Step-up Transformers/MV Switchgear | MV Switchgear | Specific Requirements | 1.21.4 | MV Switchgears shall be SF6 gas insulated or VCB (Vacuum circuit breaker). | 1 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | JBU | Step-up Transformers/MV Switchgear | MV Switchgear | Specific Requirements | 1.21.4 | The separating equipment shall be installed with visible disconnection (pivotable disconnectors). | 1 |  | 1 |  |  |  |  | Cannot be evaluated at this stage |  |  |  | 1 |  | Pass
Tbea | JBU | Step-up Transformers/MV Switchgear | MV Switchgear | Specific Requirements | 1.21.4 | Interlocks will also be mechanically interlocked between line MV switchgears. | 1 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | JBU | Step-up Transformers/MV Switchgear | MV Switchgear | Design factors to be provided | 1.21.4 | System nominal voltage | 1 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | JBU | Step-up Transformers/MV Switchgear | MV Switchgear | Design factors to be provided | 1.21.4 | System maximum voltage | 1 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | JBU | Step-up Transformers/MV Switchgear | MV Switchgear | Design factors to be provided | 1.21.4 | Rated lightning impulse voltage | 1 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | JBU | Step-up Transformers/MV Switchgear | MV Switchgear | Design factors to be provided | 1.21.4 | Rated power frequency withstand voltage | 1 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | JBU | Step-up Transformers/MV Switchgear | MV Switchgear | Design factors to be provided | 1.21.4 | Rated short circuit current | 1 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | JBU | Step-up Transformers/MV Switchgear | MV Switchgear | Standards | 1.21.5 | IEC 62446 | 1 |  | 1 |  |  |  |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  |  |  | 1 |  | Pass
Tbea | JBU | Step-up Transformers/MV Switchgear | MV Switchgear | Standards | 1.21.5 | IEC 62271-200 | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  | C |  | 1 |  | Open
Tbea | JBU | Step-up Transformers/MV Switchgear | MV Switchgear | Standards | 1.21.5 | IEC 60529 | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  | C |  | 1 |  | Open
Tbea | JBU | Inverter/Transformer Station | Inverter/Transformer Station | Specific Requirements | 1.22 | Bidder shall firmly specify the number of stations, manufacturer, capacity and type of equipment. | 1 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | JBU | Inverter/Transformer Station | Inverter/Transformer Station | Specific Requirements | 1.22 | All stations shall be equipped with fire and smoke detectors and alarm, connected to security and surveillance system | 1 |  |  |  | 1 | General understanding: expressions like "shall", "shall be supplied with", "has to be", "must be" have the meaning of "will be delivered"? Please confirm. |  |  |  | G | General understanding: expressions like "shall", "shall be supplied with", "has to be", "must be" have the meaning of "will be delivered"? Please confirm. | 1 |  | Open
Tbea | JBU | Inverter/Transformer Station | Inverter/Transformer Station | Specific Requirements | 1.22 | Fine sand filters shall be installed | 1 |  |  |  | 1 | General understanding: expressions like "shall", "shall be supplied with", "has to be", "must be" have the meaning of "will be delivered"? Please confirm. |  |  |  | G | General understanding: expressions like "shall", "shall be supplied with", "has to be", "must be" have the meaning of "will be delivered"? Please confirm. | 1 |  | Open
Tbea | JBU | Inverter/Transformer Station | Inverter/Transformer Station | Specific Requirements | 1.22 | The station shall enable the grounding of hardware and neutral will be left ground isolated | 1 |  |  |  | 1 | General understanding: expressions like "shall", "shall be supplied with", "has to be", "must be" have the meaning of "will be delivered"? Please confirm. |  |  |  | G | General understanding: expressions like "shall", "shall be supplied with", "has to be", "must be" have the meaning of "will be delivered"? Please confirm. | 1 |  | Open
Tbea | JBU | Inverter/Transformer Station | Inverter/Transformer Station | Specific Requirements | 1.22 | Every ten (10) or lesser number of stations shall be equipped with an earthing and short-circuiting equipment | 1 |  |  |  | 1 | General understanding: expressions like "shall", "shall be supplied with", "has to be", "must be" have the meaning of "will be delivered"? Please confirm. |  |  |  | G | General understanding: expressions like "shall", "shall be supplied with", "has to be", "must be" have the meaning of "will be delivered"? Please confirm. | 1 |  | Open
Zte | JBU | AC Cabling | AC Cabling | Design factors to be provided | 1.19.1 | AC cable shall be of Copper. Rated voltage, nominal voltage between phase and neutral and nominal voltage between phases to be specified by the Bidder | 1 | Technical Proposal of 100MW Solar Power Plant, page 85 |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | material is copper |  |  | C |  | 1 |  | Open
Zte | JBU | AC Cabling | AC Cabling | Design factors to be provided | 1.19.1 | Appropriate sizing to minimise voltage drop and losses | 1 | Technical Proposal of 100MW Solar Power Plant, page 114 | 1 |  |  |  | AC ohmic loss 0,1% | What is the appropriate size? | leeway to allow MPP tracking when module voltage drops. At least 10%. Ralf, ist Vital kriterium. |  |  | 1 |  | Pass
Zte | JBU | AC Cabling | AC Cabling | Design factors to be provided | 1.19.1 | Lifetime longer than 25 years | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | no datasheet |  |  | C |  | 1 |  | Open
Zte | JBU | AC Cabling | AC Cabling | Design factors to be provided | 1.19.1 | Rated voltage | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | no datasheet |  |  | C |  | 1 |  | Open
Zte | JBU | AC Cabling | AC Cabling | Design factors to be provided | 1.19.1 | Bending radius | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | no datasheet |  |  | C |  | 1 |  | Open
Zte | JBU | AC Cabling | AC Cabling | Design factors to be provided | 1.19.1 | Cables shall be suitable for the environmental conditions at the project site, including UV protection (The Bidder shall provide certification from manufacturer) | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | no datasheet |  |  | C |  | 1 |  | Open
Zte | JBU | AC Cabling | AC Cabling | Design factors to be provided | 1.19.1 | Installation to be verified by measurement-protocols | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | no datasheet |  |  | C |  | 1 |  | Open
Zte | JBU | AC Cabling | AC Cabling | Design factors to be provided | 1.19.1 | Cable installation shall ensure grounding and short-circuit protection | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | no datasheet |  |  | C |  | 1 |  | Open
Zte | JBU | AC Cabling | AC Cabling | Design factors to be provided | 1.19.1 | Sufficient and effective cable protection against attacks of rodents for any cabling underground or above is required | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | no datasheet |  |  | C |  | 1 |  | Open
Zte | JBU | AC Cabling | AC Cabling | Standards | 1.19.2 | IEC 60502 | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | no datasheet | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  | C |  | 1 |  | Open
Zte | JBU | AC Cabling | AC Cabling | Standards | 1.19.2 | IEC 60364 | 1 |  | 1 |  |  |  | no datasheet | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  |  |  | 1 |  | Pass
Zte | JBU | AC Cabling | AC Cabling | Standards | 1.19.2 | DIN-VDE-0276 | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | no datasheet | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  | C |  | 1 |  | Open
Zte | JBU | AC Cabling | AC Cabling | Standards | 1.19.2 | EN 60332-1-1 and EN 60332-2-1 | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | no datasheet | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  | C |  | 1 |  | Open
Zte | JBU | AC Cabling | AC Cabling | Specific Requirements | 1.19.3 | The runs of both the main DC and AC cables, in the System layout, should be adjusted to keep power losses below <1% at STC (Design calculations through cable loss simulation to be provided for review & comment). | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  | Part of system design | Kategorie ? | C |  | 1 |  | Open
Zte | JBU | AC Combiner Box | AC Combiner Box | Design factors to be provided | 1.20.1 | Rated voltage | 1 |  | 1 |  |  |  | not applicable |  |  |  |  | 1 |  | Pass
Zte | JBU | AC Combiner Box | AC Combiner Box | Design factors to be provided | 1.20.1 | Rated current | 1 |  | 1 |  |  |  | not applicable |  |  |  |  | 1 |  | Pass
Zte | JBU | AC Combiner Box | AC Combiner Box | Design factors to be provided | 1.20.1 | Class 2 AC surge arrestor | 1 |  | 1 |  |  |  | not applicable |  |  |  |  | 1 |  | Pass
Zte | JBU | AC Combiner Box | AC Combiner Box | Design factors to be provided | 1.20.1 | Load breaker switch of adequate size | 1 |  | 1 |  |  |  | not applicable |  |  |  |  | 1 |  | Pass
Zte | JBU | AC Combiner Box | AC Combiner Box | Design factors to be provided | 1.20.1 | Flame test | 1 |  | 1 |  |  |  | not applicable |  |  |  |  | 1 |  | Pass
Zte | JBU | AC Combiner Box | AC Combiner Box | Design factors to be provided | 1.20.1 | Waterproof test | 1 |  | 1 |  |  |  | not applicable |  |  |  |  | 1 |  | Pass
Zte | JBU | AC Combiner Box | AC Combiner Box | Design factors to be provided | 1.20.1 | Operating temperature range | 1 |  | 1 |  |  |  | not applicable |  |  |  |  | 1 |  | Pass
Zte | JBU | AC Combiner Box | AC Combiner Box | Design factors to be provided | 1.20.1 | Stripping length of the individual wire | 1 |  | 1 |  |  |  | not applicable |  |  |  |  | 1 |  | Pass
Zte | JBU | AC Combiner Box | AC Combiner Box | Standards | 1.20.2 | IP 67 | 1 |  | 1 |  |  |  | not applicable |  |  |  |  | 1 |  | Pass
Zte | JBU | AC Combiner Box | AC Combiner Box | Standards | 1.20.2 | EN 60529, DIN-VDE-0472 | 1 |  | 1 |  |  |  | not applicable | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  |  |  | 1 |  | Pass
Zte | JBU | Step-up Transformers/MV Switchgear | Step-up Transformers/MV Switchgear | Guarantees | 1.21.1 | Compatibility with NTDC grid connection code must be ensured | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  |  |  | C |  | 1 |  | Open
Zte | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Design factors to be provided | 1.21.2 | 3-phase, double wound, continuously rated, oil-cooled, enclosed transformers, use of low loss core steel and close coupled copper windings | 1 | Technical Proposal of 100MW Solar Power Plant, page 64 |  | 1 |  | Unclear: We do not understand your proposal, please detail your proposal. Especially confirm that you are compliant with our requested criteria. | dry type transformer will be used |  |  | U |  | 1 | 1 | Fail
Zte | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Design factors to be provided | 1.21.2 | Incoming terminals | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  |  |  | C |  | 1 |  | Open
Zte | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Design factors to be provided | 1.21.2 | Outgoing terminals | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  |  |  | C |  | 1 |  | Open
Zte | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Design factors to be provided | 1.21.2 | kVA rating | 1 |  | 1 | [8 empty] | 1 |  | Pass
Zte | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Design factors to be provided | 1.21.2 | Primary side voltage | 1 |  | 1 | [8 empty] | 1 |  | Pass
Zte | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Design factors to be provided | 1.21.2 | Secondary side voltage | 1 |  | 1 | [8 empty] | 1 |  | Pass
Zte | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Design factors to be provided | 1.21.2 | Insulation type | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | no datasheet |  |  | C |  | 1 |  | Open
Zte | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Design factors to be provided | 1.21.2 | Short-circuit impedance | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | no datasheet |  |  | C |  | 1 |  | Open
Zte | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Design factors to be provided | 1.21.2 | No-load losses | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | no datasheet |  |  | C |  | 1 |  | Open
Zte | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Design factors to be provided | 1.21.2 | Efficiency | 1 | Technical Proposal of 100MW Solar Power Plant, page 115 |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | no datasheet, combined AC and transformer loss is 1% according to Pvsyst simulation |  |  | C |  | 1 |  | Open
Zte | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Design factors to be provided | 1.21.2 | Operating temperature range | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | no datasheet |  |  | C |  | 1 |  | Open
Zte | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Design factors to be provided | 1.21.2 | Maximum ambient temperature and altitude | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | no datasheet |  |  | C |  | 1 |  | Open
Zte | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Design factors to be provided | 1.21.2 | Humidity tolerance | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | no datasheet |  |  | C |  | 1 |  | Open
Zte | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Design factors to be provided | 1.21.2 | Cooling method | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | no datasheet |  |  | C |  | 1 |  | Open
Zte | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Design factors to be provided | 1.21.2 | Protection system | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | no datasheet |  |  | C |  | 1 |  | Open
Zte | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Design factors to be provided | 1.21.2 | Operational data shall be logged in central operating system (e.g. oil temperature, oil level, pressure, Temperature probes (one per phase): Alarm and trip of cell etc.) | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | no datasheet |  |  | C |  | 1 |  | Open
Zte | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Standards | 1.21.3 | IEC 62446 | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | no datasheet | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  | C |  | 1 |  | Open
Zte | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Standards | 1.21.3 | IEC 60076 | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | no datasheet | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  | C |  | 1 |  | Open
Zte | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Standards | 1.21.3 | IEC 60085 | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | no datasheet | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  | C |  | 1 |  | Open
Zte | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Standards | 1.21.3 | IEC 60214 | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | no datasheet | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  | C |  | 1 |  | Open
Zte | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Standards | 1.21.3 | IEC 60137 | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | no datasheet | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  | C |  | 1 |  | Open
Zte | JBU | Step-up Transformers/MV Switchgear | Due Diligence | Quality Assurance | 1.21.3 | Factory witness testing will be required for MV transformer and switchgear to be installed at this project. The cost of the due diligence to be carried by the Employer through an independent technical consultant will be taken over by the successful bidder up to an amount of 30,000 USD. | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  |  |  | C |  | 1 |  | Open
Zte | JBU | Step-up Transformers/MV Switchgear | MV Switchgear | Specific Requirements | 1.21.4 | MV Switchgears shall be SF6 gas insulated or VCB (Vacuum circuit breaker). | 1 |  | 1 | [8 empty] | 1 |  | Pass
Zte | JBU | Step-up Transformers/MV Switchgear | MV Switchgear | Specific Requirements | 1.21.4 | The separating equipment shall be installed with visible disconnection (pivotable disconnectors). | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  | Cannot be evaluated at this stage |  | C |  | 1 |  | Open
Zte | JBU | Step-up Transformers/MV Switchgear | MV Switchgear | Specific Requirements | 1.21.4 | Interlocks will also be mechanically interlocked between line MV switchgears. | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  |  |  | C |  | 1 |  | Open
Zte | JBU | Step-up Transformers/MV Switchgear | MV Switchgear | Design factors to be provided | 1.21.4 | System nominal voltage | 1 |  | 1 | [8 empty] | 1 |  | Pass
Zte | JBU | Step-up Transformers/MV Switchgear | MV Switchgear | Design factors to be provided | 1.21.4 | System maximum voltage | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  |  |  | C |  | 1 |  | Open
Zte | JBU | Step-up Transformers/MV Switchgear | MV Switchgear | Design factors to be provided | 1.21.4 | Rated lightning impulse voltage | 1 |  | 1 | [8 empty] | 1 |  | Pass
Zte | JBU | Step-up Transformers/MV Switchgear | MV Switchgear | Design factors to be provided | 1.21.4 | Rated power frequency withstand voltage | 1 |  | 1 | [8 empty] | 1 |  | Pass
Zte | JBU | Step-up Transformers/MV Switchgear | MV Switchgear | Design factors to be provided | 1.21.4 | Rated short circuit current | 1 |  | 1 | [8 empty] | 1 |  | Pass
Zte | JBU | Step-up Transformers/MV Switchgear | MV Switchgear | Standards | 1.21.5 | IEC 62446 | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  | C |  | 1 |  | Open
Zte | JBU | Step-up Transformers/MV Switchgear | MV Switchgear | Standards | 1.21.5 | IEC 62271-200 | 1 |  | 1 |  |  |  |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  |  |  | 1 |  | Pass
Zte | JBU | Step-up Transformers/MV Switchgear | MV Switchgear | Standards | 1.21.5 | IEC 60529 | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  | C |  | 1 |  | Open
Zte | JBU | Inverter/Transformer Station | Inverter/Transformer Station | Specific Requirements | 1.22 | Bidder shall firmly specify the number of stations, manufacturer, capacity and type of equipment. | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | no datasheet |  |  | C |  | 1 |  | Open
Zte | JBU | Inverter/Transformer Station | Inverter/Transformer Station | Specific Requirements | 1.22 | All stations shall be equipped with fire and smoke detectors and alarm, connected to security and surveillance system | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | no datasheet |  |  | C |  | 1 |  | Open
Zte | JBU | Inverter/Transformer Station | Inverter/Transformer Station | Specific Requirements | 1.22 | Fine sand filters shall be installed | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | no datasheet |  |  | C |  | 1 |  | Open
Zte | JBU | Inverter/Transformer Station | Inverter/Transformer Station | Specific Requirements | 1.22 | The station shall enable the grounding of hardware and neutral will be left ground isolated | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | no datasheet |  |  | C |  | 1 |  | Open
Zte | JBU | Inverter/Transformer Station | Inverter/Transformer Station | Specific Requirements | 1.22 | Every ten (10) or lesser number of stations shall be equipped with an earthing and short-circuiting equipment | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | no datasheet |  |  | C |  | 1 |  | Open
Juwi | JBU | AC Cabling | AC Cabling | Design factors to be provided | 1.19.1 | AC cable shall be of Copper. Rated voltage, nominal voltage between phase and neutral and nominal voltage between phases to be specified by the Bidder | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Juwi | JBU | AC Cabling | AC Cabling | Design factors to be provided | 1.19.1 | Appropriate sizing to minimise voltage drop and losses | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | What is the appropriate size? | leeway to allow MPP tracking when module voltage drops. At least 10%. Ralf, ist Vital kriterium. | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Juwi | JBU | AC Cabling | AC Cabling | Design factors to be provided | 1.19.1 | Lifetime longer than 25 years | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Juwi | JBU | AC Cabling | AC Cabling | Design factors to be provided | 1.19.1 | Rated voltage | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Juwi | JBU | AC Cabling | AC Cabling | Design factors to be provided | 1.19.1 | Bending radius | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Juwi | JBU | AC Cabling | AC Cabling | Design factors to be provided | 1.19.1 | Cables shall be suitable for the environmental conditions at the project site, including UV protection (The Bidder shall provide certification from manufacturer) | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Juwi | JBU | AC Cabling | AC Cabling | Design factors to be provided | 1.19.1 | Installation to be verified by measurement-protocols | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Juwi | JBU | AC Cabling | AC Cabling | Design factors to be provided | 1.19.1 | Cable installation shall ensure grounding and short-circuit protection | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Juwi | JBU | AC Cabling | AC Cabling | Design factors to be provided | 1.19.1 | Sufficient and effective cable protection against attacks of rodents for any cabling underground or above is required | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Juwi | JBU | AC Cabling | AC Cabling | Standards | 1.19.2 | IEC 60502 | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Juwi | JBU | AC Cabling | AC Cabling | Standards | 1.19.2 | IEC 60364 | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Juwi | JBU | AC Cabling | AC Cabling | Standards | 1.19.2 | DIN-VDE-0276 | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Juwi | JBU | AC Cabling | AC Cabling | Standards | 1.19.2 | EN 60332-1-1 and EN 60332-2-1 | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Juwi | JBU | AC Cabling | AC Cabling | Specific Requirements | 1.19.3 | The runs of both the main DC and AC cables, in the System layout, should be adjusted to keep power losses below <1% at STC (Design calculations through cable loss simulation to be provided for review & comment). | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Part of system design | Kategorie ? | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Juwi | JBU | AC Combiner Box | AC Combiner Box | Design factors to be provided | 1.20.1 | Rated voltage | 1 |  | 1 |  |  |  | not applicable |  |  |  |  | 1 |  | Pass
Juwi | JBU | AC Combiner Box | AC Combiner Box | Design factors to be provided | 1.20.1 | Rated current | 1 |  | 1 |  |  |  | not applicable |  |  |  |  | 1 |  | Pass
Juwi | JBU | AC Combiner Box | AC Combiner Box | Design factors to be provided | 1.20.1 | Class 2 AC surge arrestor | 1 |  | 1 |  |  |  | not applicable |  |  |  |  | 1 |  | Pass
Juwi | JBU | AC Combiner Box | AC Combiner Box | Design factors to be provided | 1.20.1 | Load breaker switch of adequate size | 1 |  | 1 |  |  |  | not applicable |  |  |  |  | 1 |  | Pass
Juwi | JBU | AC Combiner Box | AC Combiner Box | Design factors to be provided | 1.20.1 | Flame test | 1 |  | 1 |  |  |  | not applicable |  |  |  |  | 1 |  | Pass
Juwi | JBU | AC Combiner Box | AC Combiner Box | Design factors to be provided | 1.20.1 | Waterproof test | 1 |  | 1 |  |  |  | not applicable |  |  |  |  | 1 |  | Pass
Juwi | JBU | AC Combiner Box | AC Combiner Box | Design factors to be provided | 1.20.1 | Operating temperature range | 1 |  | 1 |  |  |  | not applicable |  |  |  |  | 1 |  | Pass
Juwi | JBU | AC Combiner Box | AC Combiner Box | Design factors to be provided | 1.20.1 | Stripping length of the individual wire | 1 |  | 1 |  |  |  | not applicable |  |  |  |  | 1 |  | Pass
Juwi | JBU | AC Combiner Box | AC Combiner Box | Standards | 1.20.2 | IP 67 | 1 |  | 1 |  |  |  | not applicable |  |  |  |  | 1 |  | Pass
Juwi | JBU | AC Combiner Box | AC Combiner Box | Standards | 1.20.2 | EN 60529, DIN-VDE-0472 | 1 |  | 1 |  |  |  | not applicable | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  |  |  | 1 |  | Pass
Juwi | JBU | Step-up Transformers/MV Switchgear | Step-up Transformers/MV Switchgear | Guarantees | 1.21.1 | Compatibility with NTDC grid connection code must be ensured | 1 |  |  |  | 1 |  | L |  |  |  |  | 1 |  | Open
Juwi | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Design factors to be provided | 1.21.2 | 3-phase, double wound, continuously rated, oil-cooled, enclosed transformers, use of low loss core steel and close coupled copper windings | 1 |  | 1 | [8 empty] | 1 |  | Pass
Juwi | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Design factors to be provided | 1.21.2 | Incoming terminals | 1 |  | 1 | [8 empty] | 1 |  | Pass
Juwi | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Design factors to be provided | 1.21.2 | Outgoing terminals | 1 |  | 1 | [8 empty] | 1 |  | Pass
Juwi | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Design factors to be provided | 1.21.2 | kVA rating | 1 |  | 1 | [8 empty] | 1 |  | Pass
Juwi | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Design factors to be provided | 1.21.2 | Primary side voltage | 1 |  | 1 | [8 empty] | 1 |  | Pass
Juwi | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Design factors to be provided | 1.21.2 | Secondary side voltage | 1 |  | 1 | [8 empty] | 1 |  | Pass
Juwi | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Design factors to be provided | 1.21.2 | Insulation type | 1 |  | 1 | [8 empty] | 1 |  | Pass
Juwi | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Design factors to be provided | 1.21.2 | Short-circuit impedance | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Juwi | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Design factors to be provided | 1.21.2 | No-load losses | 1 |  | 1 | [8 empty] | 1 |  | Pass
Juwi | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Design factors to be provided | 1.21.2 | Efficiency | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | only total eff. Inv+transformer, page 287 |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Juwi | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Design factors to be provided | 1.21.2 | Operating temperature range | 1 |  | 1 | [8 empty] | 1 |  | Pass
Juwi | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Design factors to be provided | 1.21.2 | Maximum ambient temperature and altitude | 1 |  | 1 | [8 empty] | 1 |  | Pass
Juwi | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Design factors to be provided | 1.21.2 | Humidity tolerance | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Juwi | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Design factors to be provided | 1.21.2 | Cooling method | 1 |  | 1 | [8 empty] | 1 |  | Pass
Juwi | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Design factors to be provided | 1.21.2 | Protection system | 1 |  | 1 | [8 empty] | 1 |  | Pass
Juwi | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Design factors to be provided | 1.21.2 | Operational data shall be logged in central operating system (e.g. oil temperature, oil level, pressure, Temperature probes (one per phase): Alarm and trip of cell etc.) | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  |  |  | C |  | 1 |  | Open
Juwi | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Standards | 1.21.3 | IEC 62446 | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Juwi | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Standards | 1.21.3 | IEC 60076 | 1 |  | 1 |  |  |  |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  |  |  | 1 |  | Pass
Juwi | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Standards | 1.21.3 | IEC 60085 | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  | C |  | 1 |  | Open
Juwi | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Standards | 1.21.3 | IEC 60214 | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  | C |  | 1 |  | Open
Juwi | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Standards | 1.21.3 | IEC 60137 | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  | C |  | 1 |  | Open
Juwi | JBU | Step-up Transformers/MV Switchgear | Due Diligence | Quality Assurance | 1.21.3 | Factory witness testing will be required for MV transformer and switchgear to be installed at this project. The cost of the due diligence to be carried by the Employer through an independent technical consultant will be taken over by the successful bidder up to an amount of 30,000 USD. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Juwi | JBU | Step-up Transformers/MV Switchgear | MV Switchgear | Specific Requirements | 1.21.4 | MV Switchgears shall be SF6 gas insulated or VCB (Vacuum circuit breaker). | 1 |  | 1 | [8 empty] | 1 |  | Pass
Juwi | JBU | Step-up Transformers/MV Switchgear | MV Switchgear | Specific Requirements | 1.21.4 | The separating equipment shall be installed with visible disconnection (pivotable disconnectors). | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  | Cannot be evaluated at this stage |  | C |  | 1 |  | Open
Juwi | JBU | Step-up Transformers/MV Switchgear | MV Switchgear | Specific Requirements | 1.21.4 | Interlocks will also be mechanically interlocked between line MV switchgears. | 1 |  | 1 | [8 empty] | 1 |  | Pass
Juwi | JBU | Step-up Transformers/MV Switchgear | MV Switchgear | Design factors to be provided | 1.21.4 | System nominal voltage | 1 |  | 1 | [8 empty] | 1 |  | Pass
Juwi | JBU | Step-up Transformers/MV Switchgear | MV Switchgear | Design factors to be provided | 1.21.4 | System maximum voltage | 1 |  | 1 | [8 empty] | 1 |  | Pass
Juwi | JBU | Step-up Transformers/MV Switchgear | MV Switchgear | Design factors to be provided | 1.21.4 | Rated lightning impulse voltage | 1 |  | 1 | [8 empty] | 1 |  | Pass
Juwi | JBU | Step-up Transformers/MV Switchgear | MV Switchgear | Design factors to be provided | 1.21.4 | Rated power frequency withstand voltage | 1 |  | 1 | [8 empty] | 1 |  | Pass
Juwi | JBU | Step-up Transformers/MV Switchgear | MV Switchgear | Design factors to be provided | 1.21.4 | Rated short circuit current | 1 |  | 1 | [8 empty] | 1 |  | Pass
Juwi | JBU | Step-up Transformers/MV Switchgear | MV Switchgear | Standards | 1.21.5 | IEC 62446 | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Juwi | JBU | Step-up Transformers/MV Switchgear | MV Switchgear | Standards | 1.21.5 | IEC 62271-200 | 1 |  | 1 |  |  |  |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  |  |  | 1 |  | Pass
Juwi | JBU | Step-up Transformers/MV Switchgear | MV Switchgear | Standards | 1.21.5 | IEC 60529 | 1 |  | 1 |  |  |  |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  |  |  | 1 |  | Pass
Juwi | JBU | Inverter/Transformer Station | Inverter/Transformer Station | Specific Requirements | 1.22 | Bidder shall firmly specify the number of stations, manufacturer, capacity and type of equipment. | 1 |  | 1 | [8 empty] | 1 |  | Pass
Juwi | JBU | Inverter/Transformer Station | Inverter/Transformer Station | Specific Requirements | 1.22 | All stations shall be equipped with fire and smoke detectors and alarm, connected to security and surveillance system | 1 |  |  |  | 1 | Unclear: We do not understand your proposal, please detail your proposal. Especially confirm that you are compliant with our requested criteria. |  |  |  | U |  | 1 |  | Open
Juwi | JBU | Inverter/Transformer Station | Inverter/Transformer Station | Specific Requirements | 1.22 | Fine sand filters shall be installed | 1 |  |  |  | 1 | Unclear: We do not understand your proposal, please detail your proposal. Especially confirm that you are compliant with our requested criteria. |  |  |  | U |  | 1 |  | Open
Juwi | JBU | Inverter/Transformer Station | Inverter/Transformer Station | Specific Requirements | 1.22 | The station shall enable the grounding of hardware and neutral will be left ground isolated | 1 |  |  |  | 1 | Unclear: We do not understand your proposal, please detail your proposal. Especially confirm that you are compliant with our requested criteria. |  |  |  | U |  | 1 |  | Open
Juwi | JBU | Inverter/Transformer Station | Inverter/Transformer Station | Specific Requirements | 1.22 | Every ten (10) or lesser number of stations shall be equipped with an earthing and short-circuiting equipment | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  |  |  | C |  | 1 |  | Open
Chint | JBU | AC Cabling | AC Cabling | Design factors to be provided | 1.19.1 | AC cable shall be of Copper. Rated voltage, nominal voltage between phase and neutral and nominal voltage between phases to be specified by the Bidder | 1 |  | 1 | [8 empty] | 1 |  | Pass
Chint | JBU | AC Cabling | AC Cabling | Design factors to be provided | 1.19.1 | Appropriate sizing to minimise voltage drop and losses | 1 |  | 1 |  |  |  |  | What is the appropriate size? | leeway to allow MPP tracking when module voltage drops. At least 10%. Ralf, ist Vital kriterium. |  |  | 1 |  | Pass
Chint | JBU | AC Cabling | AC Cabling | Design factors to be provided | 1.19.1 | Lifetime longer than 25 years | 1 |  | 1 | [8 empty] | 1 |  | Pass
Chint | JBU | AC Cabling | AC Cabling | Design factors to be provided | 1.19.1 | Rated voltage | 1 |  | 1 | [8 empty] | 1 |  | Pass
Chint | JBU | AC Cabling | AC Cabling | Design factors to be provided | 1.19.1 | Bending radius | 1 |  | 1 | [8 empty] | 1 |  | Pass
Chint | JBU | AC Cabling | AC Cabling | Design factors to be provided | 1.19.1 | Cables shall be suitable for the environmental conditions at the project site, including UV protection (The Bidder shall provide certification from manufacturer) | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Chint | JBU | AC Cabling | AC Cabling | Design factors to be provided | 1.19.1 | Installation to be verified by measurement-protocols | 1 |  | 1 | [8 empty] | 1 |  | Pass
Chint | JBU | AC Cabling | AC Cabling | Design factors to be provided | 1.19.1 | Cable installation shall ensure grounding and short-circuit protection | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Chint | JBU | AC Cabling | AC Cabling | Design factors to be provided | 1.19.1 | Sufficient and effective cable protection against attacks of rodents for any cabling underground or above is required | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Chint | JBU | AC Cabling | AC Cabling | Standards | 1.19.2 | IEC 60502 | 1 |  | 1 |  |  |  |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  |  |  | 1 |  | Pass
Chint | JBU | AC Cabling | AC Cabling | Standards | 1.19.2 | IEC 60364 | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Chint | JBU | AC Cabling | AC Cabling | Standards | 1.19.2 | DIN-VDE-0276 | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Chint | JBU | AC Cabling | AC Cabling | Standards | 1.19.2 | EN 60332-1-1 and EN 60332-2-1 | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Chint | JBU | AC Cabling | AC Cabling | Specific Requirements | 1.19.3 | The runs of both the main DC and AC cables, in the System layout, should be adjusted to keep power losses below <1% at STC (Design calculations through cable loss simulation to be provided for review & comment). | 1 |  | 1 |  |  |  |  | Part of system design | Kategorie ? |  |  | 1 |  | Pass
Chint | JBU | AC Combiner Box | AC Combiner Box | Design factors to be provided | 1.20.1 | Rated voltage | 1 |  | 1 |  |  |  | not applicable |  |  |  |  | 1 |  | Pass
Chint | JBU | AC Combiner Box | AC Combiner Box | Design factors to be provided | 1.20.1 | Rated current | 1 |  | 1 |  |  |  | not applicable |  |  |  |  | 1 |  | Pass
Chint | JBU | AC Combiner Box | AC Combiner Box | Design factors to be provided | 1.20.1 | Class 2 AC surge arrestor | 1 |  | 1 |  |  |  | not applicable |  |  |  |  | 1 |  | Pass
Chint | JBU | AC Combiner Box | AC Combiner Box | Design factors to be provided | 1.20.1 | Load breaker switch of adequate size | 1 |  | 1 |  |  |  | not applicable |  |  |  |  | 1 |  | Pass
Chint | JBU | AC Combiner Box | AC Combiner Box | Design factors to be provided | 1.20.1 | Flame test | 1 |  | 1 |  |  |  | not applicable |  |  |  |  | 1 |  | Pass
Chint | JBU | AC Combiner Box | AC Combiner Box | Design factors to be provided | 1.20.1 | Waterproof test | 1 |  | 1 |  |  |  | not applicable |  |  |  |  | 1 |  | Pass
Chint | JBU | AC Combiner Box | AC Combiner Box | Design factors to be provided | 1.20.1 | Operating temperature range | 1 |  | 1 |  |  |  | not applicable |  |  |  |  | 1 |  | Pass
Chint | JBU | AC Combiner Box | AC Combiner Box | Design factors to be provided | 1.20.1 | Stripping length of the individual wire | 1 |  | 1 |  |  |  | not applicable |  |  |  |  | 1 |  | Pass
Chint | JBU | AC Combiner Box | AC Combiner Box | Standards | 1.20.2 | IP 67 | 1 |  | 1 |  |  |  | not applicable |  |  |  |  | 1 |  | Pass
Chint | JBU | AC Combiner Box | AC Combiner Box | Standards | 1.20.2 | EN 60529, DIN-VDE-0472 | 1 |  | 1 |  |  |  | not applicable | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  |  |  | 1 |  | Pass
Chint | JBU | Step-up Transformers/MV Switchgear | Step-up Transformers/MV Switchgear | Guarantees | 1.21.1 | Compatibility with NTDC grid connection code must be ensured | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Chint | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Design factors to be provided | 1.21.2 | 3-phase, double wound, continuously rated, oil-cooled, enclosed transformers, use of low loss core steel and close coupled copper windings | 1 |  | 1 | [8 empty] | 1 |  | Pass
Chint | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Design factors to be provided | 1.21.2 | Incoming terminals | 1 |  | 1 | [8 empty] | 1 |  | Pass
Chint | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Design factors to be provided | 1.21.2 | Outgoing terminals | 1 |  | 1 | [8 empty] | 1 |  | Pass
Chint | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Design factors to be provided | 1.21.2 | kVA rating | 1 |  | 1 | [8 empty] | 1 |  | Pass
Chint | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Design factors to be provided | 1.21.2 | Primary side voltage | 1 |  | 1 | [8 empty] | 1 |  | Pass
Chint | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Design factors to be provided | 1.21.2 | Secondary side voltage | 1 |  | 1 | [8 empty] | 1 |  | Pass
Chint | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Design factors to be provided | 1.21.2 | Insulation type | 1 |  | 1 | [8 empty] | 1 |  | Pass
Chint | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Design factors to be provided | 1.21.2 | Short-circuit impedance | 1 |  | 1 | [8 empty] | 1 |  | Pass
Chint | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Design factors to be provided | 1.21.2 | No-load losses | 1 |  | 1 | [8 empty] | 1 |  | Pass
Chint | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Design factors to be provided | 1.21.2 | Efficiency | 1 |  | 1 | [8 empty] | 1 |  | Pass
Chint | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Design factors to be provided | 1.21.2 | Operating temperature range | 1 |  | 1 | [8 empty] | 1 |  | Pass
Chint | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Design factors to be provided | 1.21.2 | Maximum ambient temperature and altitude | 1 |  | 1 | [8 empty] | 1 |  | Pass
Chint | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Design factors to be provided | 1.21.2 | Humidity tolerance | 1 |  | 1 | [8 empty] | 1 |  | Pass
Chint | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Design factors to be provided | 1.21.2 | Cooling method | 1 |  | 1 | [8 empty] | 1 |  | Pass
Chint | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Design factors to be provided | 1.21.2 | Protection system | 1 |  | 1 | [8 empty] | 1 |  | Pass
Chint | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Design factors to be provided | 1.21.2 | Operational data shall be logged in central operating system (e.g. oil temperature, oil level, pressure, Temperature probes (one per phase): Alarm and trip of cell etc.) | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  |  |  | C |  | 1 |  | Open
Chint | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Standards | 1.21.3 | IEC 62446 | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  | C |  | 1 |  | Open
Chint | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Standards | 1.21.3 | IEC 60076 | 1 |  | 1 |  |  |  |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  |  |  | 1 |  | Pass
Chint | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Standards | 1.21.3 | IEC 60085 | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Chint | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Standards | 1.21.3 | IEC 60214 | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Chint | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Standards | 1.21.3 | IEC 60137 | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Chint | JBU | Step-up Transformers/MV Switchgear | Due Diligence | Quality Assurance | 1.21.3 | Factory witness testing will be required for MV transformer and switchgear to be installed at this project. The cost of the due diligence to be carried by the Employer through an independent technical consultant will be taken over by the successful bidder up to an amount of 30,000 USD. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Chint | JBU | Step-up Transformers/MV Switchgear | MV Switchgear | Specific Requirements | 1.21.4 | MV Switchgears shall be SF6 gas insulated or VCB (Vacuum circuit breaker). | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Chint | JBU | Step-up Transformers/MV Switchgear | MV Switchgear | Specific Requirements | 1.21.4 | The separating equipment shall be installed with visible disconnection (pivotable disconnectors). | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Cannot be evaluated at this stage |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Chint | JBU | Step-up Transformers/MV Switchgear | MV Switchgear | Specific Requirements | 1.21.4 | Interlocks will also be mechanically interlocked between line MV switchgears. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Chint | JBU | Step-up Transformers/MV Switchgear | MV Switchgear | Design factors to be provided | 1.21.4 | System nominal voltage | 1 |  | 1 | [8 empty] | 1 |  | Pass
Chint | JBU | Step-up Transformers/MV Switchgear | MV Switchgear | Design factors to be provided | 1.21.4 | System maximum voltage | 1 |  | 1 | [8 empty] | 1 |  | Pass
Chint | JBU | Step-up Transformers/MV Switchgear | MV Switchgear | Design factors to be provided | 1.21.4 | Rated lightning impulse voltage | 1 |  | 1 | [8 empty] | 1 |  | Pass
Chint | JBU | Step-up Transformers/MV Switchgear | MV Switchgear | Design factors to be provided | 1.21.4 | Rated power frequency withstand voltage | 1 |  | 1 | [8 empty] | 1 |  | Pass
Chint | JBU | Step-up Transformers/MV Switchgear | MV Switchgear | Design factors to be provided | 1.21.4 | Rated short circuit current | 1 |  | 1 | [8 empty] | 1 |  | Pass
Chint | JBU | Step-up Transformers/MV Switchgear | MV Switchgear | Standards | 1.21.5 | IEC 62446 | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Chint | JBU | Step-up Transformers/MV Switchgear | MV Switchgear | Standards | 1.21.5 | IEC 62271-200 | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Chint | JBU | Step-up Transformers/MV Switchgear | MV Switchgear | Standards | 1.21.5 | IEC 60529 | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Chint | JBU | Inverter/Transformer Station | Inverter/Transformer Station | Specific Requirements | 1.22 | Bidder shall firmly specify the number of stations, manufacturer, capacity and type of equipment. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Chint | JBU | Inverter/Transformer Station | Inverter/Transformer Station | Specific Requirements | 1.22 | All stations shall be equipped with fire and smoke detectors and alarm, connected to security and surveillance system | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Chint | JBU | Inverter/Transformer Station | Inverter/Transformer Station | Specific Requirements | 1.22 | Fine sand filters shall be installed | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Chint | JBU | Inverter/Transformer Station | Inverter/Transformer Station | Specific Requirements | 1.22 | The station shall enable the grounding of hardware and neutral will be left ground isolated | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Chint | JBU | Inverter/Transformer Station | Inverter/Transformer Station | Specific Requirements | 1.22 | Every ten (10) or lesser number of stations shall be equipped with an earthing and short-circuiting equipment | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Sumec | JBU | AC Cabling | AC Cabling | Design factors to be provided | 1.19.1 | AC cable shall be of Copper. Rated voltage, nominal voltage between phase and neutral and nominal voltage between phases to be specified by the Bidder | 1 |  | 1 | [8 empty] | 1 |  | Pass
Sumec | JBU | AC Cabling | AC Cabling | Design factors to be provided | 1.19.1 | Appropriate sizing to minimise voltage drop and losses | 1 |  | 1 |  |  |  |  | What is the appropriate size? | leeway to allow MPP tracking when module voltage drops. At least 10%. Ralf, ist Vital kriterium. |  |  | 1 |  | Pass
Sumec | JBU | AC Cabling | AC Cabling | Design factors to be provided | 1.19.1 | Lifetime longer than 25 years | 1 |  |  |  | 1 |  | L |  |  |  |  | 1 |  | Open
Sumec | JBU | AC Cabling | AC Cabling | Design factors to be provided | 1.19.1 | Rated voltage | 1 |  |  |  | 1 |  | L |  |  |  |  | 1 |  | Open
Sumec | JBU | AC Cabling | AC Cabling | Design factors to be provided | 1.19.1 | Bending radius | 1 |  |  |  | 1 |  | L |  |  |  |  | 1 |  | Open
Sumec | JBU | AC Cabling | AC Cabling | Design factors to be provided | 1.19.1 | Cables shall be suitable for the environmental conditions at the project site, including UV protection (The Bidder shall provide certification from manufacturer) | 1 |  |  |  | 1 |  | L |  |  |  |  | 1 |  | Open
Sumec | JBU | AC Cabling | AC Cabling | Design factors to be provided | 1.19.1 | Installation to be verified by measurement-protocols | 1 |  |  |  | 1 |  | L |  |  |  |  | 1 |  | Open
Sumec | JBU | AC Cabling | AC Cabling | Design factors to be provided | 1.19.1 | Cable installation shall ensure grounding and short-circuit protection | 1 |  |  |  | 1 |  | L |  |  |  |  | 1 |  | Open
Sumec | JBU | AC Cabling | AC Cabling | Design factors to be provided | 1.19.1 | Sufficient and effective cable protection against attacks of rodents for any cabling underground or above is required | 1 |  |  |  | 1 |  | L |  |  |  |  | 1 |  | Open
Sumec | JBU | AC Cabling | AC Cabling | Standards | 1.19.2 | IEC 60502 | 1 |  |  |  | 1 |  | L | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  |  |  | 1 |  | Open
Sumec | JBU | AC Cabling | AC Cabling | Standards | 1.19.2 | IEC 60364 | 1 |  |  |  | 1 |  | L | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  |  |  | 1 |  | Open
Sumec | JBU | AC Cabling | AC Cabling | Standards | 1.19.2 | DIN-VDE-0276 | 1 |  |  |  | 1 |  | L | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  |  |  | 1 |  | Open
Sumec | JBU | AC Cabling | AC Cabling | Standards | 1.19.2 | EN 60332-1-1 and EN 60332-2-1 | 1 |  |  |  | 1 |  | L | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  |  |  | 1 |  | Open
Sumec | JBU | AC Cabling | AC Cabling | Specific Requirements | 1.19.3 | The runs of both the main DC and AC cables, in the System layout, should be adjusted to keep power losses below <1% at STC (Design calculations through cable loss simulation to be provided for review & comment). | 1 |  |  |  | 1 |  | L | Part of system design | Kategorie ? |  |  | 1 |  | Open
Sumec | JBU | AC Combiner Box | AC Combiner Box | Design factors to be provided | 1.20.1 | Rated voltage | 1 |  | 1 |  |  |  | not applicable |  |  |  |  | 1 |  | Pass
Sumec | JBU | AC Combiner Box | AC Combiner Box | Design factors to be provided | 1.20.1 | Rated current | 1 |  | 1 |  |  |  | not applicable |  |  |  |  | 1 |  | Pass
Sumec | JBU | AC Combiner Box | AC Combiner Box | Design factors to be provided | 1.20.1 | Class 2 AC surge arrestor | 1 |  | 1 |  |  |  | not applicable |  |  |  |  | 1 |  | Pass
Sumec | JBU | AC Combiner Box | AC Combiner Box | Design factors to be provided | 1.20.1 | Load breaker switch of adequate size | 1 |  | 1 |  |  |  | not applicable |  |  |  |  | 1 |  | Pass
Sumec | JBU | AC Combiner Box | AC Combiner Box | Design factors to be provided | 1.20.1 | Flame test | 1 |  | 1 |  |  |  | not applicable |  |  |  |  | 1 |  | Pass
Sumec | JBU | AC Combiner Box | AC Combiner Box | Design factors to be provided | 1.20.1 | Waterproof test | 1 |  | 1 |  |  |  | not applicable |  |  |  |  | 1 |  | Pass
Sumec | JBU | AC Combiner Box | AC Combiner Box | Design factors to be provided | 1.20.1 | Operating temperature range | 1 |  | 1 |  |  |  | not applicable |  |  |  |  | 1 |  | Pass
Sumec | JBU | AC Combiner Box | AC Combiner Box | Design factors to be provided | 1.20.1 | Stripping length of the individual wire | 1 |  | 1 |  |  |  | not applicable |  |  |  |  | 1 |  | Pass
Sumec | JBU | AC Combiner Box | AC Combiner Box | Standards | 1.20.2 | IP 67 | 1 |  | 1 |  |  |  | not applicable |  |  |  |  | 1 |  | Pass
Sumec | JBU | AC Combiner Box | AC Combiner Box | Standards | 1.20.2 | EN 60529, DIN-VDE-0472 | 1 |  | 1 |  |  |  | not applicable | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  |  |  | 1 |  | Pass
Sumec | JBU | Step-up Transformers/MV Switchgear | Step-up Transformers/MV Switchgear | Guarantees | 1.21.1 | Compatibility with NTDC grid connection code must be ensured | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Sumec | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Design factors to be provided | 1.21.2 | 3-phase, double wound, continuously rated, oil-cooled, enclosed transformers, use of low loss core steel and close coupled copper windings | 1 |  | 1 | [8 empty] | 1 |  | Pass
Sumec | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Design factors to be provided | 1.21.2 | Incoming terminals | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Sumec | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Design factors to be provided | 1.21.2 | Outgoing terminals | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Sumec | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Design factors to be provided | 1.21.2 | kVA rating | 1 |  | 1 | [8 empty] | 1 |  | Pass
Sumec | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Design factors to be provided | 1.21.2 | Primary side voltage | 1 |  | 1 | [8 empty] | 1 |  | Pass
Sumec | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Design factors to be provided | 1.21.2 | Secondary side voltage | 1 |  | 1 | [8 empty] | 1 |  | Pass
Sumec | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Design factors to be provided | 1.21.2 | Insulation type | 1 |  | 1 | [8 empty] | 1 |  | Pass
Sumec | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Design factors to be provided | 1.21.2 | Short-circuit impedance | 1 |  | 1 | [8 empty] | 1 |  | Pass
Sumec | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Design factors to be provided | 1.21.2 | No-load losses | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Sumec | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Design factors to be provided | 1.21.2 | Efficiency | 1 | TECHNICAL OFFER-VOLUME I, page 295 | 1 |  |  |  | 2% of losses |  |  |  |  | 1 |  | Pass
Sumec | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Design factors to be provided | 1.21.2 | Operating temperature range | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Sumec | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Design factors to be provided | 1.21.2 | Maximum ambient temperature and altitude | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Sumec | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Design factors to be provided | 1.21.2 | Humidity tolerance | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Sumec | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Design factors to be provided | 1.21.2 | Cooling method | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Sumec | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Design factors to be provided | 1.21.2 | Protection system | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Sumec | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Design factors to be provided | 1.21.2 | Operational data shall be logged in central operating system (e.g. oil temperature, oil level, pressure, Temperature probes (one per phase): Alarm and trip of cell etc.) | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Sumec | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Standards | 1.21.3 | IEC 62446 | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Sumec | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Standards | 1.21.3 | IEC 60076 | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Sumec | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Standards | 1.21.3 | IEC 60085 | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Sumec | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Standards | 1.21.3 | IEC 60214 | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Sumec | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Standards | 1.21.3 | IEC 60137 | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Sumec | JBU | Step-up Transformers/MV Switchgear | Due Diligence | Quality Assurance | 1.21.3 | Factory witness testing will be required for MV transformer and switchgear to be installed at this project. The cost of the due diligence to be carried by the Employer through an independent technical consultant will be taken over by the successful bidder up to an amount of 30,000 USD. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Sumec | JBU | Step-up Transformers/MV Switchgear | MV Switchgear | Specific Requirements | 1.21.4 | MV Switchgears shall be SF6 gas insulated or VCB (Vacuum circuit breaker). | 1 |  | 1 | [8 empty] | 1 |  | Pass
Sumec | JBU | Step-up Transformers/MV Switchgear | MV Switchgear | Specific Requirements | 1.21.4 | The separating equipment shall be installed with visible disconnection (pivotable disconnectors). | 1 |  | 1 |  |  |  |  | Cannot be evaluated at this stage |  |  |  | 1 |  | Pass
Sumec | JBU | Step-up Transformers/MV Switchgear | MV Switchgear | Specific Requirements | 1.21.4 | Interlocks will also be mechanically interlocked between line MV switchgears. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Sumec | JBU | Step-up Transformers/MV Switchgear | MV Switchgear | Design factors to be provided | 1.21.4 | System nominal voltage | 1 |  | 1 | [8 empty] | 1 |  | Pass
Sumec | JBU | Step-up Transformers/MV Switchgear | MV Switchgear | Design factors to be provided | 1.21.4 | System maximum voltage | 1 |  | 1 | [8 empty] | 1 |  | Pass
Sumec | JBU | Step-up Transformers/MV Switchgear | MV Switchgear | Design factors to be provided | 1.21.4 | Rated lightning impulse voltage | 1 |  | 1 | [8 empty] | 1 |  | Pass
Sumec | JBU | Step-up Transformers/MV Switchgear | MV Switchgear | Design factors to be provided | 1.21.4 | Rated power frequency withstand voltage | 1 |  | 1 | [8 empty] | 1 |  | Pass
Sumec | JBU | Step-up Transformers/MV Switchgear | MV Switchgear | Design factors to be provided | 1.21.4 | Rated short circuit current | 1 |  | 1 | [8 empty] | 1 |  | Pass
Sumec | JBU | Step-up Transformers/MV Switchgear | MV Switchgear | Standards | 1.21.5 | IEC 62446 | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Sumec | JBU | Step-up Transformers/MV Switchgear | MV Switchgear | Standards | 1.21.5 | IEC 62271-200 | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Sumec | JBU | Step-up Transformers/MV Switchgear | MV Switchgear | Standards | 1.21.5 | IEC 60529 | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Sumec | JBU | Inverter/Transformer Station | Inverter/Transformer Station | Specific Requirements | 1.22 | Bidder shall firmly specify the number of stations, manufacturer, capacity and type of equipment. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Sumec | JBU | Inverter/Transformer Station | Inverter/Transformer Station | Specific Requirements | 1.22 | All stations shall be equipped with fire and smoke detectors and alarm, connected to security and surveillance system | 1 |  | 1 | [8 empty] | 1 |  | Pass
Sumec | JBU | Inverter/Transformer Station | Inverter/Transformer Station | Specific Requirements | 1.22 | Fine sand filters shall be installed | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Sumec | JBU | Inverter/Transformer Station | Inverter/Transformer Station | Specific Requirements | 1.22 | The station shall enable the grounding of hardware and neutral will be left ground isolated | 1 |  | 1 | [8 empty] | 1 |  | Pass
Sumec | JBU | Inverter/Transformer Station | Inverter/Transformer Station | Specific Requirements | 1.22 | Every ten (10) or lesser number of stations shall be equipped with an earthing and short-circuiting equipment | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Juwi | JBS | System PR Specification | System PR | O&M | 1.5.2 | The target PR specification at the time of commissioning the System is equal to or greater than 0.75 (75%). | 1 | Page 392-395 | 1 |  |  |  | 74.8% |  |  |  |  | 1 |  | Pass
Juwi | JBS | System PR Specification | System PR | Losses included in PR calculation | 1.5.4 | Module Array (temperature dependence, soiling, low light inefficiency, shading, mismatches in array) | 1 | Page 392-395 | 1 |  |  |  |  | We don’t understand the question. Kindly clarify. | we want to see these losses specified. Thos need to be aligned with O+M Startegy and System composition |  |  | 1 |  | Pass
Juwi | JBS | System PR Specification | System PR | Losses included in PR calculation | 1.5.4 | Inverter (operating efficiency, operating voltage variations, power/voltage levels) | 1 | Page 392-395 | 1 |  |  |  |  | We don’t understand the question. Kindly clarify. | see relevant chapter 1.5.4 List of technical losses that make the PR |  |  | 1 |  | Pass
Juwi | JBS | System PR Specification | System PR | Losses included in PR calculation | 1.5.4 | Transformer losses | 1 | Page 392-395 | 1 |  |  |  |  | We don’t understand the question. Kindly clarify. | see relevant chapter 1.5.4 List of technical losses that make the PR |  |  | 1 |  | Pass
Juwi | JBS | System PR Specification | System PR | Losses included in PR calculation | 1.5.4 | Ohmic losses in cables | 1 | Page 392-395 | 1 |  |  |  |  | We don’t understand the question. Kindly clarify. | see relevant chapter 1.5.4 List of technical losses that make the PR |  |  | 1 |  | Pass
Juwi | JBS | System PR Specification | System PR | Losses included in PR calculation | 1.5.4 | Auxiliary loads | 1 | Page 392-395 |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | Nicht berücksichtigt | We don’t understand the question. Kindly clarify. | see relevant chapter 1.5.4 List of "losses" = auxilary loads from PV Energy that make the PR | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Juwi | JBS | Basic Scope of Supply | General items | Specific Requirements | 1.6 | The maximum DC voltage shall not exceed 1500 V | 1 | Page 392-395 | 1 | [8 empty] | 1 |  | Pass
Juwi | JBS | Basic Scope of Supply | General items | Specific Requirements | 1.6 | The required AC voltage / frequency at grid connection shall 132 kV/50 Hz | 1 |  | 1 | [8 empty] | 1 |  | Pass
Juwi | JBS | Basic Scope of Supply | Warranty | Quality Assurance | 1.6 | The Product Warranties shall be given for a duration of at least 5 years | 1 |  |  |  | 1 |  | Nicht für alle gefunden | Cannot be evaluated at this stage. Only to be checked in list of deviations. |  | C |  | 1 |  | Open
Juwi | JBS | Physical layout | System PR | Specific Requirements | 1.7.1, 1.1.8 | Layout calculations of predicted kWh over the system lifetime and PR using the tool PVSyst V5.62 or higher | 1 | Page 392-395 | 1 | [8 empty] | 1 |  | Pass
Juwi | JBS | Physical layout | System PR | Specific Requirements | 1.7.1 | Provide a report using Solar GIS data provided by the Employer | 1 | Page 41 | 1 |  |  |  |  | Replace 'Report' with ' PV-Syst report'. | 'Report' is original wording in ER in 1.7.1 |  |  | 1 |  | Pass
Juwi | JBS | Physical layout | Layout | Specific Requirements | 1.7.2 | Provide a schematic electrical Single Line Diagram (SLD) of the entire System layout from the modules to the grid-connection, identifying and listing all of the following DC and AC components. | 1 | Page 307 - 310 | 1 | [8 empty] | 1 |  | Pass
Juwi | JBS | Physical layout | Layout | Specific Requirements | 1.7.2 | The system design shall be such as to ensure ease of maintenance and a multiple ring main unit (RMU) philosophy (on MV level) must be followed for circuit breaker configuration. | 1 | Page 310 |  | 1 |  | The system design shall be such as to ensure ease of maintenance and a multiple ring main unit (RMU) philosophy (on MV level) must be followed for circuit breaker configuration. | Stichleitung mit 5 Stationen max. |  |  | U |  | 1 |  | Fail
Juwi | JBS | Physical layout | Physical layout plan | Specific Requirements | 1.7.7 | Floor plans and elevations for all buildings, housing units, containers on site: e.g. , substations, the SCADA operational room, inverters, O&M, storage facilities | 1 | Page 37 | 1 | [8 empty] | 1 |  | Pass
Juwi | JBS | Physical layout | Physical layout plan | Specific Requirements | 1.7.7 | Detailed view of the distribution of inverters and connections to the PV string/array | 1 | Page 307 - 310 | 1 | [8 empty] | 1 |  | Pass
Juwi | JBS | Physical layout | Physical layout plan | Specific Requirements | 1.7.7 | Detailed top view of the PV mounting structure, including module sizes and spacing between the module rows | 1 | Page 274 | 1 | [8 empty] | 1 |  | Pass
Juwi | JBS | Physical layout | Physical layout plan | Specific Requirements | 1.7.7 | Detailed side and front view of the PV mounting structure | 1 | Page 274 | 1 | [8 empty] | 1 |  | Pass
Juwi | JBS | Physical layout | Physical layout plan | Specific Requirements | 1.7.7 | Detailed top view of electrical cabling interconnections | 1 | Page 307 - 310 | 1 | [8 empty] | 1 |  | Pass
Juwi | JBS | Physical layout | Physical layout plan | Specific Requirements | 1.7.7 | Location of the system metering and grid connection point | 1 | Page 307 - 310 | 1 | [8 empty] | 1 |  | Pass
Juwi | JBS | Physical layout | Auxiliary equipment | Specific Requirements | 1.7.8 | Provide complete indicating, regulating, controlling, protecting and interlocking equipment necessary for safe and efficient operation of the plant and substation, including complete protection scheme. | 1 | Page 307 - 310 | 1 | [8 empty] | 1 |  | Pass
Juwi | JBS | Physical layout | Auxiliary equipment | Specific Requirements | 1.7.8 | The outline of protection schemes shall be shown on the single line diagram (SLD) | 1 | Page 309 | 1 | [8 empty] | 1 |  | Pass
Juwi | JBS | Physical layout | Auxiliary equipment | Specific Requirements | 1.7.8 | All parts of the installation are covered by two high speed protection schemes, which shall be independent to avoid common mode failures | 1 | Page 309 | 1 | [8 empty] | 1 |  | Pass
Juwi | JBS | Physical layout | Auxiliary equipment | Specific Requirements | 1.7.8 | The Bidder shall include a fire prevention and response plan | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Juwi | JBS | Physical layout | Auxiliary equipment | Specific Requirements | 1.7.8 | The fire prevention and response plan shall include a fire alarm und detection system with a main panel in the control room | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Juwi | JBS | Physical layout | Auxiliary equipment | Specific Requirements | 1.7.9 | The documentation includes clearly labelled objects and figures annotated in English language. | 1 |  |  |  | 1 |  |  |  |  | C |  | 1 |  | Open
Juwi | JBS | Physical layout | Auxiliary equipment | Specific Requirements | 1.7.9 | The scope of the documentation shall cover at least the requirements of IEC 62446. | 1 |  |  |  | 1 | Unclear: We do not understand your proposal, please detail your proposal. Especially confirm that you are compliant with our requested criteria. |  |  |  | C |  | 1 |  | Open
Juwi | JBS | Workflow, Project Management Plan and Timelines | Project schedule / Project management | Project schedule | 1.8.1 | Provide installation schedule in compliance with sub-clause 8.2 of Particular Conditions (Time for Completion is 225 days after Commencement Date). | 1 | Page 487 |  | 1 |  | Provide installation schedule in compliance with sub-clause 8.2 of Particular Conditions (Time for Completion is 225 days after Commencement Date). | 341 Tage | Find sub-clause 8.2 of Particular Conditions |  |  |  | 1 |  | Fail
Juwi | JBS | Workflow, Project Management Plan and Timelines | Project schedule / Project management | Project schedule | 1.8.1 | Provide work breakdown structures, activity decomposition and sequencing and dependability with the baseline schedule clearly showing the critical path | 1 | Page 487 | 1 | [8 empty] | 1 |  | Pass
Juwi | JBS | Workflow, Project Management Plan and Timelines | Project schedule / Project management | Project schedule | 1.8.1 | Schedule of tasks | 1 |  | 1 | [8 empty] | 1 |  | Pass
Juwi | JBS | Workflow, Project Management Plan and Timelines | Project schedule / Project management | Project schedule | 1.8.1 | Interdependencies between the tasks | 1 |  | 1 | [8 empty] | 1 |  | Pass
Juwi | JBS | Workflow, Project Management Plan and Timelines | Project schedule / Project management | Project schedule | 1.8.1 | Interdependencies of tasks with equipment order and delivery times | 1 |  | 1 | [8 empty] | 1 |  | Pass
Juwi | JBS | Workflow, Project Management Plan and Timelines | Project schedule / Project management | Project schedule | 1.8.1 | Key milestones to indicate that the progress in on schedule | 1 |  | 1 |  |  | Unclear: We do not understand your proposal, please detail your proposal. Especially confirm that you are compliant with our requested criteria. | [5 empty] | 1 |  | Pass
Juwi | JBS | Workflow, Project Management Plan and Timelines | Project schedule / Project management | Project schedule | 1.8.1 | Teams, the number and skills of personnel to be deployed for each task | 1 |  | 1 | [8 empty] | 1 |  | Pass
Juwi | JBS | Workflow, Project Management Plan and Timelines | Project schedule / Project management | Quality Assurance | 1.8.3 | Quality control of delivered modules | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  |  |  | C |  | 1 |  | Open
Juwi | JBS | Workflow, Project Management Plan and Timelines | Project schedule / Project management | Quality Assurance | 1.8.3 | Inspection of equipment delivery | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  |  |  | C |  | 1 |  | Open
Juwi | JBS | Workflow, Project Management Plan and Timelines | Project schedule / Project management | Quality Assurance | 1.8.3 | Milestones for the completion of civil, mechanical, and electrical works | 1 |  |  |  | 1 | Unclear: We do not understand your proposal, please detail your proposal. Especially confirm that you are compliant with our requested criteria. |  |  | dobble to 105 and 111 | C |  | 1 |  | Open
Juwi | JBS | Workflow, Project Management Plan and Timelines | Project schedule / Project management | Quality Assurance | 1.8.3 | Risk analysis and mitigation plan | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  |  |  | C |  | 1 |  | Open
Juwi | JBS | Workflow, Project Management Plan and Timelines | Project schedule / Project management | Quality Assurance | 1.8.3 | System acceptance QA procedure by the Employer | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  |  |  | C |  | 1 |  | Open
Juwi | JBS | Labelling | General items | Labelling | 1.26 | the ID numbering / coding system shall allow unique identification of all components and be understandable | 1 |  |  |  | 1 | Unclear: We do not understand your proposal, please detail your proposal. Especially confirm that you are compliant with our requested criteria. |  | Cannot be evaluated at this stage |  | C |  | 1 |  | Open
Juwi | JBS | Labelling | General items | Labelling | 1.26 | Tags shall be weather and UV resistant. | 1 |  |  |  | 1 |  |  | Cannot be evaluated at this stage |  | C |  | 1 |  | Open
Juwi | JBS | Labelling | General items | Labelling | 1.26 | The ID’s shall correspond to all drawings, plant documentation and control system. | 1 |  |  |  | 1 |  |  | Cannot be evaluated at this stage |  | C |  | 1 |  | Open
Juwi | JBS | Power plant documentation | Power plant documentation | Quality Assurance | 1.27.1 | The Bidder shall confirm that the complete as-built documentation of the plant will be provided in compliance with IEC 62446. Additionally all module serial numbers shall be listed with their individual location. | 1 |  |  |  | 1 |  |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  | C |  | 1 |  | Open
Juwi | JBS | Power plant documentation | Power plant documentation | Quality Assurance | 1.27.1 | Flash report list of all modules shall be provided in digital form. | 1 |  |  |  | 1 |  |  |  |  | C |  | 1 |  | Open
Juwi | JBS | Power plant documentation | Spare parts | Warranty | 1.27.2 | The successful bidder shall provide all warranty spares for a warranty period of 5 years. | 1 |  |  |  | 1 |  |  |  |  | C |  | 1 |  | Open
Juwi | JBS | Equipment guarantees | Warranty | Guarantees | 1.28 | The overall Guarantee and Power Plant Acceptance Procedures required for the Project are described in Sections 1.3, 1.4, 1.14, 1.18 and Schedule D and shall be met. | 1 |  |  |  | 1 |  |  | Link |  | C |  | 1 |  | Open
Juwi | JBS | Equipment guarantees | Modules | Guarantees | 1.28.1 | The Successful bidder shall provide a Module warranty of at least 10 years. The performance warranty of the module shall be linear with a fixed factor over 25 years. | 1 | Page 17 | 1 |  |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  | To be discussed |  |  |  | 1 |  | Pass
Juwi | JBS | Equipment guarantees | Inverter | Guarantees | 1.28.2 | The Successful Bidder shall provide an Inverter warranty of at least 5 years. A spare parts warranty shall be included for the 25 years operational period. | 1 |  |  |  | 1 |  | kein Hinweis, dass die Verlängerung auf 25 im Angebot enthalten |  |  | C |  | 1 |  | Open
Juwi | JBS | Equipment guarantees | Mounting | Guarantees | 1.28.3 | The Successful Bidder shall provide a product warranty for the structure of at least 10 years. | 1 | Page 18 | 1 | [8 empty] | 1 |  | Pass
Juwi | JBS | Equipment guarantees | Warranty | Guarantees | 1.28.4, 1.6 | A detailed list of all guarantee conditions for the main equipments (beside modules and inverters) shall be provided by the Successful Bidder with the technical offer. The product warranty shall be at least 5 years. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Juwi | JBS | Miscellaneous | Auxiliary systems | Power supply | 1.29.1 | An off-grid power station may need to be provided by the Bidder for commencing the work. Diesel generators shall be arranged by the bidder on its own. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Juwi | JBS | Miscellaneous | Project schedule / Project management | Specific Requirements | 1.29.9 | The Bidder shall submit an organizational chart illustrating management and functional relationships among all project team members including consultants, sub-contractors and vendors at each significant stage of the work, such as permitting, design, construction, testing and commissioning and O&M. | 1 | Page 406 | 1 | [8 empty] | 1 |  | Pass
Chint | JBS | System PR Specification | System PR | O&M | 1.5.2 | The target PR specification at the time of commissioning the System is equal to or greater than 0.75 (75%). | 1 |  | 1 |  |  |  | mit 75% gerade an der Grenze |  |  |  |  | 1 |  | Pass
Chint | JBS | System PR Specification | System PR | Losses included in PR calculation | 1.5.4 | Module Array (temperature dependence, soiling, low light inefficiency, shading, mismatches in array) | 1 |  | 1 |  |  |  |  | We don’t understand the question. Kindly clarify. | we want to see these losses specified. Thos need to be aligned with O+M Startegy and System composition |  |  | 1 |  | Pass
Chint | JBS | System PR Specification | System PR | Losses included in PR calculation | 1.5.4 | Inverter (operating efficiency, operating voltage variations, power/voltage levels) | 1 |  | 1 |  |  |  | Temperaturverlsute 16,9 | We don’t understand the question. Kindly clarify. | see relevant chapter 1.5.4 List of technical losses that make the PR |  |  | 1 |  | Pass
Chint | JBS | System PR Specification | System PR | Losses included in PR calculation | 1.5.4 | Transformer losses | 1 | Page 443-447 |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | Trafoverluste nicht berücksichtigt | We don’t understand the question. Kindly clarify. | see relevant chapter 1.5.4 List of technical losses that make the PR | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Chint | JBS | System PR Specification | System PR | Losses included in PR calculation | 1.5.4 | Ohmic losses in cables | 1 | Page 443-447 | 1 |  |  |  |  | We don’t understand the question. Kindly clarify. | see relevant chapter 1.5.4 List of technical losses that make the PR |  |  | 1 |  | Pass
Chint | JBS | System PR Specification | System PR | Losses included in PR calculation | 1.5.4 | Auxiliary loads | 1 | Page 443-447 |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | Nicht berücksichtigt | We don’t understand the question. Kindly clarify. | see relevant chapter 1.5.4 List of "losses" = auxilary loads from PV Energy that make the PR | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Chint | JBS | Basic Scope of Supply | General items | Specific Requirements | 1.6 | The maximum DC voltage shall not exceed 1500 V | 1 | Page 443-447 | 1 |  |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | [5 empty] | 1 |  | Pass
Chint | JBS | Basic Scope of Supply | General items | Specific Requirements | 1.6 | The required AC voltage / frequency at grid connection shall 132 kV/50 Hz | 1 | Page 443-447 | 1 | [8 empty] | 1 |  | Pass
Chint | JBS | Basic Scope of Supply | Warranty | Quality Assurance | 1.6 | The Product Warranties shall be given for a duration of at least 5 years | 1 |  |  |  | 1 |  |  | Cannot be evaluated at this stage. Only to be checked in list of deviations. |  | C |  | 1 |  | Open
Chint | JBS | Physical layout | System PR | Specific Requirements | 1.7.1, 1.1.8 | Layout calculations of predicted kWh over the system lifetime and PR using the tool PVSyst V5.62 or higher | 1 | Page 443-447 | 1 | [8 empty] | 1 |  | Pass
Chint | JBS | Physical layout | System PR | Specific Requirements | 1.7.1 | Provide a report using Solar GIS data provided by the Employer | 1 | Page 443-447 | 1 |  |  |  |  | Replace 'Report' with ' PV-Syst report'. | 'Report' is original wording in ER in 1.7.1 |  |  | 1 |  | Pass
Chint | JBS | Physical layout | Layout | Specific Requirements | 1.7.2 | Provide a schematic electrical Single Line Diagram (SLD) of the entire System layout from the modules to the grid-connection, identifying and listing all of the following DC and AC components. | 1 | Page 449- 453 | 1 | [8 empty] | 1 |  | Pass
Chint | JBS | Physical layout | Layout | Specific Requirements | 1.7.2 | The system design shall be such as to ensure ease of maintenance and a multiple ring main unit (RMU) philosophy (on MV level) must be followed for circuit breaker configuration. | 1 | Page 450 | 1 |  |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | [5 empty] | 1 |  | Pass
Chint | JBS | Physical layout | Physical layout plan | Specific Requirements | 1.7.7 | Floor plans and elevations for all buildings, housing units, containers on site: e.g. , substations, the SCADA operational room, inverters, O&M, storage facilities | 1 | Page 453 | 1 | [8 empty] | 1 |  | Pass
Chint | JBS | Physical layout | Physical layout plan | Specific Requirements | 1.7.7 | Detailed view of the distribution of inverters and connections to the PV string/array | 1 | Page 449 | 1 |  |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | [5 empty] | 1 |  | Pass
Chint | JBS | Physical layout | Physical layout plan | Specific Requirements | 1.7.7 | Detailed top view of the PV mounting structure, including module sizes and spacing between the module rows | 1 | Page 455 Page 456 |  |  | 1 | Inconsistency: Second drawing module dimensions inconsistent with datasheet.We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | [5 empty] | 1 | 1 | Open
Chint | JBS | Physical layout | Physical layout plan | Specific Requirements | 1.7.7 | Detailed side and front view of the PV mounting structure | 1 | Page 455 | 1 |  |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | [5 empty] | 1 |  | Pass
Chint | JBS | Physical layout | Physical layout plan | Specific Requirements | 1.7.7 | Detailed top view of electrical cabling interconnections | 1 | Page 455 | 1 |  |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | [5 empty] | 1 |  | Pass
Chint | JBS | Physical layout | Physical layout plan | Specific Requirements | 1.7.7 | Location of the system metering and grid connection point | 1 | Page 452 | 1 |  |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | [5 empty] | 1 |  | Pass
Chint | JBS | Physical layout | Auxiliary equipment | Specific Requirements | 1.7.8 | Provide complete indicating, regulating, controlling, protecting and interlocking equipment necessary for safe and efficient operation of the plant and substation, including complete protection scheme. | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | [5 empty] | 1 |  | Open
Chint | JBS | Physical layout | Auxiliary equipment | Specific Requirements | 1.7.8 | The outline of protection schemes shall be shown on the single line diagram (SLD) | 1 | Page 449- 453 | 1 |  |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | [5 empty] | 1 |  | Pass
Chint | JBS | Physical layout | Auxiliary equipment | Specific Requirements | 1.7.8 | All parts of the installation are covered by two high speed protection schemes, which shall be independent to avoid common mode failures | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | [5 empty] | 1 |  | Open
Chint | JBS | Physical layout | Auxiliary equipment | Specific Requirements | 1.7.8 | The Bidder shall include a fire prevention and response plan | 1 | Chapter 2 | 1 | [8 empty] | 1 |  | Pass
Chint | JBS | Physical layout | Auxiliary equipment | Specific Requirements | 1.7.8 | The fire prevention and response plan shall include a fire alarm und detection system with a main panel in the control room | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | [5 empty] | 1 |  | Open
Chint | JBS | Physical layout | Auxiliary equipment | Specific Requirements | 1.7.9 | The documentation includes clearly labelled objects and figures annotated in English language. | 1 |  | 1 |  |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | [5 empty] | 1 |  | Pass
Chint | JBS | Physical layout | Auxiliary equipment | Specific Requirements | 1.7.9 | The scope of the documentation shall cover at least the requirements of IEC 62446. | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  |  |  | C |  | 1 |  | Open
Chint | JBS | Workflow, Project Management Plan and Timelines | Project schedule / Project management | Project schedule | 1.8.1 | Provide installation schedule in compliance with sub-clause 8.2 of Particular Conditions (Time for Completion is 225 days after Commencement Date). | 1 | Page 106 | 1 |  |  |  |  | Find sub-clause 8.2 of Particular Conditions |  |  |  | 1 |  | Pass
Chint | JBS | Workflow, Project Management Plan and Timelines | Project schedule / Project management | Project schedule | 1.8.1 | Provide work breakdown structures, activity decomposition and sequencing and dependability with the baseline schedule clearly showing the critical path | 1 |  | 1 | [8 empty] | 1 |  | Pass
Chint | JBS | Workflow, Project Management Plan and Timelines | Project schedule / Project management | Project schedule | 1.8.1 | Schedule of tasks | 1 |  | 1 | [8 empty] | 1 |  | Pass
Chint | JBS | Workflow, Project Management Plan and Timelines | Project schedule / Project management | Project schedule | 1.8.1 | Interdependencies between the tasks | 1 |  | 1 | [8 empty] | 1 |  | Pass
Chint | JBS | Workflow, Project Management Plan and Timelines | Project schedule / Project management | Project schedule | 1.8.1 | Interdependencies of tasks with equipment order and delivery times | 1 |  | 1 | [8 empty] | 1 |  | Pass
Chint | JBS | Workflow, Project Management Plan and Timelines | Project schedule / Project management | Project schedule | 1.8.1 | Key milestones to indicate that the progress in on schedule | 1 |  |  |  | 1 | [6 empty] | 1 |  | Open
Chint | JBS | Workflow, Project Management Plan and Timelines | Project schedule / Project management | Project schedule | 1.8.1 | Teams, the number and skills of personnel to be deployed for each task | 1 |  | 1 | [8 empty] | 1 |  | Pass
Chint | JBS | Workflow, Project Management Plan and Timelines | Project schedule / Project management | Quality Assurance | 1.8.3 | Quality control of delivered modules | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  |  |  | C |  | 1 |  | Open
Chint | JBS | Workflow, Project Management Plan and Timelines | Project schedule / Project management | Quality Assurance | 1.8.3 | Inspection of equipment delivery | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  |  |  | C |  | 1 |  | Open
Chint | JBS | Workflow, Project Management Plan and Timelines | Project schedule / Project management | Quality Assurance | 1.8.3 | Milestones for the completion of civil, mechanical, and electrical works | 1 |  |  |  | 1 |  |  |  | dobble to 105 and 111 | C |  | 1 |  | Open
Chint | JBS | Workflow, Project Management Plan and Timelines | Project schedule / Project management | Quality Assurance | 1.8.3 | Risk analysis and mitigation plan | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  |  |  | C |  | 1 |  | Open
Chint | JBS | Workflow, Project Management Plan and Timelines | Project schedule / Project management | Quality Assurance | 1.8.3 | System acceptance QA procedure by the Employer | 1 |  |  |  | 1 | Unclear: We do not understand your proposal, please detail your proposal. Especially confirm that you are compliant with our requested criteria. |  |  |  | C |  | 1 |  | Open
Chint | JBS | Labelling | General items | Labelling | 1.26 | the ID numbering / coding system shall allow unique identification of all components and be understandable | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  | Cannot be evaluated at this stage |  | C |  | 1 |  | Open
Chint | JBS | Labelling | General items | Labelling | 1.26 | Tags shall be weather and UV resistant. | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  | Cannot be evaluated at this stage |  | C |  | 1 |  | Open
Chint | JBS | Labelling | General items | Labelling | 1.26 | The ID’s shall correspond to all drawings, plant documentation and control system. | 1 |  |  |  | 1 |  |  | Cannot be evaluated at this stage |  | C |  | 1 |  | Open
Chint | JBS | Power plant documentation | Power plant documentation | Quality Assurance | 1.27.1 | The Bidder shall confirm that the complete as-built documentation of the plant will be provided in compliance with IEC 62446. Additionally all module serial numbers shall be listed with their individual location. | 1 |  |  |  | 1 |  |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  | C |  | 1 |  | Open
Chint | JBS | Power plant documentation | Power plant documentation | Quality Assurance | 1.27.1 | Flash report list of all modules shall be provided in digital form. | 1 |  |  |  | 1 |  |  |  |  | C |  | 1 |  | Open
Chint | JBS | Power plant documentation | Spare parts | Warranty | 1.27.2 | The successful bidder shall provide all warranty spares for a warranty period of 5 years. | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  |  |  | C |  | 1 |  | Open
Chint | JBS | Equipment guarantees | Warranty | Guarantees | 1.28 | The overall Guarantee and Power Plant Acceptance Procedures required for the Project are described in Sections 1.3, 1.4, 1.14, 1.18 and Schedule D and shall be met. | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  | Link |  | C |  | 1 |  | Open
Chint | JBS | Equipment guarantees | Modules | Guarantees | 1.28.1 | The Successful bidder shall provide a Module warranty of at least 10 years. The performance warranty of the module shall be linear with a fixed factor over 25 years. | 1 | Page 21 | 1 |  |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  | To be discussed |  |  |  | 1 |  | Pass
Chint | JBS | Equipment guarantees | Inverter | Guarantees | 1.28.2 | The Successful Bidder shall provide an Inverter warranty of at least 5 years. A spare parts warranty shall be included for the 25 years operational period. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Chint | JBS | Equipment guarantees | Mounting | Guarantees | 1.28.3 | The Successful Bidder shall provide a product warranty for the structure of at least 10 years. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Chint | JBS | Equipment guarantees | Warranty | Guarantees | 1.28.4, 1.6 | A detailed list of all guarantee conditions for the main equipments (beside modules and inverters) shall be provided by the Successful Bidder with the technical offer. The product warranty shall be at least 5 years. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Chint | JBS | Miscellaneous | Auxiliary systems | Power supply | 1.29.1 | An off-grid power station may need to be provided by the Bidder for commencing the work. Diesel generators shall be arranged by the bidder on its own. | 1 | Page 116 | 1 |  |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | [5 empty] | 1 |  | Pass
Chint | JBS | Miscellaneous | Project schedule / Project management | Specific Requirements | 1.29.9 | The Bidder shall submit an organizational chart illustrating management and functional relationships among all project team members including consultants, sub-contractors and vendors at each significant stage of the work, such as permitting, design, construction, testing and commissioning and O&M. | 1 | Page 38/39 | 1 |  |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | [5 empty] | 1 |  | Pass
Tbea | JBS | System PR Specification | System PR | O&M | 1.5.2 | The target PR specification at the time of commissioning the System is equal to or greater than 0.75 (75%). | 1 | page 77 -78 |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | [5 empty] | 1 |  | Open
Tbea | JBS | System PR Specification | System PR | Losses included in PR calculation | 1.5.4 | Module Array (temperature dependence, soiling, low light inefficiency, shading, mismatches in array) | 1 | page 77 -78 |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | Fail. Shading and IAM losses missing | We don’t understand the question. Kindly clarify. | we want to see these losses specified. Thos need to be aligned with O+M Startegy and System composition | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Tbea | JBS | System PR Specification | System PR | Losses included in PR calculation | 1.5.4 | Inverter (operating efficiency, operating voltage variations, power/voltage levels) | 1 | page 77 -78 | 1 |  |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  | We don’t understand the question. Kindly clarify. | see relevant chapter 1.5.4 List of technical losses that make the PR |  |  | 1 |  | Pass
Tbea | JBS | System PR Specification | System PR | Losses included in PR calculation | 1.5.4 | Transformer losses | 1 | page 77 -78 | 1 |  |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  | We don’t understand the question. Kindly clarify. | see relevant chapter 1.5.4 List of technical losses that make the PR |  |  | 1 |  | Pass
Tbea | JBS | System PR Specification | System PR | Losses included in PR calculation | 1.5.4 | Ohmic losses in cables | 1 | page 77 -78 | 1 |  |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  | We don’t understand the question. Kindly clarify. | see relevant chapter 1.5.4 List of technical losses that make the PR |  |  | 1 |  | Pass
Tbea | JBS | System PR Specification | System PR | Losses included in PR calculation | 1.5.4 | Auxiliary loads | 1 | page 77 -78 |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | Fail Nicht berücksichtigt | We don’t understand the question. Kindly clarify. | see relevant chapter 1.5.4 List of "losses" = auxilary loads from PV Energy that make the PR | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Tbea | JBS | Basic Scope of Supply | General items | Specific Requirements | 1.6 | The maximum DC voltage shall not exceed 1500 V | 1 |  | 1 |  |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | [5 empty] | 1 |  | Pass
Tbea | JBS | Basic Scope of Supply | General items | Specific Requirements | 1.6 | The required AC voltage / frequency at grid connection shall 132 kV/50 Hz | 1 |  | 1 |  |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | [5 empty] | 1 |  | Pass
Tbea | JBS | Basic Scope of Supply | Warranty | Quality Assurance | 1.6 | The Product Warranties shall be given for a duration of at least 5 years | 1 | page 83 | 1 |  |  | General understanding: expressions like "shall", "shall be supplied with", "has to be", "must be" have the meaning of "will be delivered"? |  | Cannot be evaluated at this stage. Only to be checked in list of deviations. |  |  |  | 1 |  | Pass
Tbea | JBS | Physical layout | System PR | Specific Requirements | 1.7.1, 1.1.8 | Layout calculations of predicted kWh over the system lifetime and PR using the tool PVSyst V5.62 or higher | 1 | page 76 | 1 |  |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | [5 empty] | 1 |  | Pass
Tbea | JBS | Physical layout | System PR | Specific Requirements | 1.7.1 | Provide a report using Solar GIS data provided by the Employer | 1 | page 75 | 1 |  |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  | Replace 'Report' with ' PV-Syst report'. | 'Report' is original wording in ER in 1.7.1 |  |  | 1 |  | Pass
Tbea | JBS | Physical layout | Layout | Specific Requirements | 1.7.2 | Provide a schematic electrical Single Line Diagram (SLD) of the entire System layout from the modules to the grid-connection, identifying and listing all of the following DC and AC components. | 1 | page 85 | 1 | [8 empty] | 1 |  | Pass
Tbea | JBS | Physical layout | Layout | Specific Requirements | 1.7.2 | The system design shall be such as to ensure ease of maintenance and a multiple ring main unit (RMU) philosophy (on MV level) must be followed for circuit breaker configuration. | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  |  |  | U |  | 1 |  | Open
Tbea | JBS | Physical layout | Physical layout plan | Specific Requirements | 1.7.7 | Floor plans and elevations for all buildings, housing units, containers on site: e.g. , substations, the SCADA operational room, inverters, O&M, storage facilities | 1 | page 1124 | 1 | [8 empty] | 1 |  | Pass
Tbea | JBS | Physical layout | Physical layout plan | Specific Requirements | 1.7.7 | Detailed view of the distribution of inverters and connections to the PV string/array | 1 | page 84 | 1 | [8 empty] | 1 |  | Pass
Tbea | JBS | Physical layout | Physical layout plan | Specific Requirements | 1.7.7 | Detailed top view of the PV mounting structure, including module sizes and spacing between the module rows | 1 | page 145/146 | 1 | [8 empty] | 1 |  | Pass
Tbea | JBS | Physical layout | Physical layout plan | Specific Requirements | 1.7.7 | Detailed side and front view of the PV mounting structure | 1 | page 145/146 | 1 |  |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | [5 empty] | 1 |  | Pass
Tbea | JBS | Physical layout | Physical layout plan | Specific Requirements | 1.7.7 | Detailed top view of electrical cabling interconnections | 1 | page 134 | 1 | [8 empty] | 1 |  | Pass
Tbea | JBS | Physical layout | Physical layout plan | Specific Requirements | 1.7.7 | Location of the system metering and grid connection point | 1 | page 85 | 1 |  |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | [5 empty] | 1 |  | Pass
Tbea | JBS | Physical layout | Auxiliary equipment | Specific Requirements | 1.7.8 | Provide complete indicating, regulating, controlling, protecting and interlocking equipment necessary for safe and efficient operation of the plant and substation, including complete protection scheme. | 1 | page 85 | 1 |  |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | [5 empty] | 1 |  | Pass
Tbea | JBS | Physical layout | Auxiliary equipment | Specific Requirements | 1.7.8 | The outline of protection schemes shall be shown on the single line diagram (SLD) | 1 | page 85 | 1 |  |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | [5 empty] | 1 |  | Pass
Tbea | JBS | Physical layout | Auxiliary equipment | Specific Requirements | 1.7.8 | All parts of the installation are covered by two high speed protection schemes, which shall be independent to avoid common mode failures | 1 | page 85 | 1 |  |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | [5 empty] | 1 |  | Pass
Tbea | JBS | Physical layout | Auxiliary equipment | Specific Requirements | 1.7.8 | The Bidder shall include a fire prevention and response plan | 1 | page 86 |  |  | 1 | General understanding: expressions like "shall", "shall be supplied with", "has to be", "must be" have the meaning of "will be delivered"? Please confirm. |  |  |  | G | General understanding: expressions like "shall", "shall be supplied with", "has to be", "must be" have the meaning of "will be delivered"? Please confirm. | 1 |  | Open
Tbea | JBS | Physical layout | Auxiliary equipment | Specific Requirements | 1.7.8 | The fire prevention and response plan shall include a fire alarm und detection system with a main panel in the control room | 1 | page 87 |  |  | 1 | General understanding: expressions like "shall", "shall be supplied with", "has to be", "must be" have the meaning of "will be delivered"? Please confirm. |  |  |  | G | General understanding: expressions like "shall", "shall be supplied with", "has to be", "must be" have the meaning of "will be delivered"? Please confirm. | 1 |  | Open
Tbea | JBS | Physical layout | Auxiliary equipment | Specific Requirements | 1.7.9 | The documentation includes clearly labelled objects and figures annotated in English language. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | [5 empty] | 1 |  | Open
Tbea | JBS | Physical layout | Auxiliary equipment | Specific Requirements | 1.7.9 | The scope of the documentation shall cover at least the requirements of IEC 62446. | 1 | page 87 |  |  | 1 | General understanding: expressions like "shall", "shall be supplied with", "has to be", "must be" have the meaning of "will be delivered"? Please confirm. |  |  |  | G | General understanding: expressions like "shall", "shall be supplied with", "has to be", "must be" have the meaning of "will be delivered"? Please confirm. | 1 |  | Open
Tbea | JBS | Workflow, Project Management Plan and Timelines | Project schedule / Project management | Project schedule | 1.8.1 | Provide installation schedule in compliance with sub-clause 8.2 of Particular Conditions (Time for Completion is 225 days after Commencement Date). | 1 | page 44-45 | 1 |  |  |  |  | Find sub-clause 8.2 of Particular Conditions |  |  |  | 1 |  | Pass
Tbea | JBS | Workflow, Project Management Plan and Timelines | Project schedule / Project management | Project schedule | 1.8.1 | Provide work breakdown structures, activity decomposition and sequencing and dependability with the baseline schedule clearly showing the critical path | 1 | page 44-45 | 1 | [8 empty] | 1 |  | Pass
Tbea | JBS | Workflow, Project Management Plan and Timelines | Project schedule / Project management | Project schedule | 1.8.1 | Schedule of tasks | 1 | page 44-45 | 1 | [8 empty] | 1 |  | Pass
Tbea | JBS | Workflow, Project Management Plan and Timelines | Project schedule / Project management | Project schedule | 1.8.1 | Interdependencies between the tasks | 1 | page 44-45 | 1 | [8 empty] | 1 |  | Pass
Tbea | JBS | Workflow, Project Management Plan and Timelines | Project schedule / Project management | Project schedule | 1.8.1 | Interdependencies of tasks with equipment order and delivery times | 1 | page 44-45 | 1 | [8 empty] | 1 |  | Pass
Tbea | JBS | Workflow, Project Management Plan and Timelines | Project schedule / Project management | Project schedule | 1.8.1 | Key milestones to indicate that the progress in on schedule | 1 | page 44-45 | 1 | [8 empty] | 1 |  | Pass
Tbea | JBS | Workflow, Project Management Plan and Timelines | Project schedule / Project management | Project schedule | 1.8.1 | Teams, the number and skills of personnel to be deployed for each task | 1 | Page 13-41 | 1 | [8 empty] | 1 |  | Pass
Tbea | JBS | Workflow, Project Management Plan and Timelines | Project schedule / Project management | Quality Assurance | 1.8.3 | Quality control of delivered modules | 1 | Page 93, 1018 | 1 | [8 empty] | 1 |  | Pass
Tbea | JBS | Workflow, Project Management Plan and Timelines | Project schedule / Project management | Quality Assurance | 1.8.3 | Inspection of equipment delivery | 1 | Page 1018 | 1 | [8 empty] | 1 |  | Pass
Tbea | JBS | Workflow, Project Management Plan and Timelines | Project schedule / Project management | Quality Assurance | 1.8.3 | Milestones for the completion of civil, mechanical, and electrical works | 1 | page 1025 | 1 | [5 empty] | dobble to 105 and 111 |  |  | 1 |  | Pass
Tbea | JBS | Workflow, Project Management Plan and Timelines | Project schedule / Project management | Quality Assurance | 1.8.3 | Risk analysis and mitigation plan | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Tbea | JBS | Workflow, Project Management Plan and Timelines | Project schedule / Project management | Quality Assurance | 1.8.3 | System acceptance QA procedure by the Employer | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Tbea | JBS | Labelling | General items | Labelling | 1.26 | the ID numbering / coding system shall allow unique identification of all components and be understandable | 1 |  |  |  | 1 | General understanding: expressions like "shall", "shall be supplied with", "has to be", "must be" have the meaning of "will be delivered"? Please confirm. |  | Cannot be evaluated at this stage |  | G | General understanding: expressions like "shall", "shall be supplied with", "has to be", "must be" have the meaning of "will be delivered"? Please confirm. | 1 |  | Open
Tbea | JBS | Labelling | General items | Labelling | 1.26 | Tags shall be weather and UV resistant. | 1 |  |  |  | 1 | General understanding: expressions like "shall", "shall be supplied with", "has to be", "must be" have the meaning of "will be delivered"? Please confirm. |  | Cannot be evaluated at this stage |  | G | General understanding: expressions like "shall", "shall be supplied with", "has to be", "must be" have the meaning of "will be delivered"? Please confirm. | 1 |  | Open
Tbea | JBS | Labelling | General items | Labelling | 1.26 | The ID’s shall correspond to all drawings, plant documentation and control system. | 1 |  |  |  | 1 | General understanding: expressions like "shall", "shall be supplied with", "has to be", "must be" have the meaning of "will be delivered"? Please confirm. |  | Cannot be evaluated at this stage |  | G | General understanding: expressions like "shall", "shall be supplied with", "has to be", "must be" have the meaning of "will be delivered"? Please confirm. | 1 |  | Open
Tbea | JBS | Power plant documentation | Power plant documentation | Quality Assurance | 1.27.1 | The Bidder shall confirm that the complete as-built documentation of the plant will be provided in compliance with IEC 62446. Additionally all module serial numbers shall be listed with their individual location. | 1 |  |  |  | 1 | General understanding: expressions like "shall", "shall be supplied with", "has to be", "must be" have the meaning of "will be delivered"? Please confirm. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  | G | General understanding: expressions like "shall", "shall be supplied with", "has to be", "must be" have the meaning of "will be delivered"? Please confirm. | 1 |  | Open
Tbea | JBS | Power plant documentation | Power plant documentation | Quality Assurance | 1.27.1 | Flash report list of all modules shall be provided in digital form. | 1 |  |  |  | 1 | General understanding: expressions like "shall", "shall be supplied with", "has to be", "must be" have the meaning of "will be delivered"? Please confirm. |  |  |  | G | General understanding: expressions like "shall", "shall be supplied with", "has to be", "must be" have the meaning of "will be delivered"? Please confirm. | 1 |  | Open
Tbea | JBS | Power plant documentation | Spare parts | Warranty | 1.27.2 | The successful bidder shall provide all warranty spares for a warranty period of 5 years. | 1 |  |  |  | 1 | General understanding: expressions like "shall", "shall be supplied with", "has to be", "must be" have the meaning of "will be delivered"? Please confirm. |  |  |  | G | General understanding: expressions like "shall", "shall be supplied with", "has to be", "must be" have the meaning of "will be delivered"? Please confirm. | 1 |  | Open
Tbea | JBS | Equipment guarantees | Warranty | Guarantees | 1.28 | The overall Guarantee and Power Plant Acceptance Procedures required for the Project are described in Sections 1.3, 1.4, 1.14, 1.18 and Schedule D and shall be met. | 1 |  |  |  | 1 | General understanding: expressions like "shall", "shall be supplied with", "has to be", "must be" have the meaning of "will be delivered"? Please confirm. |  | Link |  | G | General understanding: expressions like "shall", "shall be supplied with", "has to be", "must be" have the meaning of "will be delivered"? Please confirm. | 1 |  | Open
Tbea | JBS | Equipment guarantees | Modules | Guarantees | 1.28.1 | The Successful bidder shall provide a Module warranty of at least 10 years. The performance warranty of the module shall be linear with a fixed factor over 25 years. | 1 |  |  |  | 1 | General understanding: expressions like "shall", "shall be supplied with", "has to be", "must be" have the meaning of "will be delivered"? Please confirm. |  | To be discussed |  | G | General understanding: expressions like "shall", "shall be supplied with", "has to be", "must be" have the meaning of "will be delivered"? Please confirm. | 1 |  | Open
Tbea | JBS | Equipment guarantees | Inverter | Guarantees | 1.28.2 | The Successful Bidder shall provide an Inverter warranty of at least 5 years. A spare parts warranty shall be included for the 25 years operational period. | 1 |  |  |  | 1 | General understanding: expressions like "shall", "shall be supplied with", "has to be", "must be" have the meaning of "will be delivered"? Please confirm. |  |  |  | G | General understanding: expressions like "shall", "shall be supplied with", "has to be", "must be" have the meaning of "will be delivered"? Please confirm. | 1 |  | Open
Tbea | JBS | Equipment guarantees | Mounting | Guarantees | 1.28.3 | The Successful Bidder shall provide a product warranty for the structure of at least 10 years. | 1 |  |  |  | 1 | General understanding: expressions like "shall", "shall be supplied with", "has to be", "must be" have the meaning of "will be delivered"? Please confirm. |  |  |  | G | General understanding: expressions like "shall", "shall be supplied with", "has to be", "must be" have the meaning of "will be delivered"? Please confirm. | 1 |  | Open
Tbea | JBS | Equipment guarantees | Warranty | Guarantees | 1.28.4, 1.6 | A detailed list of all guarantee conditions for the main equipments (beside modules and inverters) shall be provided by the Successful Bidder with the technical offer. The product warranty shall be at least 5 years. | 1 |  |  |  | 1 | General understanding: expressions like "shall", "shall be supplied with", "has to be", "must be" have the meaning of "will be delivered"? Please confirm. |  |  |  | G | General understanding: expressions like "shall", "shall be supplied with", "has to be", "must be" have the meaning of "will be delivered"? Please confirm. | 1 |  | Open
Tbea | JBS | Miscellaneous | Auxiliary systems | Power supply | 1.29.1 | An off-grid power station may need to be provided by the Bidder for commencing the work. Diesel generators shall be arranged by the bidder on its own. | 1 | page 51 | 1 | [8 empty] | 1 |  | Pass
Tbea | JBS | Miscellaneous | Project schedule / Project management | Specific Requirements | 1.29.9 | The Bidder shall submit an organizational chart illustrating management and functional relationships among all project team members including consultants, sub-contractors and vendors at each significant stage of the work, such as permitting, design, construction, testing and commissioning and O&M. | 1 | page 14 | 1 | [8 empty] | 1 |  | Pass
Zte | JBS | System PR Specification | System PR | O&M | 1.5.2 | The target PR specification at the time of commissioning the System is equal to or greater than 0.75 (75%). | 1 | 1. SoC to Bidding Document 30-01-14.pdf Page 107 |  |  | 1 | [6 empty] | 1 |  | Open
Zte | JBS | System PR Specification | System PR | Losses included in PR calculation | 1.5.4 | Module Array (temperature dependence, soiling, low light inefficiency, shading, mismatches in array) | 1 | 1. SoC to Bidding Document 30-01-14.pdf Page 114 |  | 1 |  | Unclear: We do not understand your proposal, please detail your proposal. Especially confirm that you are compliant with our requested criteria. | keine Verschattung gerechnet, Soiling zu gering, Qualitätsaufschlag eindeutig zu hoch. | We don’t understand the question. Kindly clarify. | we want to see these losses specified. Thos need to be aligned with O+M Startegy and System composition |  |  | 1 | 1 | Fail
Zte | JBS | System PR Specification | System PR | Losses included in PR calculation | 1.5.4 | Inverter (operating efficiency, operating voltage variations, power/voltage levels) | 1 | 1. SoC to Bidding Document 30-01-14.pdf Page 114 | 1 |  |  |  |  | We don’t understand the question. Kindly clarify. | see relevant chapter 1.5.4 List of technical losses that make the PR |  |  | 1 |  | Pass
Zte | JBS | System PR Specification | System PR | Losses included in PR calculation | 1.5.4 | Transformer losses | 1 | 1. SoC to Bidding Document 30-01-14.pdf Page 114 | 1 |  |  |  | Trocken-Transfomer Datenblatt nicht vorhanden. | We don’t understand the question. Kindly clarify. | see relevant chapter 1.5.4 List of technical losses that make the PR |  |  | 1 |  | Pass
Zte | JBS | System PR Specification | System PR | Losses included in PR calculation | 1.5.4 | Ohmic losses in cables | 1 | 1. SoC to Bidding Document 30-01-14.pdf Page 114 |  | 1 |  | Unclear: We do not understand your proposal, please detail your proposal. Especially confirm that you are compliant with our requested criteria. | fail | We don’t understand the question. Kindly clarify. | see relevant chapter 1.5.4 List of technical losses that make the PR |  |  | 1 | 1 | Fail
Zte | JBS | System PR Specification | System PR | Losses included in PR calculation | 1.5.4 | Auxiliary loads | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | fail | We don’t understand the question. Kindly clarify. | see relevant chapter 1.5.4 List of "losses" = auxilary loads from PV Energy that make the PR | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Zte | JBS | Basic Scope of Supply | General items | Specific Requirements | 1.6 | The maximum DC voltage shall not exceed 1500 V | 1 |  | 1 | [8 empty] | 1 |  | Pass
Zte | JBS | Basic Scope of Supply | General items | Specific Requirements | 1.6 | The required AC voltage / frequency at grid connection shall 132 kV/50 Hz | 1 |  | 1 | [8 empty] | 1 |  | Pass
Zte | JBS | Basic Scope of Supply | Warranty | Quality Assurance | 1.6 | The Product Warranties shall be given for a duration of at least 5 years | 1 | 1. SoC to Bidding Document 30-01-14.pdf Page 101 | 1 |  |  |  |  | Cannot be evaluated at this stage. Only to be checked in list of deviations. |  |  |  | 1 |  | Pass
Zte | JBS | Physical layout | System PR | Specific Requirements | 1.7.1, 1.1.8 | Layout calculations of predicted kWh over the system lifetime and PR using the tool PVSyst V5.62 or higher | 1 | 1. SoC to Bidding Document 30-01-14.pdf Page 106 | 1 | [8 empty] | 1 |  | Pass
Zte | JBS | Physical layout | System PR | Specific Requirements | 1.7.1 | Provide a report using Solar GIS data provided by the Employer | 1 | 1. SoC to Bidding Document 30-01-14.pdf Page 101 | 1 |  |  |  |  | Replace 'Report' with ' PV-Syst report'. | 'Report' is original wording in ER in 1.7.1 |  |  | 1 |  | Pass
Zte | JBS | Physical layout | Layout | Specific Requirements | 1.7.2 | Provide a schematic electrical Single Line Diagram (SLD) of the entire System layout from the modules to the grid-connection, identifying and listing all of the following DC and AC components. | 1 | P004 Single line diagram.pdf | 1 | [8 empty] | 1 |  | Pass
Zte | JBS | Physical layout | Layout | Specific Requirements | 1.7.2 | The system design shall be such as to ensure ease of maintenance and a multiple ring main unit (RMU) philosophy (on MV level) must be followed for circuit breaker configuration. | 1 | P004 Single line diagram.pdf | 1 | [8 empty] | 1 |  | Pass
Zte | JBS | Physical layout | Physical layout plan | Specific Requirements | 1.7.7 | Floor plans and elevations for all buildings, housing units, containers on site: e.g. , substations, the SCADA operational room, inverters, O&M, storage facilities | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  |  |  | U |  | 1 |  | Open
Zte | JBS | Physical layout | Physical layout plan | Specific Requirements | 1.7.7 | Detailed view of the distribution of inverters and connections to the PV string/array | 1 | P001 100MW PV Power plant layout.pdf, P006 1 MWp PV generation subsystem.pdf | 1 | [8 empty] | 1 |  | Pass
Zte | JBS | Physical layout | Physical layout plan | Specific Requirements | 1.7.7 | Detailed top view of the PV mounting structure, including module sizes and spacing between the module rows | 1 | P002 PV module support structure.pdf, P003 PV array layout.pdf | 1 | [8 empty] | 1 |  | Pass
Zte | JBS | Physical layout | Physical layout plan | Specific Requirements | 1.7.7 | Detailed side and front view of the PV mounting structure | 1 | P002 PV module support structure.pdf | 1 |  |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | [5 empty] | 1 |  | Pass
Zte | JBS | Physical layout | Physical layout plan | Specific Requirements | 1.7.7 | Detailed top view of electrical cabling interconnections | 1 |  | 1 |  |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | [5 empty] | 1 |  | Pass
Zte | JBS | Physical layout | Physical layout plan | Specific Requirements | 1.7.7 | Location of the system metering and grid connection point | 1 | P004 Single line diagram.pdf | 1 |  |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | [5 empty] | 1 |  | Pass
Zte | JBS | Physical layout | Auxiliary equipment | Specific Requirements | 1.7.8 | Provide complete indicating, regulating, controlling, protecting and interlocking equipment necessary for safe and efficient operation of the plant and substation, including complete protection scheme. | 1 | P004 Single line diagram.pdf | 1 | [8 empty] | 1 |  | Pass
Zte | JBS | Physical layout | Auxiliary equipment | Specific Requirements | 1.7.8 | The outline of protection schemes shall be shown on the single line diagram (SLD) | 1 |  | 1 | [8 empty] | 1 |  | Pass
Zte | JBS | Physical layout | Auxiliary equipment | Specific Requirements | 1.7.8 | All parts of the installation are covered by two high speed protection schemes, which shall be independent to avoid common mode failures | 1 | Technical Proposal of 100MW Solar Power Plant.pdfPate 17 | 1 |  |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | [5 empty] | 1 |  | Pass
Zte | JBS | Physical layout | Auxiliary equipment | Specific Requirements | 1.7.8 | The Bidder shall include a fire prevention and response plan | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Zte | JBS | Physical layout | Auxiliary equipment | Specific Requirements | 1.7.8 | The fire prevention and response plan shall include a fire alarm und detection system with a main panel in the control room | 1 | 1. SoC to Bidding Document 30-01-14.pdf Page 97 | 1 | [8 empty] | 1 |  | Pass
Zte | JBS | Physical layout | Auxiliary equipment | Specific Requirements | 1.7.9 | The documentation includes clearly labelled objects and figures annotated in English language. | 1 | 1. SoC to Bidding Document 30-01-14.pdf | 1 | [8 empty] | 1 |  | Pass
Zte | JBS | Physical layout | Auxiliary equipment | Specific Requirements | 1.7.9 | The scope of the documentation shall cover at least the requirements of IEC 62446. | 1 | 1. SoC to Bidding Document 30-01-14.pdf | 1 | [8 empty] | 1 |  | Pass
Zte | JBS | Workflow, Project Management Plan and Timelines | Project schedule / Project management | Project schedule | 1.8.1 | Provide installation schedule in compliance with sub-clause 8.2 of Particular Conditions (Time for Completion is 225 days after Commencement Date). | 1 | 1. Time Schedule for QA Soar Park.pdf | 1 |  |  |  |  | Find sub-clause 8.2 of Particular Conditions |  |  |  | 1 |  | Pass
Zte | JBS | Workflow, Project Management Plan and Timelines | Project schedule / Project management | Project schedule | 1.8.1 | Provide work breakdown structures, activity decomposition and sequencing and dependability with the baseline schedule clearly showing the critical path | 1 | 1. Time Schedule for QA Soar Park.pdf | 1 | [8 empty] | 1 |  | Pass
Zte | JBS | Workflow, Project Management Plan and Timelines | Project schedule / Project management | Project schedule | 1.8.1 | Schedule of tasks | 1 | 1. Time Schedule for QA Soar Park.pdf | 1 | [8 empty] | 1 |  | Pass
Zte | JBS | Workflow, Project Management Plan and Timelines | Project schedule / Project management | Project schedule | 1.8.1 | Interdependencies between the tasks | 1 | 1. Time Schedule for QA Soar Park.pdf | 1 | [8 empty] | 1 |  | Pass
Zte | JBS | Workflow, Project Management Plan and Timelines | Project schedule / Project management | Project schedule | 1.8.1 | Interdependencies of tasks with equipment order and delivery times | 1 | 1. Time Schedule for QA Soar Park.pdf | 1 | [8 empty] | 1 |  | Pass
Zte | JBS | Workflow, Project Management Plan and Timelines | Project schedule / Project management | Project schedule | 1.8.1 | Key milestones to indicate that the progress in on schedule | 1 | 1. Time Schedule for QA Soar Park.pdf | 1 | [8 empty] | 1 |  | Pass
Zte | JBS | Workflow, Project Management Plan and Timelines | Project schedule / Project management | Project schedule | 1.8.1 | Teams, the number and skills of personnel to be deployed for each task | 1 | Implementation proposal-0218.pdf |  |  | 1 | Unclear: We do not understand your proposal, please detail your proposal. Especially confirm that you are compliant with our requested criteria. | [5 empty] | 1 |  | Open
Zte | JBS | Workflow, Project Management Plan and Timelines | Project schedule / Project management | Quality Assurance | 1.8.3 | Quality control of delivered modules | 1 |  |  |  | 1 | Unclear: We do not understand your proposal, please detail your proposal. Especially confirm that you are compliant with our requested criteria. | fail |  |  | C |  | 1 |  | Open
Zte | JBS | Workflow, Project Management Plan and Timelines | Project schedule / Project management | Quality Assurance | 1.8.3 | Inspection of equipment delivery | 1 |  |  |  | 1 | Unclear: We do not understand your proposal, please detail your proposal. Especially confirm that you are compliant with our requested criteria. | fail |  |  | C |  | 1 |  | Open
Zte | JBS | Workflow, Project Management Plan and Timelines | Project schedule / Project management | Quality Assurance | 1.8.3 | Milestones for the completion of civil, mechanical, and electrical works | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | fail |  | dobble to 105 and 111 | C |  | 1 |  | Open
Zte | JBS | Workflow, Project Management Plan and Timelines | Project schedule / Project management | Quality Assurance | 1.8.3 | Risk analysis and mitigation plan | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | fail |  |  | C |  | 1 |  | Open
Zte | JBS | Workflow, Project Management Plan and Timelines | Project schedule / Project management | Quality Assurance | 1.8.3 | System acceptance QA procedure by the Employer | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | fail |  |  | C |  | 1 |  | Open
Zte | JBS | Labelling | General items | Labelling | 1.26 | the ID numbering / coding system shall allow unique identification of all components and be understandable | 1 | 1. SoC to Bidding Document 30-01-14.pdf | 1 |  |  |  |  | Cannot be evaluated at this stage |  |  |  | 1 |  | Pass
Zte | JBS | Labelling | General items | Labelling | 1.26 | Tags shall be weather and UV resistant. | 1 | 1. SoC to Bidding Document 30-01-14.pdf | 1 |  |  |  |  | Cannot be evaluated at this stage |  |  |  | 1 |  | Pass
Zte | JBS | Labelling | General items | Labelling | 1.26 | The ID’s shall correspond to all drawings, plant documentation and control system. | 1 | 1. SoC to Bidding Document 30-01-14.pdf | 1 |  |  |  |  | Cannot be evaluated at this stage |  |  |  | 1 |  | Pass
Zte | JBS | Power plant documentation | Power plant documentation | Quality Assurance | 1.27.1 | The Bidder shall confirm that the complete as-built documentation of the plant will be provided in compliance with IEC 62446. Additionally all module serial numbers shall be listed with their individual location. | 1 | 1. SoC to Bidding Document 30-01-14.pdf | 1 |  |  |  |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  |  |  | 1 |  | Pass
Zte | JBS | Power plant documentation | Power plant documentation | Quality Assurance | 1.27.1 | Flash report list of all modules shall be provided in digital form. | 1 | 1. SoC to Bidding Document 30-01-14.pdf | 1 | [8 empty] | 1 |  | Pass
Zte | JBS | Power plant documentation | Spare parts | Warranty | 1.27.2 | The successful bidder shall provide all warranty spares for a warranty period of 5 years. | 1 | 1. SoC to Bidding Document 30-01-14.pdf | 1 | [8 empty] | 1 |  | Pass
Zte | JBS | Equipment guarantees | Warranty | Guarantees | 1.28 | The overall Guarantee and Power Plant Acceptance Procedures required for the Project are described in Sections 1.3, 1.4, 1.14, 1.18 and Schedule D and shall be met. | 1 | 1. SoC to Bidding Document 30-01-14.pdf | 1 |  |  |  |  | Link |  |  |  | 1 |  | Pass
Zte | JBS | Equipment guarantees | Modules | Guarantees | 1.28.1 | The Successful bidder shall provide a Module warranty of at least 10 years. The performance warranty of the module shall be linear with a fixed factor over 25 years. | 1 | 1. SoC to Bidding Document 30-01-14.pdf | 1 |  |  |  |  | To be discussed |  |  |  | 1 |  | Pass
Zte | JBS | Equipment guarantees | Inverter | Guarantees | 1.28.2 | The Successful Bidder shall provide an Inverter warranty of at least 5 years. A spare parts warranty shall be included for the 25 years operational period. | 1 | 1. SoC to Bidding Document 30-01-14.pdf | 1 | [8 empty] | 1 |  | Pass
Zte | JBS | Equipment guarantees | Mounting | Guarantees | 1.28.3 | The Successful Bidder shall provide a product warranty for the structure of at least 10 years. | 1 | 1. SoC to Bidding Document 30-01-14.pdf | 1 | [8 empty] | 1 |  | Pass
Zte | JBS | Equipment guarantees | Warranty | Guarantees | 1.28.4, 1.6 | A detailed list of all guarantee conditions for the main equipments (beside modules and inverters) shall be provided by the Successful Bidder with the technical offer. The product warranty shall be at least 5 years. | 1 | 1. SoC to Bidding Document 30-01-14.pdf | 1 | [8 empty] | 1 |  | Pass
Zte | JBS | Miscellaneous | Auxiliary systems | Power supply | 1.29.1 | An off-grid power station may need to be provided by the Bidder for commencing the work. Diesel generators shall be arranged by the bidder on its own. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Zte | JBS | Miscellaneous | Project schedule / Project management | Specific Requirements | 1.29.9 | The Bidder shall submit an organizational chart illustrating management and functional relationships among all project team members including consultants, sub-contractors and vendors at each significant stage of the work, such as permitting, design, construction, testing and commissioning and O&M. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Sumec | MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Bills of Materials, BoMs: (glass, encapsulant, backsheet, ribbon, adhesives, cable, junction box, connector) | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Sumec | MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Maximum rated power | 1 |  | 1 | [8 empty] | 1 |  | Pass
Sumec | MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Rated power tolerance | 1 |  | 1 | [8 empty] | 1 |  | Pass
Sumec | MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Minimum efficiency at 200 W/m² (25°, AM 1.5) | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Sumec | MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Materials and workmanship warranty of a minimum of 10 years | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Sumec | MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Power warranty/performance guarantee of a minimum of 25 years: the power output should not fall below 90% within 10 years, and below 80% within 25 years; linear warranty mandatory | 1 |  | 1 | [8 empty] | 1 |  | Pass
Sumec | MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Type of cells comprising the module, and number of cells in series | 1 | Vol I page 270 | 1 | [5 empty] | manufacturer |  |  | 1 |  | Pass
Sumec | MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Voltage at the maximum power point | 1 | Vol I page 270 | 1 | [8 empty] | 1 |  | Pass
Sumec | MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Current at the maximum current point | 1 | Vol I page 270 | 1 | [8 empty] | 1 |  | Pass
Sumec | MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Open-circuit voltage | 1 | Vol I page 270 | 1 | [8 empty] | 1 |  | Pass
Sumec | MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Short-circuit current | 1 | Vol I page 270 | 1 | [8 empty] | 1 |  | Pass
Sumec | MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Maximum system voltage | 1 | Vol I page 270 | 1 | [5 empty] | … at SK-II safety class |  |  | 1 |  | Pass
Sumec | MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Operating temperature range and nominal operating cell temperature NOCT | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | What range is acceptable | There is as small range anyway Will result in the PR losses | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Sumec | MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Tolerance to wind (maximum load) impact (mechanical load) | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  | minimum 2400 Pa | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Sumec | MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Manufacturers installation guidelines | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Sumec | MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Manufacturers confirmation for the suitability of module for specific weather conditions and the high UV-radiation | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  | especially reliability at high UV irridiance / Product warranty | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Sumec | MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Provide guarantees and data sheets (to be transferred to Employer upon COD) | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Sumec | MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Specify number of modules and total MWp to be provided | 1 |  | 1 |  |  |  | taken from Pvsyst Reports |  |  |  |  | 1 |  | Pass
Sumec | MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Degradation Curve from Manufacturer | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Sumec | MAW | Modules | Modules | Standards (as applicable to crystalline silicion or thin-film) | 1.14.3 | IEC 61215 | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? | no, just a statement of compliance | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Sumec | MAW | Modules | Modules | Standards (as applicable to crystalline silicion or thin-film) | 1.14.3 | IEC 61416 | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? | not existing | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Sumec | MAW | Modules | Modules | Standards (as applicable to crystalline silicion or thin-film) | 1.14.3 | IEC 61646 | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? | no, just a statement of compliance | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Sumec | MAW | Modules | Modules | Standards (as applicable to crystalline silicion or thin-film) | 1.14.3 | IEC 61730 | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? | no, just a statement of compliance | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Sumec | MAW | Modules | Modules | Standards (as applicable to crystalline silicion or thin-film) | 1.14.3 | IEC 60364-4-41 | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? | no, just a statement of compliance 'protection against electric shock | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Sumec | MAW | Modules | Modules | Standards (as applicable to crystalline silicion or thin-film) | 1.14.3 | IEC 61701 | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? | no, just a statement of compliance | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Sumec | MAW | Modules | Modules | Standards (as applicable to crystalline silicion or thin-film) | 1.14.3 | IEC 60904-1, IEC 60904-3 | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? | no, just a statement of compliance | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Sumec | MAW | Modules | Modules | Pre-shipment quality assurance | 1.14.4 | Pre-shipment flash tested data Quality assurance for PV modules on-site and in laboratory simulator must meet the class AAA requirements of IEC 60904-9. The sun simulator must be calibrated with a reference cell, which itself was calibrated by a member of the WPVS scheme, with a maximum uncertainty of Isc of 1%. unique barcode (SNr) and labelled performance headlines (P(mpp), I(sc), U(oc), I(mpp), U(mpp) maximum current, maximum voltage Positive power sorting | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Cannot be evaluated at this stage. | compliance necessary | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Sumec | MAW | Modules | Modules | Pre-shipment quality assurance | 1.14.4 | All modules must undergo Electroluminiscense (EL) inspection with a resolution of minimum 4 MPixel prior to shipment. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Cannot be evaluated at this stage. | compliance necessary | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Sumec | MAW | Modules | Modules | Pre-shipment quality assurance | 1.14.4 | A sufficient EVA cross linking has to be verified per production line through a gel content test supervised by an accredited (IEC 17025 or national pendant) independent certified module testing agency. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Cannot be evaluated at this stage. | compliance necessary | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Sumec | MAW | Modules | Modules | Quality assurance on site | 1.14.5 | The modules shall undergo an incoming inspection at arrival on construction site. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Cannot be evaluated at this stage. | stated and accepted | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Sumec | MAW | Modules | Due Diligence | Quality Assurance | 1.14.6 | The bidder will bear the cost of the Quality assurance for PV modules on-site and in laboratory to be carried out by the Employer through an independent technical consultant up to 150,000 USD. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Sumec | MAW | Modules | Modules | Pre-shipment quality assurance | 1.14.7 | Warranties and evidence shall be given by the bidder that their selected modules have been tested for susceptibility to Potential Induced Degradation (PID). | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Sumec | MAW | Modules | Credentials | Project references | 1.14.8 | To show the proven technology a minimum of 500MW of proposed product type series must be in operation and reference projects shall be named. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Related to project references |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Sumec | MAW | DC Cables | DC Cables | Specific Requirements | 1.15.1 | Are Ohmic losses less than 1% at full power? | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | DC: 1.4%, AC: no considered |  | DC+AC losses < 2% | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Sumec | MAW | DC Cables | DC Cables | Design factors to be provided | 1.15.2 | String cable shall be of the following type: single conductor type, copper, 1000 V / Class II (according to protection class II / 1000V, IEC 61140, single core cable, tinned copper conductor, XLPE Insulation, double EVA jacket (resistant to heat and cold, resistant to ozone, UV, oil and chemicals), Temperature: 90 º C (Temperature Max. Allowable: 120 º C), Halogen free | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | It should be in accordance with the inverter values. | possibly 1500V for such system design | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Sumec | MAW | DC Cables | DC Cables | Design factors to be provided | 1.15.2 | Connectors of Modules and string cables shall be connected of self-locking type, have IP65 rating and shall be from same manufacturer and type | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Sumec | MAW | DC Cables | DC Cables | Design factors to be provided | 1.15.2 | The DC main (downstream of combiner box) wiring harness shall have the quality: Aluminum / Copper / 1000 V / Class II | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | It should be in accordance with the inverter values. | possibly 1500V for such system design | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Sumec | MAW | DC Cables | DC Cables | Design factors to be provided | 1.15.2 | Balance of electrical potential | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Need to be disscussed | equipotential bonding earthing mesh | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Sumec | MAW | DC Cables | DC Cables | Design factors to be provided | 1.15.2 | Installation to be verified by measurement-protocols | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Cannot be evaluated at this stage. | blanc protocol | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Sumec | MAW | DC Cables | DC Cables | Design factors to be provided | 1.15.2 | Clear and systematic labelling required | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Sumec | MAW | DC Cables | DC Cables | Design factors to be provided | 1.15.2 | Lifetime of 30 years is assured | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | What proof is required. | Life time test of nonmetal materials IEC 60811-408:2012 / (DIN EN 60811-408; VDE 0473-811-408:2012-12) 30 y assurance never seen until today | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Sumec | MAW | DC Cables | DC Cables | Design factors to be provided | 1.15.2 | Sizing of cables shall be specified according to the number of modules and strings per array | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  | voltage drop calculation | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Sumec | MAW | DC Cables | DC Cables | Standards | 1.15.3 | IEC 60364-1 | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Sumec | MAW | DC Connectors | DC Connectors | Standards | 1.16.2 | EN 50521 | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? | PV Connectors no, just a statement of compliance | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Sumec | MAW | DC Connectors | DC Connectors | Standards | 1.16.2 | IEC 60512 | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? | Connectors E-Systems no, just a statement of compliance | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Sumec | MAW | DC Junction Box | DC Junction Box | Design factors to be provided | 1.17.1 | At least IP54 | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | DC Junction box is applicable in what conditions? | depending on DC Design | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Sumec | MAW | DC Junction Box | DC Junction Box | Design factors to be provided | 1.17.1 | DC fuses shall permit up to maximum 1000 V (or 1500V if designed). String box design, including all operating elements shall satisfy safety requirements | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Will inverter voltage(1500V) effect the maximum voltage(1000V)? | depends on spec of inverter. | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Sumec | MAW | DC Junction Box | DC Junction Box | Design factors to be provided | 1.17.1 | Monitored input-couples | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Sumec | MAW | DC Junction Box | DC Junction Box | Design factors to be provided | 1.17.1 | Class 2 DC surge arrestor | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Sumec | MAW | DC Junction Box | DC Junction Box | Design factors to be provided | 1.17.1 | Dust and heat protection | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Sumec | MAW | DC Junction Box | DC Junction Box | Specifications | 1.17.2 | Current monitoring | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Sumec | MAW | DC Junction Box | DC Junction Box | Specifications | 1.17.2 | Touch-safe protective cover | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Sumec | MAW | DC Junction Box | DC Junction Box | Specifications | 1.17.2, 1.17.1 | Monitoring interface for SCADA | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Sumec | MAW | DC Junction Box | DC Junction Box | Standards | 1.17.3 | EN 61000-6 | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? | EMV no, just a statement of compliance | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Sumec | MAW | DC Junction Box | DC Junction Box | Standards | 1.17.3 | EN 60439-1 | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? | arcing fault / Störlichtbogen Verhalten no, just a statement of compliance | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Sumec | MAW | DC Junction Box | DC Junction Box | Standards | 1.17.3 | EN 50178 | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? | High currat devices no, just a statement of compliance | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Sumec | MAW | Inverters | Warranty | Warranty option | 1.18.1 | The Bidder shall arrange a full-service package for the selected inverters for a product warranty period of 5 years, with an option to cover additional 20 years including provisions for any necessary replacements including O&M service plan guaranteeing 99% availability. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Sumec | MAW | Inverters | Inverters | Strategic Reason for Inverter Selection | 1.18.2 | Balance of System (BOS) costs of inverter and labour | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  | financial bid | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Sumec | MAW | Inverters | Inverters | Strategic Reason for Inverter Selection | 1.18.2 | Dust and heat protection | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  | derating? | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Sumec | MAW | Inverters | Inverters | Strategic Reason for Inverter Selection | 1.18.2 | Timely and effective monitoring at a granular/zoomed-in level | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Sumec | MAW | Inverters | Inverters | Strategic Reason for Inverter Selection | 1.18.2 | Available uptime | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Sumec | MAW | Inverters | Inverters | Strategic Reason for Inverter Selection | 1.18.2 | Concept of protection against overload, short-circuit, grid-failure, internal failure, over-temperature (de-rating), surge protection | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Its too general, needs to be reviewed. | failure codes and consquences (automatic/manual restart, throw away safety devices) | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Sumec | MAW | Inverters | O&M | Guarantees | 1.18.2 | For central inverters concept: the bidder shall ensure with an undertaking from the manufacturer that the concerned skilled staff will be made available at the site within 24 hours of reporting the defect to the manufacturer. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Sumec | MAW | Inverters | Inverters | Functionalities | 1.18.3 | Maximum Power Point Tracking (MPPT) and string/sub-array management | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Sumec | MAW | Inverters | Inverters | Functionalities | 1.18.3 | Matching grid voltage and frequency at point-of-coupling | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Sumec | MAW | Inverters | Inverters | Functionalities | 1.18.3 | Anti-islanding protection | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Sumec | MAW | Inverters | Inverters | Functionalities | 1.18.3 | Voltage regulation through reactive power support: remotely set point control for voltage stability | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | 8.2 needs to ensure these questions are answered in the bids. |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Sumec | MAW | Inverters | Inverters | Functionalities | 1.18.3 | Frequency regulation | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | 8.2 needs to ensure these questions are answered in the bids. |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Sumec | MAW | Inverters | Inverters | Functionalities | 1.18.3 | Voltage and frequency fault ride-through: no disconnection of the connection through voltage dip and change of active power generation, feed-in of reactive power during the fault for voltage stabilisation | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | 8.2 needs to ensure these questions are answered in the bids. |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Sumec | MAW | Inverters | Inverters | Functionalities | 1.18.3 | Limitation of voltage fluctuation due to switching operations and long-term flicker | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | 8.2 needs to ensure these questions are answered in the bids. |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Sumec | MAW | Inverters | Inverters | Functionalities | 1.18.3 | Limitation of short-circuit current | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | 8.2 needs to ensure these questions are answered in the bids. |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Sumec | MAW | Inverters | Inverters | Functionalities | 1.18.3 | Limitation of steady-stage voltage changes to 2% of the nominal value | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Sumec | MAW | Inverters | Inverters | Functionalities | 1.18.3 | Limitation of current harmonics and higher frequency components up to 9 kHz | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Sumec | MAW | Inverters | Inverters | Functionalities | 1.18.3 | Active power control reduction: remotely set point of control in case of network congestions or risk of system collapse, if deemed necessary | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | 8.2 needs to ensure these questions are answered in the bids. |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Sumec | MAW | Inverters | Monitoring | Functionalities | 1.18.3 | Advanced communication, with intelligent alerts/warnings, to the SCADA server | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Sumec | MAW | Inverters | Inverters | Specific Requirements | 1.18.6 | Specifications of table in Schedule C shall be met | 1 |  |  |  | 1 |  |  | Link to table |  | C |  | 1 |  | Open
Sumec | MAW | Inverters | Inverters | Design factors to be provided | 1.18.7 | Input voltage range (The voltage window for MPP tracking shall accommodate the expected degradation of the modules.) | 1 | Vol I page 283 | 1 | [8 empty] | 1 |  | Pass
Sumec | MAW | Inverters | Inverters | Design factors to be provided | 1.18.7 | PV array configuration options: positive ground, negative ground | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Sumec | MAW | Inverters | Inverters | Design factors to be provided | 1.18.7 | Integrated transformer/transformerless / Outside Dry Type Transformer | 1 | Vol I page 283 | 1 | [8 empty] | 1 |  | Pass
Sumec | MAW | Inverters | Inverters | Design factors to be provided | 1.18.7 | Peak efficiency/ Weighted efficiency | 1 | Vol I page 283 | 1 | [8 empty] | 1 |  | Pass
Sumec | MAW | Inverters | Inverters | Design factors to be provided | 1.18.7 | Nominal power | 1 | Vol I page 283 | 1 | [8 empty] | 1 |  | Pass
Sumec | MAW | Inverters | Inverters | Design factors to be provided | 1.18.7 | Nominal output voltage | 1 | Vol I page 283 | 1 | [8 empty] | 1 |  | Pass
Sumec | MAW | Inverters | Inverters | Design factors to be provided | 1.18.7 | Output voltage range | 1 | Vol I page 283 | 1 | [8 empty] | 1 |  | Pass
Sumec | MAW | Inverters | Inverters | Design factors to be provided | 1.18.7 | Maximum output current | 1 | Vol I page 283 | 1 | [8 empty] | 1 |  | Pass
Sumec | MAW | Inverters | Inverters | Design factors to be provided | 1.18.7 | Nominal output frequency, 3-phase | 1 | Vol I page 283 | 1 | [8 empty] | 1 |  | Pass
Sumec | MAW | Inverters | Inverters | Design factors to be provided | 1.18.7 | Operating temperature range | 1 | Vol I page 283 | 1 |  |  |  |  | What is the acceptable range? | 60°C Derating? |  |  | 1 |  | Pass
Sumec | MAW | Inverters | Inverters | Design factors to be provided | 1.18.7 | Cooling method | 1 | Vol I page 283 | 1 |  |  |  | Adaptive forced-air cooling |  |  |  |  | 1 |  | Pass
Sumec | MAW | Inverters | Inverters | Design factors to be provided | 1.18.7 | Detection of insulation faults | 1 | Vol I page 283 | 1 | [8 empty] | 1 |  | Pass
Sumec | MAW | Inverters | Inverters | Design factors to be provided | 1.18.7 | Protection rating: NEMA 3R, IP54/IP55/IP60 | 1 | Vol I page 283 |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | Datenblatt IP-Wert 20 |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Sumec | MAW | Inverters | Inverters | Standards | 1.18.8 | IEEE 1547 | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? | no, just a statement of compliance Interconnecting Distributed Resources | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Sumec | MAW | Inverters | Inverters | Standards | 1.18.8 | TUV, VDE, or equivalent certification of passing the relevant standards | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Sumec | MAW | Inverters | Inverters | Manufacturers confirmation | 1.18.9 | The Bidder shall deliver a manufacturer's confirmation in his Bid for the suitability of the inverter for the specific weather conditions applicable in Bahawalpur Pakistan. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Sumec | MAW | Inverters | Credentials | Project references | 1.18.10 | A minimum of 100 MWp of similar product/type must be in operation and reference projects shall be named. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Sumec | MAW | Inverters | Inverters | Quality Assurance | 1.18.11 | Check of protection against overload, short-circuit, grid-failure, internal failure, over-temperature (de-rating), surge protection, detection of insulation faults of AC Cables. Bidder shall firmly specify the manufacturer, types and length of cables to be installed | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | 8.2 needs to ensure these questions are answered in the bids. |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Sumec | MAW | Inverters | Inverters | Quality Assurance | 1.18.11 | Test run in the field for maximum and EU-efficiency of all Inverters | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | 8.2 needs to ensure these questions are answered in the bids. |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Sumec | MAW | Inverters | Inverters | Quality Assurance | 1.18.11 | Test run and check of MPP tracking of all inverters | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | 8.2 needs to ensure these questions are answered in the bids. |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Sumec | MAW | Inverters | Inverters | Quality Assurance | 1.18.11 | The Bidder shall deliver detailed protocols of performance test run (warm power test) for every single inverter | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Cannot be evaluated at this stage |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Sumec | MAW | Inverters | Inverters | Quality Assurance | 1.18.11 | After commissioning, 1 of 10 inverters will be measured on site (power curve and efficiency) by an approved independent technical consultant on behalf of the Employer. The on-site measurements shall be accepted by the Bidder as average values for all inverters | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Cannot be evaluated at this stage | compliance! | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Sumec | MAW | Inverters | Due diligence | Quality Assurance | 1.18.12 | The Bidder accepts that the cost of the Quality assurance for Inverters to be carried by the Employer through an independent technical consultant shall be taken over by the successful bidder up to an amount of 100,000 USD. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Sumec | JBS | System PR Specification | System PR | O&M | 1.5.2 | The target PR specification at the time of commissioning the System is equal to or greater than 0.75 (75%). | 1 |  |  |  | 1 | The PR of 80.5% does not consider several parameter, see following items. Please calculate new. | [5 empty] | 1 |  | Open
Sumec | JBS | System PR Specification | System PR | Losses included in PR calculation | 1.5.4 | Module Array (temperature dependence, soiling, low light inefficiency, shading, mismatches in array) | 1 | Vol 1 page 294 ff |  |  | 1 | Please calculate new considering shading losses and low light inefficiency losses |  | We don’t understand the question. Kindly clarify. | we want to see these losses specified. Thos need to be aligned with O+M Startegy and System composition |  |  | 1 |  | Open
Sumec | JBS | System PR Specification | System PR | Losses included in PR calculation | 1.5.4 | Inverter (operating efficiency, operating voltage variations, power/voltage levels) | 1 | Vol 1 page 296 ff | 1 |  |  |  |  | We don’t understand the question. Kindly clarify. | see relevant chapter 1.5.4 List of technical losses that make the PR |  |  | 1 |  | Pass
Sumec | JBS | System PR Specification | System PR | Losses included in PR calculation | 1.5.4 | Transformer losses | 1 | Vol 1 page 294 ff | 1 |  |  |  |  | We don’t understand the question. Kindly clarify. | see relevant chapter 1.5.4 List of technical losses that make the PR |  |  | 1 |  | Pass
Sumec | JBS | System PR Specification | System PR | Losses included in PR calculation | 1.5.4 | Ohmic losses in cables | 1 | Vol 1 page 294 ff | 1 |  |  |  |  | We don’t understand the question. Kindly clarify. | see relevant chapter 1.5.4 List of technical losses that make the PR |  |  | 1 |  | Pass
Sumec | JBS | System PR Specification | System PR | Losses included in PR calculation | 1.5.4 | Auxiliary loads | 1 | Vol 1 page 296 ff | 1 |  |  |  |  | We don’t understand the question. Kindly clarify. | see relevant chapter 1.5.4 List of "losses" = auxilary loads from PV Energy that make the PR |  |  | 1 |  | Pass
Sumec | JBS | Basic Scope of Supply | General items | Specific Requirements | 1.6 | The maximum DC voltage shall not exceed 1500 V | 1 | Volume 1 page 8 | 1 | [8 empty] | 1 |  | Pass
Sumec | JBS | Basic Scope of Supply | General items | Specific Requirements | 1.6 | The required AC voltage / frequency at grid connection shall 132 kV/50 Hz | 1 | Vol 1page 311 ff | 1 | [8 empty] | 1 |  | Pass
Sumec | JBS | Basic Scope of Supply | Warranty | Quality Assurance | 1.6 | The Product Warranties shall be given for a duration of at least 5 years | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Cannot be evaluated at this stage. Only to be checked in list of deviations. |  |  |  | 1 |  | Open
Sumec | JBS | Physical layout | System PR | Specific Requirements | 1.7.1, 1.1.8 | Layout calculations of predicted kWh over the system lifetime and PR using the tool PVSyst V5.62 or higher | 1 |  | 1 | [8 empty] | 1 |  | Pass
Sumec | JBS | Physical layout | System PR | Specific Requirements | 1.7.1 | Provide a report using Solar GIS data provided by the Employer | 1 | Vol 1page 249 | 1 |  |  |  |  | Replace 'Report' with ' PV-Syst report'. | 'Report' is original wording in ER in 1.7.1 |  |  | 1 |  | Pass
Sumec | JBS | Physical layout | Layout | Specific Requirements | 1.7.2 | Provide a schematic electrical Single Line Diagram (SLD) of the entire System layout from the modules to the grid-connection, identifying and listing all of the following DC and AC components. | 1 | Vol 3page 4 | 1 | [8 empty] | 1 |  | Pass
Sumec | JBS | Physical layout | Layout | Specific Requirements | 1.7.2 | The system design shall be such as to ensure ease of maintenance and a multiple ring main unit (RMU) philosophy (on MV level) must be followed for circuit breaker configuration. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Sumec | JBS | Physical layout | Physical layout plan | Specific Requirements | 1.7.7 | Floor plans and elevations for all buildings, housing units, containers on site: e.g. , substations, the SCADA operational room, inverters, O&M, storage facilities | 1 | Vol 3page 15 | 1 | [8 empty] | 1 |  | Pass
Sumec | JBS | Physical layout | Physical layout plan | Specific Requirements | 1.7.7 | Detailed view of the distribution of inverters and connections to the PV string/array | 1 | Vol 3page 4 | 1 | [8 empty] | 1 |  | Pass
Sumec | JBS | Physical layout | Physical layout plan | Specific Requirements | 1.7.7 | Detailed top view of the PV mounting structure, including module sizes and spacing between the module rows | 1 | Vol 3page 21 |  |  | 1 | Is the row distance calculated with the lowest sun elevation angle of the year? | [5 empty] | 1 |  | Open
Sumec | JBS | Physical layout | Physical layout plan | Specific Requirements | 1.7.7 | Detailed side and front view of the PV mounting structure | 1 | Vol 3page 21 | 1 | [8 empty] | 1 |  | Pass
Sumec | JBS | Physical layout | Physical layout plan | Specific Requirements | 1.7.7 | Detailed top view of electrical cabling interconnections | 1 |  | 1 | [8 empty] | 1 |  | Pass
Sumec | JBS | Physical layout | Physical layout plan | Specific Requirements | 1.7.7 | Location of the system metering and grid connection point | 1 |  | 1 | [8 empty] | 1 |  | Pass
Sumec | JBS | Physical layout | Auxiliary equipment | Specific Requirements | 1.7.8 | Provide complete indicating, regulating, controlling, protecting and interlocking equipment necessary for safe and efficient operation of the plant and substation, including complete protection scheme. | 1 | Vol 3page 9 | 1 | [8 empty] | 1 |  | Pass
Sumec | JBS | Physical layout | Auxiliary equipment | Specific Requirements | 1.7.8 | The outline of protection schemes shall be shown on the single line diagram (SLD) | 1 |  | 1 | [8 empty] | 1 |  | Pass
Sumec | JBS | Physical layout | Auxiliary equipment | Specific Requirements | 1.7.8 | All parts of the installation are covered by two high speed protection schemes, which shall be independent to avoid common mode failures | 1 | Vol 3page 9 | 1 | [8 empty] | 1 |  | Pass
Sumec | JBS | Physical layout | Auxiliary equipment | Specific Requirements | 1.7.8 | The Bidder shall include a fire prevention and response plan | 1 | Vol 1 page 161 ff; Vol 2 page 320 ff | 1 | [8 empty] | 1 |  | Pass
Sumec | JBS | Physical layout | Auxiliary equipment | Specific Requirements | 1.7.8 | The fire prevention and response plan shall include a fire alarm und detection system with a main panel in the control room | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Sumec | JBS | Physical layout | Auxiliary equipment | Specific Requirements | 1.7.9 | The documentation includes clearly labelled objects and figures annotated in English language. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Sumec | JBS | Physical layout | Auxiliary equipment | Specific Requirements | 1.7.9 | The scope of the documentation shall cover at least the requirements of IEC 62446. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Sumec | JBS | Workflow, Project Management Plan and Timelines | Project schedule / Project management | Project schedule | 1.8.1 | Provide installation schedule in compliance with sub-clause 8.2 of Particular Conditions (Time for Completion is 225 days after Commencement Date). | 1 | Vol 1 page 170 | 1 |  |  |  | 215 Tage | Find sub-clause 8.2 of Particular Conditions |  |  |  | 1 |  | Pass
Sumec | JBS | Workflow, Project Management Plan and Timelines | Project schedule / Project management | Project schedule | 1.8.1 | Provide work breakdown structures, activity decomposition and sequencing and dependability with the baseline schedule clearly showing the critical path | 1 | Vol 1 page 170 | 1 | [8 empty] | 1 |  | Pass
Sumec | JBS | Workflow, Project Management Plan and Timelines | Project schedule / Project management | Project schedule | 1.8.1 | Schedule of tasks | 1 | Vol 1 page 171 ff | 1 | [8 empty] | 1 |  | Pass
Sumec | JBS | Workflow, Project Management Plan and Timelines | Project schedule / Project management | Project schedule | 1.8.1 | Interdependencies between the tasks | 1 | Vol 1 page 170 | 1 | [8 empty] | 1 |  | Pass
Sumec | JBS | Workflow, Project Management Plan and Timelines | Project schedule / Project management | Project schedule | 1.8.1 | Interdependencies of tasks with equipment order and delivery times | 1 |  |  |  | 1 | Please provide a plan with equipment ordering. | [5 empty] | 1 |  | Open
Sumec | JBS | Workflow, Project Management Plan and Timelines | Project schedule / Project management | Project schedule | 1.8.1 | Key milestones to indicate that the progress in on schedule | 1 | Vol 1 page 170 | 1 | [8 empty] | 1 |  | Pass
Sumec | JBS | Workflow, Project Management Plan and Timelines | Project schedule / Project management | Project schedule | 1.8.1 | Teams, the number and skills of personnel to be deployed for each task | 1 | Vol 1 page 48 ff | 1 | [8 empty] | 1 |  | Pass
Sumec | JBS | Workflow, Project Management Plan and Timelines | Project schedule / Project management | Quality Assurance | 1.8.3 | Quality control of delivered modules | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Sumec | JBS | Workflow, Project Management Plan and Timelines | Project schedule / Project management | Quality Assurance | 1.8.3 | Inspection of equipment delivery | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Sumec | JBS | Workflow, Project Management Plan and Timelines | Project schedule / Project management | Quality Assurance | 1.8.3 | Milestones for the completion of civil, mechanical, and electrical works | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  | dobble to 105 and 111 | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Sumec | JBS | Workflow, Project Management Plan and Timelines | Project schedule / Project management | Quality Assurance | 1.8.3 | Risk analysis and mitigation plan | 1 | Vol 1 page 133 | 1 | [8 empty] | 1 |  | Pass
Sumec | JBS | Workflow, Project Management Plan and Timelines | Project schedule / Project management | Quality Assurance | 1.8.3 | System acceptance QA procedure by the Employer | 1 | Vol 1 page 142 |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Sumec | JBS | Labelling | General items | Labelling | 1.26 | the ID numbering / coding system shall allow unique identification of all components and be understandable | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Cannot be evaluated at this stage |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Sumec | JBS | Labelling | General items | Labelling | 1.26 | Tags shall be weather and UV resistant. | 1 | Vol 1 page 99 | 1 |  |  |  |  | Cannot be evaluated at this stage |  |  |  | 1 |  | Pass
Sumec | JBS | Labelling | General items | Labelling | 1.26 | The ID’s shall correspond to all drawings, plant documentation and control system. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Cannot be evaluated at this stage |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Sumec | JBS | Power plant documentation | Power plant documentation | Quality Assurance | 1.27.1 | The Bidder shall confirm that the complete as-built documentation of the plant will be provided in compliance with IEC 62446. Additionally all module serial numbers shall be listed with their individual location. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Sumec | JBS | Power plant documentation | Power plant documentation | Quality Assurance | 1.27.1 | Flash report list of all modules shall be provided in digital form. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Sumec | JBS | Power plant documentation | Spare parts | Warranty | 1.27.2 | The successful bidder shall provide all warranty spares for a warranty period of 5 years. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Sumec | JBS | Equipment guarantees | Warranty | Guarantees | 1.28 | The overall Guarantee and Power Plant Acceptance Procedures required for the Project are described in Sections 1.3, 1.4, 1.14, 1.18 and Schedule D and shall be met. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Link |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Sumec | JBS | Equipment guarantees | Modules | Guarantees | 1.28.1 | The Successful bidder shall provide a Module warranty of at least 10 years. The performance warranty of the module shall be linear with a fixed factor over 25 years. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | To be discussed |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Sumec | JBS | Equipment guarantees | Inverter | Guarantees | 1.28.2 | The Successful Bidder shall provide an Inverter warranty of at least 5 years. A spare parts warranty shall be included for the 25 years operational period. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Sumec | JBS | Equipment guarantees | Mounting | Guarantees | 1.28.3 | The Successful Bidder shall provide a product warranty for the structure of at least 10 years. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Sumec | JBS | Equipment guarantees | Warranty | Guarantees | 1.28.4, 1.6 | A detailed list of all guarantee conditions for the main equipments (beside modules and inverters) shall be provided by the Successful Bidder with the technical offer. The product warranty shall be at least 5 years. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Sumec | JBS | Miscellaneous | Auxiliary systems | Power supply | 1.29.1 | An off-grid power station may need to be provided by the Bidder for commencing the work. Diesel generators shall be arranged by the bidder on its own. | 1 | Vol 1 Page 37 | 1 | [8 empty] | 1 |  | Pass
Sumec | JBS | Miscellaneous | Project schedule / Project management | Specific Requirements | 1.29.9 | The Bidder shall submit an organizational chart illustrating management and functional relationships among all project team members including consultants, sub-contractors and vendors at each significant stage of the work, such as permitting, design, construction, testing and commissioning and O&M. | 1 | Vol 1 Page 35, 45 ff | 1 | [8 empty] | 1 |  | Pass
Chint | JBU | Supervisory Control and Data Acquisition (SCADA) | SCADA | Specific Requirements | 1.9.1 | Safe and redundant archive for operational data. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | General understanding: expressions like "shall", "has to be", "must be" have the meaning of "will be delivered"? Please confirm. |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Chint | JBU | Supervisory Control and Data Acquisition (SCADA) | SCADA | Specific Requirements | 1.9.1 | Remote access to all operational data for independent monitoring purposes shall be possible (NTDC requirements) | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Chint | JBU | Supervisory Control and Data Acquisition (SCADA) | SCADA | Specific Requirements | 1.9.1 | The system has to provide different access-levels with different access rights allocated. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Chint | JBU | Supervisory Control and Data Acquisition (SCADA) | SCADA | Specific Requirements | 1.9.2 | Control room to remotely monitor and manage the whole system, on a 24 x 7 basis, with the capability of Web-based information sharing | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  |  |  | C |  | 1 |  | Open
Chint | JBU | Supervisory Control and Data Acquisition (SCADA) | SCADA | Specific Requirements | 1.9.2 | Alarms/alerts and timely notification of key performance indicators | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Chint | JBU | Supervisory Control and Data Acquisition (SCADA) | SCADA | Specific Requirements | 1.9.2 | Data must be readily available for the fulfilment of all warranties and performance guarantees | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Cannot be evaluated at this stage. | statement | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Chint | JBU | Supervisory Control and Data Acquisition (SCADA) | SCADA | Specific Requirements | 1.9.2 | Data logging at intervals of not less than one minute, processing, transmission, and back-up | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  |  | not more (!) | C |  | 1 |  | Open
Chint | JBU | Supervisory Control and Data Acquisition (SCADA) | SCADA | Specific Requirements | 1.9.2 | Separate inverter, zone, and string level (current and voltage) monitoring | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Chint | JBU | Supervisory Control and Data Acquisition (SCADA) | SCADA | Specific Requirements | 1.9.2 | Back-up power for a minimum of twelve hours | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  |  |  | C |  | 1 |  | Open
Chint | JBU | Supervisory Control and Data Acquisition (SCADA) | SCADA | Specific Requirements | 1.9.2 | Data shall be provided via FTP (Push/Pull) to the Employer | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Chint | JBU | Supervisory Control and Data Acquisition (SCADA) | SCADA | Specific Requirements | 1.9.2 | All communication/data cables outside of buildings must be fiber-optic cables | 1 |  |  |  | 1 | Unclear: We do not understand your proposal, please detail your proposal. Especially confirm that you are compliant with our requested criteria. |  |  |  | U |  | 1 |  | Open
Chint | JBU | Meteorological Sensors | Auxiliary Systems | Specific Requirements | 1.10.1 | Irradiation and temperature measurements are to be recorded at intervals of 15 min or less. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Chint | JBU | Meteorological Sensors | Auxiliary Systems | Specific Requirements | 1.10.1 | The equipment should have the capability of recording and storing data for 24 hours using auxiliary DC power. | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  | Should be priority 1 question |  | C |  | 1 |  | Open
Chint | JBU | Meteorological Sensors | Auxiliary Systems | Specific Requirements | 1.10.2 | The irradiation measurement equipment should be calibrated by an independent certified third party at least every two years. The calibration must be traceable to international standards. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Should be checked in list of deviations |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Chint | JBU | Meteorological Sensors | Auxiliary Systems | Specific Requirements | 1.10.2 | Seven pyranometers shall be placed : three for measuring the horizontal plane irradiation and the others for the in-plane irradiation. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | As in 1.10.2, it is seven pyranometer per system, please clarify the word "per system" | 1.1.1: "100 MWp (DC capacity at Standard Testing Conditions, abbreviated STC … hereinafter called 'the System') " | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Chint | JBU | Meteorological Sensors | Auxiliary Systems | Specific Requirements | 1.10.2 | The pyranometers should conform to the standards of ISO 9060 (SR5: secondary standard) or the WMO classification, and IEC 60904. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Do we need to know some parameter values according to standards mentioned or just a statement of comlience with the standard would be sufficient? | compliance will be necessary, no data due diligence right now. | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Chint | JBU | Meteorological Sensors | Auxiliary Systems | Specific Requirements | 1.10.3 | Ambient air and the module temperature shall be measured at every 5 installed MWp in conformity with IEC 60751 AA | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Chint | JBU | Site Preparation and site access | Site Preparation and site access | Specific Requirements | 1.11.1 | The Bidder shall provide foundations and structures in accordance with the actual soil conditions. | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  |  | refer to Soil study | C |  | 1 |  | Open
Chint | JBU | Earthworks | Site Preparation and site access | Specific Requirements | 1.12 | Within the plant boundary limits, access roads to all stations shall be suitable for heavy load trucks (axle load: min. 12 tonn). | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  |  |  | C |  | 1 |  | Open
Chint | JBU | Earthworks | Site Preparation and site access | Specific Requirements | 1.12 | Position and specification of underground cable connections must be documented during installation | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  | Cannot be avaluated at this stage. |  | C |  | 1 |  | Open
Chint | JBU | Earthworks | Site Preparation and site access | Specific Requirements | 1.12, 1.13.4, 1.7.7 | Cross-sections of foundations for stations shall be provided, including explanation of the foundations laying down, height, penetration, and method of installing foundation posts, mounting fixtures | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | no layouts of station foundations |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Chint | JBU | Earthworks | Site Preparation and site access | Design factors to be provided | 1.12 | All earth works required have to be specified and included in the offer | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  |  |  | C |  | 1 |  | Open
Chint | JBU | Earthworks | Site Preparation and site access | Specific Requirements | 1.12 | After completion of construction and all earthworks ground shall be levelled and stabilized. | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  |  | (maintanance, dust) | C |  | 1 |  | Open
Chint | JBU | Mounting | Mounting | Specific Requirements | 1.13.1 | The system is fixed-tilted. Tilt angle is specified. | 1 |  | 1 | [8 empty] | 1 |  | Pass
Chint | JBU | Mounting | Mounting | Specific Requirements | 1.13.3 | Mounting structure is made of durable material, resistant to sandstorms and compatible with the module frame material so as to avoid any adverse electrolytic/galvanic effects. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Information about materials to be known before evaluation. | right | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Chint | JBU | Mounting | Mounting | Specific Requirements | 1.13.3 | Mounting system resists high wind speeds (up to 40 m/s) | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Chint | JBU | Mounting | Mounting | Specific Requirements | 1.13.3 | Mounting system resists corrosion (passing the salt spray test IEC 61701, among other verification), | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Information about materials to be known before evaluation. | right | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Chint | JBU | Mounting | Mounting | Specific Requirements | 1.13.3 | Mounting system resists UV induced degradation | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Chint | JBU | Mounting | Mounting | Specific Requirements | 1.13.5 | All fastening structures must be verified for durability and resistance to environmental degradation for 25 years | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | What sort of mechanism is required for verification? | Sub structure description / materials double to line 172 - 175 | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Chint | JBU | Mounting | Mounting | Specific Requirements | 1.13.8 | The mounting structures must be earthed | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Chint | JBU | Mounting | Mounting | Specific Requirements | 1.13.9 | Specific site conditions have been considered. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Needs to be discussed. | … specific requirements of the soil conditions Static | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Chint | JBU | Other infrastructure | Auxiliary systems | Design factors to be provided | 1.25.1 | One administration and office building with car port for 10 vehicles shall be provided, with sufficient space for operating personal, control room, security office, regular office rooms for permanent and visiting staff, meeting room, kitchen sanitary systems (toilet, showers separate for male and female), first aid, control room, electrical rooms, etc. The building shall have windows for office rooms and air conditioning system (split units) for all office rooms. | 1 |  | 1 |  |  |  |  | Priority to be discussed |  |  |  | 1 |  | Pass
Chint | JBU | Other infrastructure | Auxiliary systems | Design factors to be provided | 1.25.1 | Warehouse for spare parts and workshop for minor mechanical/electrical works. | 1 |  | 1 | [8 empty] | 1 |  | Pass
Chint | JBU | Other infrastructure | Auxiliary systems | Design factors to be provided | 1.25.1 | Water storage facility for drinking water, sanitary water (sufficient for 1 week) | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Chint | JBU | Other infrastructure | Auxiliary systems | Design factors to be provided | 1.25.1 | Service water system sufficiently sized for cleaning cycle of modules | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Chint | JBU | Other infrastructure | Auxiliary systems | Design factors to be provided | 1.25.1 | Sewage system including sewage disposal for Construction and O&M phase | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Chint | JBU | Other infrastructure | Auxiliary systems | Guarantees | 1.25.4 | All buildings should be designed in accordance with the requirements of the Pakistan Building Code (available at www.pec.org.pk/buildingcode.aspx) and latest Seismic Provisions 2007. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Link to code |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Chint | JBU | Other infrastructure | Auxiliary systems | Security Surveillance System | 1.25.5 | The system shall comply with insurance requirements | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Chint | JBU | Other infrastructure | Auxiliary systems | Security Surveillance System | 1.25.5 | The Bidder shall provide security personnel for 24 h / 7 days a week for the whole year | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Chint | JBU | Other infrastructure | Auxiliary systems | DC Backup System / uninterrupted power supply (UPS) | 1.25.6 | IEC-60051 and IEC-60439 standards apply | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Sumec | RM | Supervisory Control and Data Acquisition (SCADA) | SCADA | Specific Requirements | 1.9.1 | Safe and redundant archive for operational data. | 1 | Vol-III, F7 Vol-I, p321-328 | 1 |  |  | General understanding: expressions like "shall", "has to be", "must be" have the meaning of "will be delivered"? | 10 Ethernet rings /97 Inv. DataCollectorCabinet |  |  | General understanding: expressions like "shall", "has to be", "must be" have the meaning of "will be delivered"? |  | 1 |  | Pass
Sumec | RM | Supervisory Control and Data Acquisition (SCADA) | SCADA | Specific Requirements | 1.9.1 | Remote access to all operational data for independent monitoring purposes shall be possible (NTDC requirements) | 1 |  | 1 | [8 empty] | 1 |  | Pass
Sumec | RM | Supervisory Control and Data Acquisition (SCADA) | SCADA | Specific Requirements | 1.9.1 | The system has to provide different access-levels with different access rights allocated. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Sumec | RM | Supervisory Control and Data Acquisition (SCADA) | SCADA | Specific Requirements | 1.9.2 | Control room to remotely monitor and manage the whole system, on a 24 x 7 basis, with the capability of Web-based information sharing | 1 |  | 1 | [8 empty] | 1 |  | Pass
Sumec | RM | Supervisory Control and Data Acquisition (SCADA) | SCADA | Specific Requirements | 1.9.2 | Alarms/alerts and timely notification of key performance indicators | 1 |  | 1 | [8 empty] | 1 |  | Pass
Sumec | RM | Supervisory Control and Data Acquisition (SCADA) | SCADA | Specific Requirements | 1.9.2 | Data must be readily available for the fulfilment of all warranties and performance guarantees | 1 |  | 1 |  |  |  |  | Cannot be evaluated at this stage. | statement |  |  | 1 |  | Pass
Sumec | RM | Supervisory Control and Data Acquisition (SCADA) | SCADA | Specific Requirements | 1.9.2 | Data logging at intervals of not less than one minute, processing, transmission, and back-up | 1 |  |  |  | 1 |  |  |  | not more (!) |  |  | 1 |  | Open
Sumec | RM | Supervisory Control and Data Acquisition (SCADA) | SCADA | Specific Requirements | 1.9.2 | Separate inverter, zone, and string level (current and voltage) monitoring | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Sumec | RM | Supervisory Control and Data Acquisition (SCADA) | SCADA | Specific Requirements | 1.9.2 | Back-up power for a minimum of twelve hours | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 200Ah means what? |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Sumec | RM | Supervisory Control and Data Acquisition (SCADA) | SCADA | Specific Requirements | 1.9.2 | Data shall be provided via FTP (Push/Pull) to the Employer | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Sumec | RM | Supervisory Control and Data Acquisition (SCADA) | SCADA | Specific Requirements | 1.9.2 | All communication/data cables outside of buildings must be fiber-optic cables | 1 | Vol-I, p23 |  | 1 |  | All communication/data cables outside of buildings must be fiber-optic cables | 45km of DJYVRP2-22-2*1.0 = copper for outside |  |  |  |  | 1 |  | Fail
Sumec | RM | Meteorological Sensors | Auxiliary Systems | Specific Requirements | 1.10.1 | Irradiation and temperature measurements are to be recorded at intervals of 15 min or less. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Sumec | RM | Meteorological Sensors | Auxiliary Systems | Specific Requirements | 1.10.1 | The equipment should have the capability of recording and storing data for 24 hours using auxiliary DC power. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Should be priority 1 question |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Sumec | RM | Meteorological Sensors | Auxiliary Systems | Specific Requirements | 1.10.2 | The irradiation measurement equipment should be calibrated by an independent certified third party at least every two years. The calibration must be traceable to international standards. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Should be checked in list of deviations |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Sumec | RM | Meteorological Sensors | Auxiliary Systems | Specific Requirements | 1.10.2 | Seven pyranometers shall be placed : three for measuring the horizontal plane irradiation and the others for the in-plane irradiation. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | As in 1.10.2, it is seven pyranometer per system, please clarify the word "per system" | 1.1.1: "100 MWp (DC capacity at Standard Testing Conditions, abbreviated STC … hereinafter called 'the System') " | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Sumec | RM | Meteorological Sensors | Auxiliary Systems | Specific Requirements | 1.10.2 | The pyranometers should conform to the standards of ISO 9060 (SR5: secondary standard) or the WMO classification, and IEC 60904. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Do we need to know some parameter values according to standards mentioned or just a statement of comlience with the standard would be sufficient? | compliance will be necessary, no data due diligence right now. | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Sumec | RM | Meteorological Sensors | Auxiliary Systems | Specific Requirements | 1.10.3 | Ambient air and the module temperature shall be measured at every 5 installed MWp in conformity with IEC 60751 AA | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Sumec | RM | Site Preparation and site access | Site Preparation and site access | Specific Requirements | 1.11.1 | The Bidder shall provide foundations and structures in accordance with the actual soil conditions. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | only example for bracket pile not final |  | refer to Soil study | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Sumec | RM | Earthworks | Site Preparation and site access | Specific Requirements | 1.12 | Within the plant boundary limits, access roads to all stations shall be suitable for heavy load trucks (axle load: min. 12 tonn). | 1 | Vol-I, p37 p68 |  |  | 1 |  | Vol-II, p398 exvacation: 42000m³ backfilling: 1500m³ foundation (Stations?): 780m³ |  |  |  |  | 1 |  | Open
Sumec | RM | Earthworks | Site Preparation and site access | Specific Requirements | 1.12 | Position and specification of underground cable connections must be documented during installation | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Cannot be avaluated at this stage. |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Sumec | RM | Earthworks | Site Preparation and site access | Specific Requirements | 1.12, 1.13.4, 1.7.7 | Cross-sections of foundations for stations shall be provided, including explanation of the foundations laying down, height, penetration, and method of installing foundation posts, mounting fixtures | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Sumec | RM | Earthworks | Site Preparation and site access | Design factors to be provided | 1.12 | All earth works required have to be specified and included in the offer | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Sumec | RM | Earthworks | Site Preparation and site access | Specific Requirements | 1.12 | After completion of construction and all earthworks ground shall be levelled and stabilized. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  | (maintanance, dust) | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Sumec | RM | Mounting | Mounting | Specific Requirements | 1.13.1 | The system is fixed-tilted. Tilt angle is specified. | 1 | Vol-II,p396 Vol-I, p80 | 1 |  |  |  | 27° |  |  |  |  | 1 |  | Pass
Sumec | RM | Mounting | Mounting | Specific Requirements | 1.13.3 | Mounting structure is made of durable material, resistant to sandstorms and compatible with the module frame material so as to avoid any adverse electrolytic/galvanic effects. | 1 | Vol-III, F19 |  |  | 1 |  | hot dip galv. Stee | Information about materials to be known before evaluation. | right |  |  | 1 |  | Open
Sumec | RM | Mounting | Mounting | Specific Requirements | 1.13.3 | Mounting system resists high wind speeds (up to 40 m/s) | 1 | Vol-III, F19 |  |  | 1 | [6 empty] | 1 |  | Open
Sumec | RM | Mounting | Mounting | Specific Requirements | 1.13.3 | Mounting system resists corrosion (passing the salt spray test IEC 61701, among other verification), | 1 | Vol-III, F19 |  |  | 1 |  | hot dip galv. Stee | Information about materials to be known before evaluation. | right |  |  | 1 |  | Open
Sumec | RM | Mounting | Mounting | Specific Requirements | 1.13.3 | Mounting system resists UV induced degradation | 1 | Vol-III, F19 |  |  | 1 |  | hot dip galv. Stee |  |  |  |  | 1 |  | Open
Sumec | RM | Mounting | Mounting | Specific Requirements | 1.13.5 | All fastening structures must be verified for durability and resistance to environmental degradation for 25 years | 1 | Vol-III, F19 |  |  | 1 |  | hot dip galv. Steel: Thickness? | What sort of mechanism is required for verification? | Sub structure description / materials double to line 172 - 175 |  |  | 1 |  | Open
Sumec | RM | Mounting | Mounting | Specific Requirements | 1.13.8 | The mounting structures must be earthed | 1 | Vol-III, F19 |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Sumec | RM | Mounting | Mounting | Specific Requirements | 1.13.9 | Specific site conditions have been considered. | 1 | Vol-III, F19 |  |  | 1 |  | "Final geo survey" shall be executed by bidder. Breacket Pile foundation offered | Needs to be discussed. | … specific requirements of the soil conditions Static |  |  | 1 |  | Open
Sumec | RM | Other infrastructure | Auxiliary systems | Design factors to be provided | 1.25.1 | One administration and office building with car port for 10 vehicles shall be provided, with sufficient space for operating personal, control room, security office, regular office rooms for permanent and visiting staff, meeting room, kitchen sanitary systems (toilet, showers separate for male and female), first aid, control room, electrical rooms, etc. The building shall have windows for office rooms and air conditioning system (split units) for all office rooms. | 1 | Vol-III, F2 F12, F13 | 1 |  |  | not applicable |  | Priority to be discussed |  |  |  | 1 |  | Pass
Sumec | RM | Other infrastructure | Auxiliary systems | Design factors to be provided | 1.25.1 | Warehouse for spare parts and workshop for minor mechanical/electrical works. | 1 | Vol-III, F12-13 | 1 |  |  |  | Standard rooms in office buildings |  |  |  |  | 1 |  | Pass
Sumec | RM | Other infrastructure | Auxiliary systems | Design factors to be provided | 1.25.1 | Water storage facility for drinking water, sanitary water (sufficient for 1 week) | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Sumec | RM | Other infrastructure | Auxiliary systems | Design factors to be provided | 1.25.1 | Service water system sufficiently sized for cleaning cycle of modules | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Sumec | RM | Other infrastructure | Auxiliary systems | Design factors to be provided | 1.25.1 | Sewage system including sewage disposal for Construction and O&M phase | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Sumec | RM | Other infrastructure | Auxiliary systems | Guarantees | 1.25.4 | All buildings should be designed in accordance with the requirements of the Pakistan Building Code (available at www.pec.org.pk/buildingcode.aspx) and latest Seismic Provisions 2007. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Link to code |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Sumec | RM | Other infrastructure | Auxiliary systems | Security Surveillance System | 1.25.5 | The system shall comply with insurance requirements | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Sumec | RM | Other infrastructure | Auxiliary systems | Security Surveillance System | 1.25.5 | The Bidder shall provide security personnel for 24 h / 7 days a week for the whole year | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 |  | Open
Sumec | RM | Other infrastructure | Auxiliary systems | DC Backup System / uninterrupted power supply (UPS) | 1.25.6 | IEC-60051 and IEC-60439 standards apply | 1 | Vol-I, p40 |  |  | 1 | Please confirm requiered international standards | All listed standards arer China | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  |  |  | 1 |  | Open
Sumec | GD | Scope of the Bid | General items | Specific Requirements | 1.1.2 | The Offer shall include a list of all vendors and/or sub-contractors for major equipment. | 1 |  |  |  | 1 | [6 empty] | 1 |  | Open
Sumec | GD | Scope of the Bid | General items | Quality Assurance | 1.1.3 | Defect components consequences: If one tested sample fails in one criterion, all items of the same category will be regarded as failed and rejected. | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  | Only to be checked in list of deviations. | yes, we need to be sure that they comply as for most of the critera |  |  | 1 | 1 | Open
Sumec | GD | Scope of the Bid | General items | Guarantees | 1.1.5 | Energy Purchase Agreement (EPA) practices are followed | 1 |  |  |  | 1 | Important reasons: due to current uncertainty of the criteria we accept an open status. Please clarify that yo acknowledge the criteria and comply unless a reason of high importance will not allow you you to comply. In such a situation the parties will seek to agree a compromise. |  | This cannot be evaluated at this stage. | we need a sentence that it should and can only be disregarded for important reasons |  |  | 1 |  | Open
Sumec | GD | Scope of the Bid | Layout | Guarantees | 1.1.6 | The bidder confirms that the system complies with all applicable requirements of the NEPRA Grid Code of Pakistan and its Draft Amendment no. 2 for Solar Power Projects. | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  | Only to be checked in list of deviations. |  |  |  | 1 |  | Open
Sumec | GD | Scope of the Bid | Credentials | EPC | 1.1.9 | The bid includes professional experience of the Bidders in ground mounted utility-scale PV and financial information about their long-term stability | 3 |  | 1 | [8 empty] | 1 |  | Pass
Sumec | GD | Scope of the Bid | General items | Specific Requirements | 1.1.9 | The bid covers the planning of the System design, the required functionality of the System in terms of its sub-systems and components, detailed feature-wise descriptions of the components to be used in the System, the planning of the System installation, its integration, testing, monitoring, commissioning and O&M of the System | 1 |  |  |  | 1 | We can not find all of the requested criteria in your documents. Please confirm that your bid is compliant with all expectations and requirements of Section 6 of the RFP and provide a list with ALL exeptions or alterations. This applies to both, the EOPC And the O&M part. |  | This question should be removed as detailed design of every component/sub-system will be checked and evaluated thoroughly in technical evaluation | no, its an overall critera an need to be met |  |  | 1 | 1 | Open
Sumec | GD | Scope of the Bid | Credentials | EPC | 1.1.10 | The Bidder, or the Lead company in case of JV is a EPC contractor | 1 |  | 1 |  |  |  |  | This is a non-technical question. We suggest such question should be separated from technical questions and placed in checklist for "General/Substantive Responsiveness of Bid" | a question of reliability and experience of solid understanding of the task/System Technology. See also 1.1.10 |  |  | 1 |  | Pass
Sumec | GD | Conditions for Disqualification and Additional Information Required | Credentials | EPC | 1.2.6 | Detailed list of all the sites with the affirmation that the bidder played the leading EPC role in the turnkey installation of these systems. | 3 |  | 1 | [8 empty] | 1 |  | Pass
Sumec | GD | Conditions for Disqualification and Additional Information Required | Credentials | EPC | 1.2.6 | Cumulative MWp of ground mounted PV turnkey installations >5 MWp with stating of actual MWp per project, project location, date of commissioning, module type and Inverter type. | 1 |  | 1 | [5 empty] | experience of Bidder / EPC |  |  | 1 | 1 | Pass
Sumec | GD | Conditions for Disqualification and Additional Information Required | Credentials | EPC | 1.2.6 | References and contact data (mail and phone) from owners of all installations > 5 MW with quotes of the corresponding system Performance Ratios, as well as system performance vs. initial yield assessment per year since the installation. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  | for selection of referenz objects |  |  | 1 | 1 | Open
Sumec | GD | Conditions for Disqualification and Additional Information Required | Credentials | EPC | 1.2.6 | Approval from bidder to owners or owner representatives to answer questions freely regarding the past performance of the bidder and performance of the system against contractual obligations. | 2 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | [5 empty] | 1 |  | Open
Sumec | GD | Conditions for Disqualification and Additional Information Required | Credentials | O&M | 1.2.6 | Cumulative MWp of ground mounted PV installations for which O&M services have been delivered by the bidder or his O&M subcontractor. | 2 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | [5 empty] | 1 |  | Open
Sumec | GD | Conditions for Disqualification and Additional Information Required | Credentials | O&M | 1.2.6 | References, contact data and approval from owners or owner representatives of all installations > 5 MW from bidder or his O&M subcontractor to answer questions freely regarding the past performance of the bidder and performance of the system against contractual obligations. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | [5 empty] | 1 | 1 | Open
Sumec | GD | Technical Bid Evaluation Criteria | Credentials | Guarantees | 1.3.1 | To have met the contractual requirements of the EPC and O&M deliverables including certificate to the effect that the entire equipment is brand new as required vide notification number NEPRA/UTS-01/777-779 dated Jan 21 ,2014, | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Only to be checked in list of deviations. |  |  |  | 1 | 1 | Open
Sumec | GD | Technical Bid Evaluation Criteria | Credentials | EPC | 1.3.1 | the systems have been completed on time and within budget, | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | [5 empty] | 1 | 1 | Open
Sumec | GD | Technical Bid Evaluation Criteria | Credentials | O&M | 1.3.1 | that they have started supplying electricity to the grid and are still operating satisfactorily in 9 out of 10 MW for all the cases | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | [5 empty] | 1 | 1 | Open
Sumec | GD | Technical Bid Evaluation Criteria | Credentials | O&M | 1.3.1 | In case of a non-performance, comprehensible evidence has to be given why this case will not affect this project. | 3 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | [5 empty] | 1 |  | Open
Sumec | GD | Technical Bid Evaluation Criteria | Credentials | O&M | 1.3.2 | Prove at least 100 MW of EPC experience and 50 MW of full O&M experience for a period longer than 24 months. | 1 |  | 1 | [8 empty] | 1 |  | Pass
Sumec | GD | Technical Bid Evaluation Criteria | Due Diligence | Quality Assurance | 1.3.5 | The cost of the due diligence to be carried out by the Employer through an independent technical consultant before contract signature will be taken over by the successful bidder up to an amount of 50,000 USD independent of the result. The due diligence will cover a module factory visit, an inverter factory inspection and a due diligence on the provided financial, EPC and O&M credentials including up to three site visits. | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  | Only to be checked in list of deviations. |  |  |  | 1 |  | Open
Sumec | GD | PR and System Performance Guarantee | System PR | Guarantees | 1.4.1 | A 25 years commitment, in the form of a whole System performance guarantee, is required. The performance guarantee is based on measuring the PR with the actual kWh-AC delivery per year adjusted for the actual POA irradiation for the same period | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  | Only to be checked in list of deviations. |  |  |  | 1 | 1 | Open
Sumec | GD | PR and System Performance Guarantee | System PR | System PR | 1.4.1 | The billing system/metering system will be installed at interconnection point of 132 kV bus bar of HV substation to be installed by the EPC Contractor and the 132 kV Transmission line of NTDC existing at site. | 2 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  | Only to be checked in list of deviations. |  |  |  | 1 |  | Open
Sumec | GD | PR and System Performance Guarantee | System PR | System PR | 1.4.2 | Guaranteed PR values in the form of the Table in 1.4.1 for the acceptance phase and annual output of the PV system shall be specified. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Link to table in Documents sheet |  |  |  | 1 | 1 | Open
Sumec | GD | PR and System Performance Guarantee | System PR | System PR | 1.4.4 | The initial PR will be first measured after the time of commissioning of the completed PV System during the acceptance phase of 30 days. | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  | Cannot be evaluated at this stage. Only to be checked in list of deviations. |  |  |  | 1 | 1 | Open
Sumec | GD | PR and System Performance Guarantee | Compensations | System PR | 1.4.4 | The successful Bidder shall conduct the initial PR test for the daylight hours of at least 30 consecutive days, recording data at a frequency of fifteen minute intervals or less, to validate the guaranteed PR value for acceptance. Any excused downtime (e.g., from Grid Operator ordered shutdowns, grid failure, theft, force majeure) will be excluded from that calculation by an independent consultant (Auditing Body). That day will be taken out and another day added, if the initial PR falls short of the guaranteed PR value, the successful Bidder shall be obliged to identify and rectify the causes for the performance shortfall at their own cost. | 2 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  | Cannot be evaluated at this stage. Only to be checked in list of deviations. |  |  |  | 1 |  | Open
Sumec | GD | PR and System Performance Guarantee | Compensations | System PR | 1.4.4 | If the measured PR within further 30 days does not reach the guaranteed PR, the Employer can demand that the price of the system will be reduced by the percentage of shortfall times 1.2 for liquidated damages or the contractor will have to install more power at its own cost or combination of both. | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  | Cannot be evaluated at this stage. Only to be checked in list of deviations. |  |  |  | 1 | 1 | Open
Sumec | GD | PR and System Performance Guarantee | Compensations | O&M | 1.4.5 | If the annual measured PR falls below the guaranteed PR value according to Table 1.4.1, the liquidated damages will be levied on the successful Bidder at the rate of USD 0.20-per-kWh or the kWh Value the Employer receives for each kWh of shortfall – whichever is higher. Adjustments shall be made for any events outside the control of the O&M operator as grid outages, from grid operator ordered shutdowns, or force majeure events during the year. | 2 |  |  |  | 1 |  |  | Cannot be evaluated at this stage. Only to be checked in list of deviations. | Only to be checked in list of deviations. |  |  | 1 |  | Open
Sumec | GD | PR and System Performance Guarantee | Compensations | O&M | 1.4.5 | In case the PR is higher than the guaranteed PR value, the net value of this excess energy will be shared as follows: 50% towards the asset replacement fund, 25% towards the Employer, 25% towards the O&M contractor | 3 |  |  |  | 1 |  |  | Cannot be evaluated at this stage. Only to be checked in list of deviations. |  |  |  | 1 |  | Open
Sumec | GD | PR and System Performance Guarantee | Compensations | O&M | 1.4.5 | For timely compensation the PR Calculation will be carried out provisionally for each quarter whereby the contractor and employer might jointly agree on different PR values for each quarter. In the last quarter of each calendar year the annual PR compensation of the full year will be carried out and any provisions will be offset by the annual compensation. | 3 |  |  |  | 1 |  |  | Cannot be evaluated at this stage. Only to be checked in list of deviations. |  |  |  | 1 |  | Open
Sumec | GD | PR and System Performance Guarantee | Compensations | O&M | 1.4.6 | If the successful Bidder defaults in being able to provide the O&M services required for the Systems performance guarantee, then it will be liable to cover all costs – but at least in the amount of Liquidated Damages imposed to the Employer by its PPA agreements - incurred by the Employer, including the loss of the guaranteed electricity export to the grid (but at a minimum rate of USD 0.20-per-kWh) for the disrupted period, in finding and hiring a replacement for the purpose. | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  | Cannot be evaluated at this stage. Only to be checked in list of deviations. |  |  |  | 1 | 1 | Open
Juwi | GD | Scope of the Bid | General items | Specific Requirements | 1.1.2 | The Offer shall include a list of all vendors and/or sub-contractors for major equipment. | 1 |  |  |  | 1 | [6 empty] | 1 |  | Open
Juwi | GD | Scope of the Bid | General items | Quality Assurance | 1.1.3 | Defect components consequences: If one tested sample fails in one criterion, all items of the same category will be regarded as failed and rejected. | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  | Only to be checked in list of deviations. | yes, we need to be sure that they comply as for most of the critera |  |  | 1 | 1 | Open
Juwi | GD | Scope of the Bid | General items | Guarantees | 1.1.5 | Energy Purchase Agreement (EPA) practices are followed | 1 |  |  |  | 1 | Important reasons: due to current uncertainty of the criteria we accept an open status. Please clarify that yo acknowledge the criteria and comply unless a reason of high importance will not allow you you to comply. In such a situation the parties will seek to agree a compromise. |  | This cannot be evaluated at this stage. | we need a sentence that it should and can only be disregarded for important reasons |  |  | 1 |  | Open
Juwi | GD | Scope of the Bid | Layout | Guarantees | 1.1.6 | The bidder confirms that the system complies with all applicable requirements of the NEPRA Grid Code of Pakistan and its Draft Amendment no. 2 for Solar Power Projects. | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  | Only to be checked in list of deviations. |  |  |  | 1 |  | Open
Juwi | GD | Scope of the Bid | Credentials | EPC | 1.1.9 | The bid includes professional experience of the Bidders in ground mounted utility-scale PV and financial information about their long-term stability | 3 |  | 1 | [8 empty] | 1 |  | Pass
Juwi | GD | Scope of the Bid | General items | Specific Requirements | 1.1.9 | The bid covers the planning of the System design, the required functionality of the System in terms of its sub-systems and components, detailed feature-wise descriptions of the components to be used in the System, the planning of the System installation, its integration, testing, monitoring, commissioning and O&M of the System | 1 |  |  | 1 |  | We can not find all of the requested criteria in your documents. Please confirm that your bid is compliant with all expectations and requirements of Section 6 of the RFP and provide a list with ALL exeptions or alterations. This applies to both, the EOPC And the O&M part. |  | This question should be removed as detailed design of every component/sub-system will be checked and evaluated thoroughly in technical evaluation | no, its an overall critera an need to be met |  |  | 1 | 1 | Fail
Juwi | GD | Scope of the Bid | Credentials | EPC | 1.1.10 | The Bidder, or the Lead company in case of JV is a EPC contractor | 1 |  | 1 |  |  |  |  | This is a non-technical question. We suggest such question should be separated from technical questions and placed in checklist for "General/Substantive Responsiveness of Bid" | a question of reliability and experience of solid understanding of the task/System Technology. See also 1.1.10 |  |  | 1 |  | Pass
Juwi | GD | Conditions for Disqualification and Additional Information Required | Credentials | EPC | 1.2.6 | Detailed list of all the sites with the affirmation that the bidder played the leading EPC role in the turnkey installation of these systems. | 3 |  | 1 | [8 empty] | 1 |  | Pass
Juwi | GD | Conditions for Disqualification and Additional Information Required | Credentials | EPC | 1.2.6 | Cumulative MWp of ground mounted PV turnkey installations >5 MWp with stating of actual MWp per project, project location, date of commissioning, module type and Inverter type. | 1 |  | 1 | [5 empty] | experience of Bidder / EPC |  |  | 1 | 1 | Pass
Juwi | GD | Conditions for Disqualification and Additional Information Required | Credentials | EPC | 1.2.6 | References and contact data (mail and phone) from owners of all installations > 5 MW with quotes of the corresponding system Performance Ratios, as well as system performance vs. initial yield assessment per year since the installation. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  | for selection of referenz objects |  |  | 1 | 1 | Open
Juwi | GD | Conditions for Disqualification and Additional Information Required | Credentials | EPC | 1.2.6 | Approval from bidder to owners or owner representatives to answer questions freely regarding the past performance of the bidder and performance of the system against contractual obligations. | 2 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | [5 empty] | 1 |  | Open
Juwi | GD | Conditions for Disqualification and Additional Information Required | Credentials | O&M | 1.2.6 | Cumulative MWp of ground mounted PV installations for which O&M services have been delivered by the bidder or his O&M subcontractor. | 2 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | [5 empty] | 1 |  | Open
Juwi | GD | Conditions for Disqualification and Additional Information Required | Credentials | O&M | 1.2.6 | References, contact data and approval from owners or owner representatives of all installations > 5 MW from bidder or his O&M subcontractor to answer questions freely regarding the past performance of the bidder and performance of the system against contractual obligations. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | [5 empty] | 1 | 1 | Open
Juwi | GD | Technical Bid Evaluation Criteria | Credentials | Guarantees | 1.3.1 | To have met the contractual requirements of the EPC and O&M deliverables including certificate to the effect that the entire equipment is brand new as required vide notification number NEPRA/UTS-01/777-779 dated Jan 21 ,2014, | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Only to be checked in list of deviations. |  |  |  | 1 | 1 | Open
Juwi | GD | Technical Bid Evaluation Criteria | Credentials | EPC | 1.3.1 | the systems have been completed on time and within budget, | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | [5 empty] | 1 | 1 | Open
Juwi | GD | Technical Bid Evaluation Criteria | Credentials | O&M | 1.3.1 | that they have started supplying electricity to the grid and are still operating satisfactorily in 9 out of 10 MW for all the cases | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | [5 empty] | 1 | 1 | Open
Juwi | GD | Technical Bid Evaluation Criteria | Credentials | O&M | 1.3.1 | In case of a non-performance, comprehensible evidence has to be given why this case will not affect this project. | 3 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | [5 empty] | 1 |  | Open
Juwi | GD | Technical Bid Evaluation Criteria | Credentials | O&M | 1.3.2 | Prove at least 100 MW of EPC experience and 50 MW of full O&M experience for a period longer than 24 months. | 1 |  | 1 | [8 empty] | 1 |  | Pass
Juwi | GD | Technical Bid Evaluation Criteria | Due Diligence | Quality Assurance | 1.3.5 | The cost of the due diligence to be carried out by the Employer through an independent technical consultant before contract signature will be taken over by the successful bidder up to an amount of 50,000 USD independent of the result. The due diligence will cover a module factory visit, an inverter factory inspection and a due diligence on the provided financial, EPC and O&M credentials including up to three site visits. | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  | Only to be checked in list of deviations. |  |  |  | 1 |  | Open
Juwi | GD | PR and System Performance Guarantee | System PR | Guarantees | 1.4.1 | A 25 years commitment, in the form of a whole System performance guarantee, is required. The performance guarantee is based on measuring the PR with the actual kWh-AC delivery per year adjusted for the actual POA irradiation for the same period | 1 |  |  | 1 |  | Unclear: We do not understand your proposal, please detail your proposal. Especially confirm that you are compliant with our requested criteria. |  | Only to be checked in list of deviations. |  |  |  | 1 | 1 | Fail
Juwi | GD | PR and System Performance Guarantee | System PR | System PR | 1.4.1 | The billing system/metering system will be installed at interconnection point of 132 kV bus bar of HV substation to be installed by the EPC Contractor and the 132 kV Transmission line of NTDC existing at site. | 2 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  | Only to be checked in list of deviations. |  |  |  | 1 |  | Open
Juwi | GD | PR and System Performance Guarantee | System PR | System PR | 1.4.2 | Guaranteed PR values in the form of the Table in 1.4.1 for the acceptance phase and annual output of the PV system shall be specified. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Link to table in Documents sheet |  |  |  | 1 | 1 | Open
Juwi | GD | PR and System Performance Guarantee | System PR | System PR | 1.4.4 | The initial PR will be first measured after the time of commissioning of the completed PV System during the acceptance phase of 30 days. | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  | Cannot be evaluated at this stage. Only to be checked in list of deviations. |  |  |  | 1 | 1 | Open
Juwi | GD | PR and System Performance Guarantee | Compensations | System PR | 1.4.4 | The successful Bidder shall conduct the initial PR test for the daylight hours of at least 30 consecutive days, recording data at a frequency of fifteen minute intervals or less, to validate the guaranteed PR value for acceptance. Any excused downtime (e.g., from Grid Operator ordered shutdowns, grid failure, theft, force majeure) will be excluded from that calculation by an independent consultant (Auditing Body). That day will be taken out and another day added, if the initial PR falls short of the guaranteed PR value, the successful Bidder shall be obliged to identify and rectify the causes for the performance shortfall at their own cost. | 2 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  | Cannot be evaluated at this stage. Only to be checked in list of deviations. |  |  |  | 1 |  | Open
Juwi | GD | PR and System Performance Guarantee | Compensations | System PR | 1.4.4 | If the measured PR within further 30 days does not reach the guaranteed PR, the Employer can demand that the price of the system will be reduced by the percentage of shortfall times 1.2 for liquidated damages or the contractor will have to install more power at its own cost or combination of both. | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  | Cannot be evaluated at this stage. Only to be checked in list of deviations. |  |  |  | 1 | 1 | Open
Juwi | GD | PR and System Performance Guarantee | Compensations | O&M | 1.4.5 | If the annual measured PR falls below the guaranteed PR value according to Table 1.4.1, the liquidated damages will be levied on the successful Bidder at the rate of USD 0.20-per-kWh or the kWh Value the Employer receives for each kWh of shortfall – whichever is higher. Adjustments shall be made for any events outside the control of the O&M operator as grid outages, from grid operator ordered shutdowns, or force majeure events during the year. | 2 |  |  |  | 1 |  |  | Cannot be evaluated at this stage. Only to be checked in list of deviations. | Only to be checked in list of deviations. |  |  | 1 |  | Open
Juwi | GD | PR and System Performance Guarantee | Compensations | O&M | 1.4.5 | In case the PR is higher than the guaranteed PR value, the net value of this excess energy will be shared as follows: 50% towards the asset replacement fund, 25% towards the Employer, 25% towards the O&M contractor | 3 |  |  |  | 1 |  |  | Cannot be evaluated at this stage. Only to be checked in list of deviations. |  |  |  | 1 |  | Open
Juwi | GD | PR and System Performance Guarantee | Compensations | O&M | 1.4.5 | For timely compensation the PR Calculation will be carried out provisionally for each quarter whereby the contractor and employer might jointly agree on different PR values for each quarter. In the last quarter of each calendar year the annual PR compensation of the full year will be carried out and any provisions will be offset by the annual compensation. | 3 |  |  |  | 1 |  |  | Cannot be evaluated at this stage. Only to be checked in list of deviations. |  |  |  | 1 |  | Open
Juwi | GD | PR and System Performance Guarantee | Compensations | O&M | 1.4.6 | If the successful Bidder defaults in being able to provide the O&M services required for the Systems performance guarantee, then it will be liable to cover all costs – but at least in the amount of Liquidated Damages imposed to the Employer by its PPA agreements - incurred by the Employer, including the loss of the guaranteed electricity export to the grid (but at a minimum rate of USD 0.20-per-kWh) for the disrupted period, in finding and hiring a replacement for the purpose. | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  | Cannot be evaluated at this stage. Only to be checked in list of deviations. |  |  |  | 1 | 1 | Open
Zte | GD | Scope of the Bid | General items | Specific Requirements | 1.1.2 | The Offer shall include a list of all vendors and/or sub-contractors for major equipment. | 1 |  |  |  | 1 | [6 empty] | 1 |  | Open
Zte | GD | Scope of the Bid | General items | Quality Assurance | 1.1.3 | Defect components consequences: If one tested sample fails in one criterion, all items of the same category will be regarded as failed and rejected. | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  | Only to be checked in list of deviations. | yes, we need to be sure that they comply as for most of the critera |  |  | 1 | 1 | Open
Zte | GD | Scope of the Bid | General items | Guarantees | 1.1.5 | Energy Purchase Agreement (EPA) practices are followed | 1 |  |  |  | 1 | Important reasons: due to current uncertainty of the criteria we accept an open status. Please clarify that yo acknowledge the criteria and comply unless a reason of high importance will not allow you you to comply. In such a situation the parties will seek to agree a compromise. |  | This cannot be evaluated at this stage. | we need a sentence that it should and can only be disregarded for important reasons |  |  | 1 |  | Open
Zte | GD | Scope of the Bid | Layout | Guarantees | 1.1.6 | The bidder confirms that the system complies with all applicable requirements of the NEPRA Grid Code of Pakistan and its Draft Amendment no. 2 for Solar Power Projects. | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  | Only to be checked in list of deviations. |  |  |  | 1 |  | Open
Zte | GD | Scope of the Bid | Credentials | EPC | 1.1.9 | The bid includes professional experience of the Bidders in ground mounted utility-scale PV and financial information about their long-term stability | 3 |  | 1 | [8 empty] | 1 |  | Pass
Zte | GD | Scope of the Bid | General items | Specific Requirements | 1.1.9 | The bid covers the planning of the System design, the required functionality of the System in terms of its sub-systems and components, detailed feature-wise descriptions of the components to be used in the System, the planning of the System installation, its integration, testing, monitoring, commissioning and O&M of the System | 1 |  |  |  | 1 | We can not find all of the requested criteria in your documents. Please confirm that your bid is compliant with all expectations and requirements of Section 6 of the RFP and provide a list with ALL exeptions or alterations. This applies to both, the EOPC And the O&M part. |  | This question should be removed as detailed design of every component/sub-system will be checked and evaluated thoroughly in technical evaluation | no, its an overall critera an need to be met |  |  | 1 | 1 | Open
Zte | GD | Scope of the Bid | Credentials | EPC | 1.1.10 | The Bidder, or the Lead company in case of JV is a EPC contractor | 1 |  | 1 |  |  |  |  | This is a non-technical question. We suggest such question should be separated from technical questions and placed in checklist for "General/Substantive Responsiveness of Bid" | a question of reliability and experience of solid understanding of the task/System Technology. See also 1.1.10 |  |  | 1 |  | Pass
Zte | GD | Conditions for Disqualification and Additional Information Required | Credentials | EPC | 1.2.6 | Detailed list of all the sites with the affirmation that the bidder played the leading EPC role in the turnkey installation of these systems. | 3 |  | 1 | [8 empty] | 1 |  | Pass
Zte | GD | Conditions for Disqualification and Additional Information Required | Credentials | EPC | 1.2.6 | Cumulative MWp of ground mounted PV turnkey installations >5 MWp with stating of actual MWp per project, project location, date of commissioning, module type and Inverter type. | 1 |  | 1 | [5 empty] | experience of Bidder / EPC |  |  | 1 | 1 | Pass
Zte | GD | Conditions for Disqualification and Additional Information Required | Credentials | EPC | 1.2.6 | References and contact data (mail and phone) from owners of all installations > 5 MW with quotes of the corresponding system Performance Ratios, as well as system performance vs. initial yield assessment per year since the installation. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  | for selection of referenz objects |  |  | 1 | 1 | Open
Zte | GD | Conditions for Disqualification and Additional Information Required | Credentials | EPC | 1.2.6 | Approval from bidder to owners or owner representatives to answer questions freely regarding the past performance of the bidder and performance of the system against contractual obligations. | 2 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | [5 empty] | 1 |  | Open
Zte | GD | Conditions for Disqualification and Additional Information Required | Credentials | O&M | 1.2.6 | Cumulative MWp of ground mounted PV installations for which O&M services have been delivered by the bidder or his O&M subcontractor. | 2 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | [5 empty] | 1 |  | Open
Zte | GD | Conditions for Disqualification and Additional Information Required | Credentials | O&M | 1.2.6 | References, contact data and approval from owners or owner representatives of all installations > 5 MW from bidder or his O&M subcontractor to answer questions freely regarding the past performance of the bidder and performance of the system against contractual obligations. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | [5 empty] | 1 | 1 | Open
Zte | GD | Technical Bid Evaluation Criteria | Credentials | Guarantees | 1.3.1 | To have met the contractual requirements of the EPC and O&M deliverables including certificate to the effect that the entire equipment is brand new as required vide notification number NEPRA/UTS-01/777-779 dated Jan 21 ,2014, | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Only to be checked in list of deviations. |  |  |  | 1 | 1 | Open
Zte | GD | Technical Bid Evaluation Criteria | Credentials | EPC | 1.3.1 | the systems have been completed on time and within budget, | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | [5 empty] | 1 | 1 | Open
Zte | GD | Technical Bid Evaluation Criteria | Credentials | O&M | 1.3.1 | that they have started supplying electricity to the grid and are still operating satisfactorily in 9 out of 10 MW for all the cases | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | [5 empty] | 1 | 1 | Open
Zte | GD | Technical Bid Evaluation Criteria | Credentials | O&M | 1.3.1 | In case of a non-performance, comprehensible evidence has to be given why this case will not affect this project. | 3 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | [5 empty] | 1 |  | Open
Zte | GD | Technical Bid Evaluation Criteria | Credentials | O&M | 1.3.2 | Prove at least 100 MW of EPC experience and 50 MW of full O&M experience for a period longer than 24 months. | 1 |  | 1 | [8 empty] | 1 |  | Pass
Zte | GD | Technical Bid Evaluation Criteria | Due Diligence | Quality Assurance | 1.3.5 | The cost of the due diligence to be carried out by the Employer through an independent technical consultant before contract signature will be taken over by the successful bidder up to an amount of 50,000 USD independent of the result. The due diligence will cover a module factory visit, an inverter factory inspection and a due diligence on the provided financial, EPC and O&M credentials including up to three site visits. | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  | Only to be checked in list of deviations. |  |  |  | 1 |  | Open
Zte | GD | PR and System Performance Guarantee | System PR | Guarantees | 1.4.1 | A 25 years commitment, in the form of a whole System performance guarantee, is required. The performance guarantee is based on measuring the PR with the actual kWh-AC delivery per year adjusted for the actual POA irradiation for the same period | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  | Only to be checked in list of deviations. |  |  |  | 1 | 1 | Open
Zte | GD | PR and System Performance Guarantee | System PR | System PR | 1.4.1 | The billing system/metering system will be installed at interconnection point of 132 kV bus bar of HV substation to be installed by the EPC Contractor and the 132 kV Transmission line of NTDC existing at site. | 2 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  | Only to be checked in list of deviations. |  |  |  | 1 |  | Open
Zte | GD | PR and System Performance Guarantee | System PR | System PR | 1.4.2 | Guaranteed PR values in the form of the Table in 1.4.1 for the acceptance phase and annual output of the PV system shall be specified. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Link to table in Documents sheet |  |  |  | 1 | 1 | Open
Zte | GD | PR and System Performance Guarantee | System PR | System PR | 1.4.4 | The initial PR will be first measured after the time of commissioning of the completed PV System during the acceptance phase of 30 days. | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  | Cannot be evaluated at this stage. Only to be checked in list of deviations. |  |  |  | 1 | 1 | Open
Zte | GD | PR and System Performance Guarantee | Compensations | System PR | 1.4.4 | The successful Bidder shall conduct the initial PR test for the daylight hours of at least 30 consecutive days, recording data at a frequency of fifteen minute intervals or less, to validate the guaranteed PR value for acceptance. Any excused downtime (e.g., from Grid Operator ordered shutdowns, grid failure, theft, force majeure) will be excluded from that calculation by an independent consultant (Auditing Body). That day will be taken out and another day added, if the initial PR falls short of the guaranteed PR value, the successful Bidder shall be obliged to identify and rectify the causes for the performance shortfall at their own cost. | 2 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  | Cannot be evaluated at this stage. Only to be checked in list of deviations. |  |  |  | 1 |  | Open
Zte | GD | PR and System Performance Guarantee | Compensations | System PR | 1.4.4 | If the measured PR within further 30 days does not reach the guaranteed PR, the Employer can demand that the price of the system will be reduced by the percentage of shortfall times 1.2 for liquidated damages or the contractor will have to install more power at its own cost or combination of both. | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  | Cannot be evaluated at this stage. Only to be checked in list of deviations. |  |  |  | 1 | 1 | Open
Zte | GD | PR and System Performance Guarantee | Compensations | O&M | 1.4.5 | If the annual measured PR falls below the guaranteed PR value according to Table 1.4.1, the liquidated damages will be levied on the successful Bidder at the rate of USD 0.20-per-kWh or the kWh Value the Employer receives for each kWh of shortfall – whichever is higher. Adjustments shall be made for any events outside the control of the O&M operator as grid outages, from grid operator ordered shutdowns, or force majeure events during the year. | 2 |  |  |  | 1 |  |  | Cannot be evaluated at this stage. Only to be checked in list of deviations. | Only to be checked in list of deviations. |  |  | 1 |  | Open
Zte | GD | PR and System Performance Guarantee | Compensations | O&M | 1.4.5 | In case the PR is higher than the guaranteed PR value, the net value of this excess energy will be shared as follows: 50% towards the asset replacement fund, 25% towards the Employer, 25% towards the O&M contractor | 3 |  |  |  | 1 |  |  | Cannot be evaluated at this stage. Only to be checked in list of deviations. |  |  |  | 1 |  | Open
Zte | GD | PR and System Performance Guarantee | Compensations | O&M | 1.4.5 | For timely compensation the PR Calculation will be carried out provisionally for each quarter whereby the contractor and employer might jointly agree on different PR values for each quarter. In the last quarter of each calendar year the annual PR compensation of the full year will be carried out and any provisions will be offset by the annual compensation. | 3 |  |  |  | 1 |  |  | Cannot be evaluated at this stage. Only to be checked in list of deviations. |  |  |  | 1 |  | Open
Zte | GD | PR and System Performance Guarantee | Compensations | O&M | 1.4.6 | If the successful Bidder defaults in being able to provide the O&M services required for the Systems performance guarantee, then it will be liable to cover all costs – but at least in the amount of Liquidated Damages imposed to the Employer by its PPA agreements - incurred by the Employer, including the loss of the guaranteed electricity export to the grid (but at a minimum rate of USD 0.20-per-kWh) for the disrupted period, in finding and hiring a replacement for the purpose. | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  | Cannot be evaluated at this stage. Only to be checked in list of deviations. |  |  |  | 1 | 1 | Open
Tbea | GD | Scope of the Bid | General items | Specific Requirements | 1.1.2 | The Offer shall include a list of all vendors and/or sub-contractors for major equipment. | 1 |  |  |  | 1 | [6 empty] | 1 |  | Open
Tbea | GD | Scope of the Bid | General items | Quality Assurance | 1.1.3 | Defect components consequences: If one tested sample fails in one criterion, all items of the same category will be regarded as failed and rejected. | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  | Only to be checked in list of deviations. | yes, we need to be sure that they comply as for most of the critera |  |  | 1 | 1 | Open
Tbea | GD | Scope of the Bid | General items | Guarantees | 1.1.5 | Energy Purchase Agreement (EPA) practices are followed | 1 |  |  |  | 1 | Important reasons: due to current uncertainty of the criteria we accept an open status. Please clarify that yo acknowledge the criteria and comply unless a reason of high importance will not allow you you to comply. In such a situation the parties will seek to agree a compromise. |  | This cannot be evaluated at this stage. | we need a sentence that it should and can only be disregarded for important reasons |  |  | 1 |  | Open
Tbea | GD | Scope of the Bid | Layout | Guarantees | 1.1.6 | The bidder confirms that the system complies with all applicable requirements of the NEPRA Grid Code of Pakistan and its Draft Amendment no. 2 for Solar Power Projects. | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  | Only to be checked in list of deviations. |  |  |  | 1 |  | Open
Tbea | GD | Scope of the Bid | Credentials | EPC | 1.1.9 | The bid includes professional experience of the Bidders in ground mounted utility-scale PV and financial information about their long-term stability | 3 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | GD | Scope of the Bid | General items | Specific Requirements | 1.1.9 | The bid covers the planning of the System design, the required functionality of the System in terms of its sub-systems and components, detailed feature-wise descriptions of the components to be used in the System, the planning of the System installation, its integration, testing, monitoring, commissioning and O&M of the System | 1 |  |  |  | 1 | We can not find all of the requested criteria in your documents. Please confirm that your bid is compliant with all expectations and requirements of Section 6 of the RFP and provide a list with ALL exeptions or alterations. This applies to both, the EOPC And the O&M part. |  | This question should be removed as detailed design of every component/sub-system will be checked and evaluated thoroughly in technical evaluation | no, its an overall critera an need to be met |  |  | 1 | 1 | Open
Tbea | GD | Scope of the Bid | Credentials | EPC | 1.1.10 | The Bidder, or the Lead company in case of JV is a EPC contractor | 1 |  | 1 |  |  |  |  | This is a non-technical question. We suggest such question should be separated from technical questions and placed in checklist for "General/Substantive Responsiveness of Bid" | a question of reliability and experience of solid understanding of the task/System Technology. See also 1.1.10 |  |  | 1 |  | Pass
Tbea | GD | Conditions for Disqualification and Additional Information Required | Credentials | EPC | 1.2.6 | Detailed list of all the sites with the affirmation that the bidder played the leading EPC role in the turnkey installation of these systems. | 3 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | GD | Conditions for Disqualification and Additional Information Required | Credentials | EPC | 1.2.6 | Cumulative MWp of ground mounted PV turnkey installations >5 MWp with stating of actual MWp per project, project location, date of commissioning, module type and Inverter type. | 1 |  | 1 | [5 empty] | experience of Bidder / EPC |  |  | 1 | 1 | Pass
Tbea | GD | Conditions for Disqualification and Additional Information Required | Credentials | EPC | 1.2.6 | References and contact data (mail and phone) from owners of all installations > 5 MW with quotes of the corresponding system Performance Ratios, as well as system performance vs. initial yield assessment per year since the installation. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  | for selection of referenz objects |  |  | 1 | 1 | Open
Tbea | GD | Conditions for Disqualification and Additional Information Required | Credentials | EPC | 1.2.6 | Approval from bidder to owners or owner representatives to answer questions freely regarding the past performance of the bidder and performance of the system against contractual obligations. | 2 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | [5 empty] | 1 |  | Open
Tbea | GD | Conditions for Disqualification and Additional Information Required | Credentials | O&M | 1.2.6 | Cumulative MWp of ground mounted PV installations for which O&M services have been delivered by the bidder or his O&M subcontractor. | 2 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | [5 empty] | 1 |  | Open
Tbea | GD | Conditions for Disqualification and Additional Information Required | Credentials | O&M | 1.2.6 | References, contact data and approval from owners or owner representatives of all installations > 5 MW from bidder or his O&M subcontractor to answer questions freely regarding the past performance of the bidder and performance of the system against contractual obligations. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | [5 empty] | 1 | 1 | Open
Tbea | GD | Technical Bid Evaluation Criteria | Credentials | Guarantees | 1.3.1 | To have met the contractual requirements of the EPC and O&M deliverables including certificate to the effect that the entire equipment is brand new as required vide notification number NEPRA/UTS-01/777-779 dated Jan 21 ,2014, | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Only to be checked in list of deviations. |  |  |  | 1 | 1 | Open
Tbea | GD | Technical Bid Evaluation Criteria | Credentials | EPC | 1.3.1 | the systems have been completed on time and within budget, | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | [5 empty] | 1 | 1 | Open
Tbea | GD | Technical Bid Evaluation Criteria | Credentials | O&M | 1.3.1 | that they have started supplying electricity to the grid and are still operating satisfactorily in 9 out of 10 MW for all the cases | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | [5 empty] | 1 | 1 | Open
Tbea | GD | Technical Bid Evaluation Criteria | Credentials | O&M | 1.3.1 | In case of a non-performance, comprehensible evidence has to be given why this case will not affect this project. | 3 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | [5 empty] | 1 |  | Open
Tbea | GD | Technical Bid Evaluation Criteria | Credentials | O&M | 1.3.2 | Prove at least 100 MW of EPC experience and 50 MW of full O&M experience for a period longer than 24 months. | 1 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | GD | Technical Bid Evaluation Criteria | Due Diligence | Quality Assurance | 1.3.5 | The cost of the due diligence to be carried out by the Employer through an independent technical consultant before contract signature will be taken over by the successful bidder up to an amount of 50,000 USD independent of the result. The due diligence will cover a module factory visit, an inverter factory inspection and a due diligence on the provided financial, EPC and O&M credentials including up to three site visits. | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  | Only to be checked in list of deviations. |  |  |  | 1 |  | Open
Tbea | GD | PR and System Performance Guarantee | System PR | Guarantees | 1.4.1 | A 25 years commitment, in the form of a whole System performance guarantee, is required. The performance guarantee is based on measuring the PR with the actual kWh-AC delivery per year adjusted for the actual POA irradiation for the same period | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  | Only to be checked in list of deviations. |  |  |  | 1 | 1 | Open
Tbea | GD | PR and System Performance Guarantee | System PR | System PR | 1.4.1 | The billing system/metering system will be installed at interconnection point of 132 kV bus bar of HV substation to be installed by the EPC Contractor and the 132 kV Transmission line of NTDC existing at site. | 2 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  | Only to be checked in list of deviations. |  |  |  | 1 |  | Open
Tbea | GD | PR and System Performance Guarantee | System PR | System PR | 1.4.2 | Guaranteed PR values in the form of the Table in 1.4.1 for the acceptance phase and annual output of the PV system shall be specified. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Link to table in Documents sheet |  |  |  | 1 | 1 | Open
Tbea | GD | PR and System Performance Guarantee | System PR | System PR | 1.4.4 | The initial PR will be first measured after the time of commissioning of the completed PV System during the acceptance phase of 30 days. | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  | Cannot be evaluated at this stage. Only to be checked in list of deviations. |  |  |  | 1 | 1 | Open
Tbea | GD | PR and System Performance Guarantee | Compensations | System PR | 1.4.4 | The successful Bidder shall conduct the initial PR test for the daylight hours of at least 30 consecutive days, recording data at a frequency of fifteen minute intervals or less, to validate the guaranteed PR value for acceptance. Any excused downtime (e.g., from Grid Operator ordered shutdowns, grid failure, theft, force majeure) will be excluded from that calculation by an independent consultant (Auditing Body). That day will be taken out and another day added, if the initial PR falls short of the guaranteed PR value, the successful Bidder shall be obliged to identify and rectify the causes for the performance shortfall at their own cost. | 2 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  | Cannot be evaluated at this stage. Only to be checked in list of deviations. |  |  |  | 1 |  | Open
Tbea | GD | PR and System Performance Guarantee | Compensations | System PR | 1.4.4 | If the measured PR within further 30 days does not reach the guaranteed PR, the Employer can demand that the price of the system will be reduced by the percentage of shortfall times 1.2 for liquidated damages or the contractor will have to install more power at its own cost or combination of both. | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  | Cannot be evaluated at this stage. Only to be checked in list of deviations. |  |  |  | 1 | 1 | Open
Tbea | GD | PR and System Performance Guarantee | Compensations | O&M | 1.4.5 | If the annual measured PR falls below the guaranteed PR value according to Table 1.4.1, the liquidated damages will be levied on the successful Bidder at the rate of USD 0.20-per-kWh or the kWh Value the Employer receives for each kWh of shortfall – whichever is higher. Adjustments shall be made for any events outside the control of the O&M operator as grid outages, from grid operator ordered shutdowns, or force majeure events during the year. | 2 |  |  |  | 1 |  |  | Cannot be evaluated at this stage. Only to be checked in list of deviations. | Only to be checked in list of deviations. |  |  | 1 |  | Open
Tbea | GD | PR and System Performance Guarantee | Compensations | O&M | 1.4.5 | In case the PR is higher than the guaranteed PR value, the net value of this excess energy will be shared as follows: 50% towards the asset replacement fund, 25% towards the Employer, 25% towards the O&M contractor | 3 |  |  |  | 1 |  |  | Cannot be evaluated at this stage. Only to be checked in list of deviations. |  |  |  | 1 |  | Open
Tbea | GD | PR and System Performance Guarantee | Compensations | O&M | 1.4.5 | For timely compensation the PR Calculation will be carried out provisionally for each quarter whereby the contractor and employer might jointly agree on different PR values for each quarter. In the last quarter of each calendar year the annual PR compensation of the full year will be carried out and any provisions will be offset by the annual compensation. | 3 |  |  |  | 1 |  |  | Cannot be evaluated at this stage. Only to be checked in list of deviations. |  |  |  | 1 |  | Open
Tbea | GD | PR and System Performance Guarantee | Compensations | O&M | 1.4.6 | If the successful Bidder defaults in being able to provide the O&M services required for the Systems performance guarantee, then it will be liable to cover all costs – but at least in the amount of Liquidated Damages imposed to the Employer by its PPA agreements - incurred by the Employer, including the loss of the guaranteed electricity export to the grid (but at a minimum rate of USD 0.20-per-kWh) for the disrupted period, in finding and hiring a replacement for the purpose. | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  | Cannot be evaluated at this stage. Only to be checked in list of deviations. |  |  |  | 1 | 1 | Open
Chint | GD | Scope of the Bid | General items | Specific Requirements | 1.1.2 | The Offer shall include a list of all vendors and/or sub-contractors for major equipment. | 1 |  | 1 | [8 empty] | 1 |  | Pass
Chint | GD | Scope of the Bid | General items | Quality Assurance | 1.1.3 | Defect components consequences: If one tested sample fails in one criterion, all items of the same category will be regarded as failed and rejected. | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  | Only to be checked in list of deviations. | yes, we need to be sure that they comply as for most of the critera |  |  | 1 | 1 | Open
Chint | GD | Scope of the Bid | General items | Guarantees | 1.1.5 | Energy Purchase Agreement (EPA) practices are followed | 1 |  |  |  | 1 | Important reasons: due to current uncertainty of the criteria we accept an open status. Please clarify that yo acknowledge the criteria and comply unless a reason of high importance will not allow you you to comply. In such a situation the parties will seek to agree a compromise. |  | This cannot be evaluated at this stage. | we need a sentence that it should and can only be disregarded for important reasons |  |  | 1 |  | Open
Chint | GD | Scope of the Bid | Layout | Guarantees | 1.1.6 | The bidder confirms that the system complies with all applicable requirements of the NEPRA Grid Code of Pakistan and its Draft Amendment no. 2 for Solar Power Projects. | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  | Only to be checked in list of deviations. |  |  |  | 1 |  | Open
Chint | GD | Scope of the Bid | Credentials | EPC | 1.1.9 | The bid includes professional experience of the Bidders in ground mounted utility-scale PV and financial information about their long-term stability | 3 |  | 1 | [8 empty] | 1 |  | Pass
Chint | GD | Scope of the Bid | General items | Specific Requirements | 1.1.9 | The bid covers the planning of the System design, the required functionality of the System in terms of its sub-systems and components, detailed feature-wise descriptions of the components to be used in the System, the planning of the System installation, its integration, testing, monitoring, commissioning and O&M of the System | 3 |  |  |  | 1 | We can not find all of the requested criteria in your documents. Please confirm that your bid is compliant with all expectations and requirements of Section 6 of the RFP and provide a list with ALL exeptions or alterations. This applies to both, the EOPC And the O&M part. |  | This question should be removed as detailed design of every component/sub-system will be checked and evaluated thoroughly in technical evaluation | no, its an overall critera an need to be met |  |  | 1 | 1 | Open
Chint | GD | Scope of the Bid | Credentials | EPC | 1.1.10 | The Bidder, or the Lead company in case of JV is a EPC contractor | 1 |  | 1 |  |  |  |  | This is a non-technical question. We suggest such question should be separated from technical questions and placed in checklist for "General/Substantive Responsiveness of Bid" | a question of reliability and experience of solid understanding of the task/System Technology. See also 1.1.10 |  |  | 1 |  | Pass
Chint | GD | Conditions for Disqualification and Additional Information Required | Credentials | EPC | 1.2.6 | Detailed list of all the sites with the affirmation that the bidder played the leading EPC role in the turnkey installation of these systems. | 3 |  | 1 | [8 empty] | 1 |  | Pass
Chint | GD | Conditions for Disqualification and Additional Information Required | Credentials | EPC | 1.2.6 | Cumulative MWp of ground mounted PV turnkey installations >5 MWp with stating of actual MWp per project, project location, date of commissioning, module type and Inverter type. | 1 |  | 1 | [5 empty] | experience of Bidder / EPC |  |  | 1 | 1 | Pass
Chint | GD | Conditions for Disqualification and Additional Information Required | Credentials | EPC | 1.2.6 | References and contact data (mail and phone) from owners of all installations > 5 MW with quotes of the corresponding system Performance Ratios, as well as system performance vs. initial yield assessment per year since the installation. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  | for selection of referenz objects |  |  | 1 | 1 | Open
Chint | GD | Conditions for Disqualification and Additional Information Required | Credentials | EPC | 1.2.6 | Approval from bidder to owners or owner representatives to answer questions freely regarding the past performance of the bidder and performance of the system against contractual obligations. | 2 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | [5 empty] | 1 |  | Open
Chint | GD | Conditions for Disqualification and Additional Information Required | Credentials | O&M | 1.2.6 | Cumulative MWp of ground mounted PV installations for which O&M services have been delivered by the bidder or his O&M subcontractor. | 2 |  | 1 | [8 empty] | 1 |  | Pass
Chint | GD | Conditions for Disqualification and Additional Information Required | Credentials | O&M | 1.2.6 | References, contact data and approval from owners or owner representatives of all installations > 5 MW from bidder or his O&M subcontractor to answer questions freely regarding the past performance of the bidder and performance of the system against contractual obligations. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | [5 empty] | 1 | 1 | Open
Chint | GD | Technical Bid Evaluation Criteria | Credentials | Guarantees | 1.3.1 | To have met the contractual requirements of the EPC and O&M deliverables including certificate to the effect that the entire equipment is brand new as required vide notification number NEPRA/UTS-01/777-779 dated Jan 21 ,2014, | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Only to be checked in list of deviations. |  |  |  | 1 | 1 | Open
Chint | GD | Technical Bid Evaluation Criteria | Credentials | EPC | 1.3.1 | the systems have been completed on time and within budget, | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | [5 empty] | 1 | 1 | Open
Chint | GD | Technical Bid Evaluation Criteria | Credentials | O&M | 1.3.1 | that they have started supplying electricity to the grid and are still operating satisfactorily in 9 out of 10 MW for all the cases | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | [5 empty] | 1 | 1 | Open
Chint | GD | Technical Bid Evaluation Criteria | Credentials | O&M | 1.3.1 | In case of a non-performance, comprehensible evidence has to be given why this case will not affect this project. | 3 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | [5 empty] | 1 |  | Open
Chint | GD | Technical Bid Evaluation Criteria | Credentials | O&M | 1.3.2 | Prove at least 100 MW of EPC experience and 50 MW of full O&M experience for a period longer than 24 months. | 1 |  | 1 | [8 empty] | 1 |  | Pass
Chint | GD | Technical Bid Evaluation Criteria | Due Diligence | Quality Assurance | 1.3.5 | The cost of the due diligence to be carried out by the Employer through an independent technical consultant before contract signature will be taken over by the successful bidder up to an amount of 50,000 USD independent of the result. The due diligence will cover a module factory visit, an inverter factory inspection and a due diligence on the provided financial, EPC and O&M credentials including up to three site visits. | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  | Only to be checked in list of deviations. |  |  |  | 1 |  | Open
Chint | GD | PR and System Performance Guarantee | System PR | Guarantees | 1.4.1 | A 25 years commitment, in the form of a whole System performance guarantee, is required. The performance guarantee is based on measuring the PR with the actual kWh-AC delivery per year adjusted for the actual POA irradiation for the same period | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  | Only to be checked in list of deviations. |  |  |  | 1 | 1 | Open
Chint | GD | PR and System Performance Guarantee | System PR | System PR | 1.4.1 | The billing system/metering system will be installed at interconnection point of 132 kV bus bar of HV substation to be installed by the EPC Contractor and the 132 kV Transmission line of NTDC existing at site. | 2 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  | Only to be checked in list of deviations. |  |  |  | 1 |  | Open
Chint | GD | PR and System Performance Guarantee | System PR | System PR | 1.4.2 | Guaranteed PR values in the form of the Table in 1.4.1 for the acceptance phase and annual output of the PV system shall be specified. | 1 |  | 1 |  |  |  |  | Link to table in Documents sheet |  |  |  | 1 | 1 | Pass
Chint | GD | PR and System Performance Guarantee | System PR | System PR | 1.4.4 | The initial PR will be first measured after the time of commissioning of the completed PV System during the acceptance phase of 30 days. | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  | Cannot be evaluated at this stage. Only to be checked in list of deviations. |  |  |  | 1 | 1 | Open
Chint | GD | PR and System Performance Guarantee | Compensations | System PR | 1.4.4 | The successful Bidder shall conduct the initial PR test for the daylight hours of at least 30 consecutive days, recording data at a frequency of fifteen minute intervals or less, to validate the guaranteed PR value for acceptance. Any excused downtime (e.g., from Grid Operator ordered shutdowns, grid failure, theft, force majeure) will be excluded from that calculation by an independent consultant (Auditing Body). That day will be taken out and another day added, if the initial PR falls short of the guaranteed PR value, the successful Bidder shall be obliged to identify and rectify the causes for the performance shortfall at their own cost. | 2 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  | Cannot be evaluated at this stage. Only to be checked in list of deviations. |  |  |  | 1 |  | Open
Chint | GD | PR and System Performance Guarantee | Compensations | System PR | 1.4.4 | If the measured PR within further 30 days does not reach the guaranteed PR, the Employer can demand that the price of the system will be reduced by the percentage of shortfall times 1.2 for liquidated damages or the contractor will have to install more power at its own cost or combination of both. | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  | Cannot be evaluated at this stage. Only to be checked in list of deviations. |  |  |  | 1 | 1 | Open
Chint | GD | PR and System Performance Guarantee | Compensations | O&M | 1.4.5 | If the annual measured PR falls below the guaranteed PR value according to Table 1.4.1, the liquidated damages will be levied on the successful Bidder at the rate of USD 0.20-per-kWh or the kWh Value the Employer receives for each kWh of shortfall – whichever is higher. Adjustments shall be made for any events outside the control of the O&M operator as grid outages, from grid operator ordered shutdowns, or force majeure events during the year. | 2 |  |  |  | 1 |  |  | Cannot be evaluated at this stage. Only to be checked in list of deviations. | Only to be checked in list of deviations. |  |  | 1 |  | Open
Chint | GD | PR and System Performance Guarantee | Compensations | O&M | 1.4.5 | In case the PR is higher than the guaranteed PR value, the net value of this excess energy will be shared as follows: 50% towards the asset replacement fund, 25% towards the Employer, 25% towards the O&M contractor | 3 |  |  |  | 1 |  |  | Cannot be evaluated at this stage. Only to be checked in list of deviations. |  |  |  | 1 |  | Open
Chint | GD | PR and System Performance Guarantee | Compensations | O&M | 1.4.5 | For timely compensation the PR Calculation will be carried out provisionally for each quarter whereby the contractor and employer might jointly agree on different PR values for each quarter. In the last quarter of each calendar year the annual PR compensation of the full year will be carried out and any provisions will be offset by the annual compensation. | 3 |  |  |  | 1 |  |  | Cannot be evaluated at this stage. Only to be checked in list of deviations. |  |  |  | 1 |  | Open
Chint | GD | PR and System Performance Guarantee | Compensations | O&M | 1.4.6 | If the successful Bidder defaults in being able to provide the O&M services required for the Systems performance guarantee, then it will be liable to cover all costs – but at least in the amount of Liquidated Damages imposed to the Employer by its PPA agreements - incurred by the Employer, including the loss of the guaranteed electricity export to the grid (but at a minimum rate of USD 0.20-per-kWh) for the disrupted period, in finding and hiring a replacement for the purpose. | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  | Cannot be evaluated at this stage. Only to be checked in list of deviations. |  |  |  | 1 | 1 | Open

## JUE (hidden)
Bidder | Expert | Chapter in RfP | Topic | Subtopic | Clause | Question | 1 Vital 2 Valuable 3 Not Important | Link to Bidders Documents | Pass =1 | Fail =1 | Open =1 | Question to bidder for clarification | Comments
Zte | JUE | Scope of the Bid | O&M | General Requirements | 2.1.2 | Responsibility to keep Performance Ratio and Availability at highest levels | 1 |  | 1
Zte | JUE | Scope of the Bid | O&M | General Requirements | 2.1.2 | Preventive maintenance | 2 |  | 1
Zte | JUE | Scope of the Bid | O&M | General Requirements | 2.1.2 | Provision and Installation of spare parts, keeping of spare parts stock (refill of used spares). Reporting of status and consumption to be continuously updated | 2 |  |  |  | 1 | Unclear: We do not understand your proposal, please detail your proposal. Especially confirm that you are compliant with our requested criteria. | not completely described
Zte | JUE | Scope of the Bid | O&M | General Requirements | 2.1.2 | Corrective maintenance with guaranteed response times | 1 |  |  | 1 |  | Unclear: We do not understand your proposal, please detail your proposal. Especially confirm that you are compliant with our requested criteria. | not correct described
Zte | JUE | Scope of the Bid | O&M | General Requirements | 2.1.2 | Daily, monthly and yearly performance and production reporting | 1 |  |  | 1 |  | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | no reporting is described
Zte | JUE | Scope of the Bid | O&M | General Requirements | 2.1.2 | Operation of the Plant (including 24/7 presence of O&M and security staff on the project site). | 1 |  | 1
Zte | JUE | Scope of the Bid | O&M | General Requirements | 2.1.2 | Cleaning of the Plant, preventive and corrective maintenance of the civil works and the fences. | 1 |  |  | 1 |  | Unclear: We do not understand your proposal, please detail your proposal. Especially confirm that you are compliant with our requested criteria. | not correct described
Zte | JUE | Scope of the Bid | O&M | General Requirements | 2.1.2 | Cleaning of Modules and irradiation sensors to prevent dust accumulation to undesirable level. | 1 |  |  | 1 |  | Unclear: We do not understand your proposal, please detail your proposal. Especially confirm that you are compliant with our requested criteria. | not correct described
Zte | JUE | Scope of the Bid | O&M | General Requirements | 2.1.2 | Ordinary road and land maintenance to the extent required for proper maintenance of the Plant. | 3 |  |  | 1 |  | Unclear: We do not understand your proposal, please detail your proposal. Especially confirm that you are compliant with our requested criteria. | not described
Zte | JUE | Scope of the Bid | O&M | General Requirements | 2.1.2 | Smooth functioning of all interconnections and data communications of the system performance | 2 |  |  | 1 |  | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing
Zte | JUE | Scope of the Bid | O&M | General Requirements | 2.1.2 | Optimal level of SCADA monitoring | 1
Zte | JUE | Scope of the Bid | O&M | General Requirements | 2.1.2 | Coordination and compliance with NTDC requirements | 1 |  | 1
Zte | JUE | Scope of the Bid | O&M | General Requirements | 2.1.2 | Maintaining a customer support hotline for the Employer/NTDC | 3 |  |  | 1 |  | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing
Zte | JUE | Scope of the Bid | O&M | General Requirements | 2.1.2 | Providing regular reports of repairs, maintenance, and tests | 3 |  |  | 1 |  | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing
Zte | JUE | Scope of the Bid | O&M | General Requirements | 2.1.2 | Performance variance analysis of the module strings and inverters | 1 |  |  | 1 |  | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing
Zte | JUE | Scope of the Bid | O&M | General Requirements | 2.1.2 | Periodic maintenance of inverter, transformer, combiner boxes etc., according manufacturer's requirements | 1 |  |  | 1 |  | Unclear: We do not understand your proposal, please detail your proposal. Especially confirm that you are compliant with our requested criteria. | no period is described
Zte | JUE | Scope of the Bid | O&M | General Requirements | 2.1.2 | Scheduled maintenance routines: e.g., inspections of modules with polarized sunglasses to check for discolouration, the first signs of de-lamination, loose wires in the electronics, corrosion of mounting structures, erosion | 1 |  | 1
Zte | JUE | Scope of the Bid | O&M | General Requirements | 2.1.2 | Track chronic negative deviations in the module string output, i.e., power tolerances consistently in the negative | 3 |  |  | 1 |  | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing
Zte | JUE | Scope of the Bid | O&M | General Requirements | 2.1.2 | Negotiating a warranty reserve for replacements with the suppliers | 3 |  |  | 1 |  | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing
Zte | JUE | Scope of the Bid | O&M | General Requirements | 2.1.2 | Maintaining adequate reserves for timely replacement | 2 |  |  | 1 |  | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing
Zte | JUE | Scope of the Bid | O&M | General Requirements | 2.1.2 | Insuring products at different levels but for sensible costs; the insurance policy shall not become expensive compared to the replacement cost of the item | 3 |  |  | 1 |  | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing
Zte | JUE | Scope of the Bid | O&M | General Requirements | 2.1.2 | Warranties and insurance policies should be assignable/transferrable to the Employer in case it decides to take over the O&M | 1 |  |  | 1 |  | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing
Zte | JUE | Scope of the Bid | O&M | General Requirements | 2.1.2 | Reporting the monitoring and surveillance system. | 3 |  |  | 1 |  | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing
Zte | JUE | Scope of the Bid | O&M | General Requirements | 2.1.2 | Technical report elaboration. | 3 |  |  | 1 |  | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing
Zte | JUE | Scope of the Bid | O&M | General Requirements | 2.1.2 | On site Security services. | 3 |  |  |  | 1 | Unclear: We do not understand your proposal, please detail your proposal. Especially confirm that you are compliant with our requested criteria. | not completely described
Zte | JUE | Scope of the Bid | O&M | General Requirements | 2.1.2 | Provide all O&M Staff, trained and certified as far as applicable. For security reasons, a 24 h/ 7 days a week staffing of security and maintenance shall be provided. The staffing concept and selected key employees shall be presented to the Employer for approval. | 1 | 2. Operation & Maintenance Services Proposal_v1.0_20140218.pdf 3.1 Page 13 |  | 1 |  |  | 3 3.1 Inspection personnel should be trained and get certificate.
Zte | JUE | Initial Inspection | O&M | General Requirements | 2.2.1 | familiarize himself with the specific plant equipment and specific maintenance requirements / training of staff | 1 | 3. Operation & Maintenance Services Proposal_v1.0_20140218.pdf 3.1 Page 13 |  | 1 |  |  | 3 3.1 Inspection personnel should be trained and get certificate.
Zte | JUE | Initial Inspection | O&M | General Requirements | 2.2.2 | Maintenance routines, inspection check-lists, working files, | 1 |  |  |  | 1 | Unclear: We do not understand your proposal, please detail your proposal. Especially confirm that you are compliant with our requested criteria. | not completely described
Zte | JUE | Initial Inspection | O&M | General Requirements | 2.2.3 | coordinate with the Employer and keep him updated regarding his progress of preparation, status of construction, pending issues of Construction, Commissioning and testing. | 2 |  |  | 1 |  |  | Cannot be evaluated at this stage
Zte | JUE | Bi-annual inspection | O&M | PV Generator | 2.3.1 | 100% visual inspection of modules regarding damage in spring | 1 |  |  |  | 1 | Unclear: We do not understand your proposal, please detail your proposal. Especially confirm that you are compliant with our requested criteria. | not completely described
Zte | JUE | Bi-annual inspection | O&M | PV Generator | 2.3.1 | Random visual inspection of modules regarding damage in autumn | 2 | [5 empty] | Cannot be evaluated at this stage
Zte | JUE | Bi-annual inspection | O&M | PV Generator | 2.3.1 | Random check of module clip with respect to loosening; if necessary replacement of clips (min. 10%, documentation of location, during 5 years inspection of whole PV plant) | 2 |  |  | 1 |  |  | Cannot be evaluated at this stage missing
Zte | JUE | Bi-annual inspection | O&M | PV Generator | 2.3.1 | Random testing of the steadiness of the mounting foundation/system and random inspection regarding corrosion at substructure (min. 10%, documentation of location, during 10 years inspection of whole PV plant) | 1 |  |  | 1 |  | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing
Zte | JUE | Bi-annual inspection | O&M | PV Generator | 2.3.1 | Documentation of wear and tear of moving components, monitoring of dust intrusion and corrosion. | 2 |  | 1
Zte | JUE | Bi-annual inspection | O&M | PV Generator | 2.3.1 | Cleaning of sensors and switches | 1 |  |  | 1 |  |  | sensors shall be done by independent Meteo Station Operator
Zte | JUE | Bi-annual inspection | O&M | PV Generator | 2.3.1 | Cleaning of all modules | 1 |  | 1
Zte | JUE | Bi-annual inspection | O&M | Inverter (100%) | 2.3.2 | Functional check of ventilator system of inverter station | 1 |  |  | 1 |  | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing
Zte | JUE | Bi-annual inspection | O&M | Inverter (100%) | 2.3.2 | Cleaning of the filter mats in the air leaks | 2 |  |  | 1 |  | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing
Zte | JUE | Bi-annual inspection | O&M | Inverter (100%) | 2.3.2 | Replacement of dirty filter mats | 2 |  |  | 1 |  | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing
Zte | JUE | Bi-annual inspection | O&M | Inverter (100%) | 2.3.2 | Inspection of the interior of the electrical cabinet regarding dust deposit, dirtiness, humidity, water penetration from outside. If necessary the cabinet has to be cleaned. | 1 |  | 1
Zte | JUE | Bi-annual inspection | O&M | Inverter (100%) | 2.3.2 | Testing of inverter features according to maintenance schedule of manufacturer. | 1 |  |  | 1 |  | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing
Zte | JUE | Bi-annual inspection | O&M | Inverter (100%) | 2.3.2 | Maintenance of inverters according to manufacturer's instruction. | 1 |  |  | 1 |  | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing
Zte | JUE | Bi-annual inspection | O&M | Monitoring | 2.3.3 | Functionality testing of the monitoring system | 3 |  |  | 1 |  | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing
Zte | JUE | Bi-annual inspection | O&M | Maintenance | 2.3.3 | Maintenance of all Power plant components according to manufacturer's instructions | 1 |  |  | 1 |  | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing
Zte | JUE | Main Annual Inspection | O&M | PV Generator | 2.4.1 | Visual inspection of all accessible cable trenches and cable trays regarding damage | 1 |  | 1
Zte | JUE | Main Annual Inspection | O&M | PV Generator | 2.4.1 | Visual inspection and random testing of string connector (min. 10% with Documentation of location , during 10 years testing of whole PV plant) | 1 |  | 1
Zte | JUE | Main Annual Inspection | O&M | PV Generator | 2.4.1 | Inspection of DC distribution box: Visual inspection of all clamps and degree of pollution. Testing of over-voltage protection | 1 |  | 1
Zte | JUE | Main Annual Inspection | O&M | PV Generator | 2.4.1 | Maintenance of sensors based on manufacturer’s instructions | 1 |  |  | 1
Zte | JUE | Main Annual Inspection | O&M | Inverter (100%) | 2.4.2 | Test of the internal miniature circuit breakers and power switch, test of emergency shut-off | 1 |  | 1
Zte | JUE | Main Annual Inspection | O&M | Inverter (100%) | 2.4.2 | Visual inspection of all fuses | 1 |  |  |  | 1 | Unclear: We do not understand your proposal, please detail your proposal. Especially confirm that you are compliant with our requested criteria. | not completely described
Zte | JUE | Main Annual Inspection | O&M | Inverter (100%) | 2.4.2 | Inspection of over-voltage protection and upstream fuses regarding external damage | 1 |  |  | 1 |  | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing
Zte | JUE | Main Annual Inspection | O&M | Inverter (100%) | 2.4.2 | Functional check of internal and external over- and under-voltage monitoring through operation of test terminal | 1 |  |  | 1 |  | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing
Zte | JUE | Main Annual Inspection | O&M | Inverter (100%) | 2.4.2 | Functional check of insulation monitoring | 1 |  |  | 1 |  | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing
Zte | JUE | Main Annual Inspection | O&M | Inverter (100%) | 2.4.2 | Check of control and auxiliary voltages | 2 |  | 1
Zte | JUE | Main Annual Inspection | O&M | Inverter (100%) | 2.4.2 | Check of the safety circuit for the interruption of the AC-grid protection in the case of failure (emergency shut-off, over-/ under-voltage, over temperature, etc.) based on the local conditions | 1 |  | 1
Zte | JUE | Main Annual Inspection | O&M | Inverter (100%) | 2.4.2 | Visual inspection of AC and DC clamps regarding tightness and colouring, tightening of clamps | 1 |  | 1
Zte | JUE | Main Annual Inspection | O&M | Inverter (100%) | 2.4.2 | Maintenance of inverters according to manufacturer instruction | 1 |  |  |  | 1 | Unclear: We do not understand your proposal, please detail your proposal. Especially confirm that you are compliant with our requested criteria. | not completely described
Zte | JUE | Main Annual Inspection | O&M | Roads | 2.4.3 | Visual inspection of roads within the PV plant shall be carried out to ascertain that these are maintained in good condition for the intended purpose. | 2 |  |  | 1 |  | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing
Zte | JUE | Main Annual Inspection | O&M | Substation and Transmission Line | 2.4.4 | Visual inspection of transformer and switchboard rooms and cleaning if necessary | 1 |  |  |  | 1 | Unclear: We do not understand your proposal, please detail your proposal. Especially confirm that you are compliant with our requested criteria. | not completely described
Zte | JUE | Main Annual Inspection | O&M | Substation and Transmission Line | 2.4.4 | Visual inspection of Transmission Line and report of damage to the grid operator | 2 |  |  |  | 1 | Unclear: We do not understand your proposal, please detail your proposal. Especially confirm that you are compliant with our requested criteria. | not completely described
Zte | JUE | Main Annual Inspection | O&M | Substation and Transmission Line | 2.4.4 | Maintenance of substation and transmission line according to manufacturer instruction | 1 |  |  |  | 1 | Unclear: We do not understand your proposal, please detail your proposal. Especially confirm that you are compliant with our requested criteria. | not completely described
Zte | JUE | Main Annual Inspection | O&M | Auxiliary system | 2.4.5 | Inspection of security system inclusive fence, all gates, all cameras etc. Random test of the fence fastening, if necessary retightening of the screws | 2 |  |  | 1 |  | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing
Zte | JUE | Main Annual Inspection | O&M | Auxiliary system | 2.4.5 | If existing: inspection of requirements out of the building permit | 2 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing
Zte | JUE | Main Annual Inspection | O&M | Auxiliary system | 2.4.5 | Maintenance of all components according to manufacturer instruction | 1 |  |  | 1 |  | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing
Zte | JUE | Special inspection (every 4 years) | O&M | Specific Requirements | 2.5.1 | Measurement of inverters and generators according to recognized international standards and according to results from commissioning certificates (insulation, loop resistance, earthing, DC-open circuit voltage) | 2 |  |  | 1 |  | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing
Zte | JUE | Special inspection (every 4 years) | O&M | Specific Requirements | 2.5.1 | Protection systems of medium voltage switching panels of the stations | 1 |  |  | 1 |  | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing
Zte | JUE | Special inspection (every 4 years) | O&M | Specific Requirements | 2.5.1 | Oil check of transformers | 1 |  |  | 1 |  | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing
Zte | JUE | Special inspection (every 4 years) | O&M | Specific Requirements | 2.5.1 | Control of station equipment | 2 |  | 1
Zte | JUE | Deactivation | O&M | Allowed deactivation periods | 2.6.1 | Times with irradiation level < 300 W/m² | 2 |  |  | 1 |  | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing
Zte | JUE | Deactivation | O&M | Allowed deactivation periods | 2.6.1 | Approved by The Employer to ensure consideration of Employer's obligations | 2 |  |  | 1 |  | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing
Zte | JUE | Deactivation | O&M | Allowed deactivation periods | 2.6.1 | Approved from grid operator | 2 |  |  | 1 |  | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing
Zte | JUE | Deactivation | O&M | Specific Requirements | 2.6.2 | All deactivations during maintenance works shall be completely documented. | 2 |  |  | 1 |  | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing
Zte | JUE | Deactivation | O&M | Specific Requirements | 2.6.3 | Deactivation shall not be considered as permitted downtime. | 2 |  |  | 1 |  | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing
Zte | JUE | Change of Inspection and Maintenance Work procedures | O&M | Specific Requirements | 2.7 | work in accordance with all applicable laws | 2 |  |  | 1 |  | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing
Zte | JUE | Performance of maintenance and repair works | O&M | Specific Requirements | 2.8.1 | Corresponding regulations of the respective component manufacturer shall have to be followed during maintenance works | 1 |  |  | 1 |  | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing
Zte | JUE | Performance of maintenance and repair works | O&M | Specific Requirements | 2.8.2 | Report document for maintenance works (blanc sample requiered for bid) | 1 |  |  | 1 |  | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing
Zte | JUE | Performance of maintenance and repair works | O&M | Specific Requirements | 2.8.3 | Observe and respect the maintenance and operation specifications of the manufacturer of the components | 3 |  |  | 1 |  | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing
Zte | JUE | Performance of maintenance and repair works | O&M | Specific Requirements | 2.8.4 | Observe and respect the local law, regulations and international PV standards. | 3 |  |  | 1 |  | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing
Zte | JUE | Performance of maintenance and repair works | O&M | Specific Requirements | 2.8.5 | During his work the Bidder shall be held responsible for the public safety of the PV plant | 2 |  |  | 1 |  | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing
Zte | JUE | On-site monitoring | O&M | Specific Requirements | 2.9.1 | Permanent (24/7) staffing of the Power Plant, consisting of security and O&M personnel. | 1 |  | 1
Zte | JUE | On-site monitoring | O&M | Specific Requirements | 2.9.2 | Bidder shall arrange service contracts with specialized sub-contractors | 2 |  |  | 1 |  | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing
Zte | JUE | On-site monitoring | O&M | Specific Requirements | 2.9.3 | All operational data shall be logged on-site in parallel to the remote data storage | 2 |  |  | 1 |  | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing
Zte | JUE | On-site monitoring | O&M | Specific Requirements | 2.9.4 | The data of irradiation sensors shall be monitored by an independent expert on a continuous basis | 2 |  |  | 1 |  | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing
Zte | JUE | Remote Supervision | O&M | Specific Requirements | 2.10.1 | On-call service provided for the Employer for availability outside business hours and during weekends (24/7). | 1 |  |  | 1 |  | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing
Zte | JUE | Remote Supervision | O&M | Specific Requirements | 2.10.2 | Any reductions in performance shall have to be logged. | 1 |  |  | 1 |  | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing
Zte | JUE | Remote Supervision | O&M | Specific Requirements | 2.10.3 | The data will comprise, apart from electrical parameters of the PV plant: currents, voltages, irradiation values, kind and period of reductions in performance such as curtailment by the grid operator | 2 |  |  | 1 |  | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing
Zte | JUE | Remote Supervision | O&M | Specific Requirements | 2.10.4 | The data shall present the status of the plant such as the performance ratio annual overview and the current feed-in power | 2 |  |  | 1 |  | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing
Zte | JUE | Remote Supervision | O&M | Specific Requirements | 2.10.5 | The remote supervision shall also control the operation of the PV plant. | 2 |  |  |  | 1 | Unclear: We do not understand your proposal, please detail your proposal. Especially confirm that you are compliant with our requested criteria. | not completely described
Zte | JUE | Remote Supervision | O&M | Specific Requirements | 2.10.6 | The remote supervision shall also include the taking of measures for removal of faults. | 2 |  |  |  | 1 | Unclear: We do not understand your proposal, please detail your proposal. Especially confirm that you are compliant with our requested criteria. | not completely described
Zte | JUE | Remote Supervision | O&M | Specific Requirements | 2.10.7 | The Bidder shall provide to the Employer permanent online access to the power plant control system for parallel monitoring | 1
Zte | JUE | Remote Supervision | O&M | Specific Requirements | 2.10.8 | Monthly / quarterly and annual reports based on the data of the remote supervision provided to the Employer 4 weeks after the last period of reporting at the latest. | 1 |  |  | 1 |  | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing
Zte | JUE | Remote Supervision | O&M | Specific Requirements | 2.10.9 | The fees for telephone connection and/or data transfer services are included in the annual remuneration. | 2 |  |  | 1 |  | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing
Zte | JUE | Reaction to Fault Messages / Response Times | O&M | Specific Requirements | 2.11.1 | Every fault message has to be registered in the monitoring software. According to the fault message, the Bidder shall issue a fault diagnosis within a response time of 2 hours (24/7) | 1 |  |  |  | 1 | Unclear: We do not understand your proposal, please detail your proposal. Especially confirm that you are compliant with our requested criteria. | not completely described
Zte | JUE | Reaction to Fault Messages / Response Times | O&M | Specific Requirements | 2.11.2 | profit relevant Fault Events: Downtime registration/ reasons/ repair/ in monthly report (blanc of monthly report?) | 1 |  |  | 1 |  | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing
Zte | JUE | Fault Management / Warranty defects | O&M | Specific Requirements | 2.12.1 | Fault Management: all handling and communication | 2 |  |  | 1 |  | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing
Zte | JUE | Fault Management / Warranty defects | O&M | Specific Requirements | 2.12.2 | Fault Management: Handling / correspondence with third parties | 2 |  |  | 1 |  | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing
Zte | JUE | Fault Management / Warranty defects | O&M | Specific Requirements | 2.12.3 | Fault Management = without repair works | 3 |  |  | 1 |  | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing
Zte | JUE | Fault Management / Warranty defects | O&M | Specific Requirements | 2.12.4 | Product warranties in favour of contractor / Bidder (responsible) to claim all warranties for at least 5 years | 1 |  |  | 1 |  | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing
Zte | JUE | Fault Management / Warranty defects | O&M | Specific Requirements | 2.12.5 | Operational defects, which are not considered as warranty defects - see repair works section below | 1 |  |  | 1 |  | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing
Zte | JUE | Fault Management / Warranty defects | O&M | Specific Requirements | 2.12.6 | All defects shall be documented within the same day of detection, | 2 |  |  | 1 |  | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing
Zte | JUE | Fault Calls | O&M | Specific Requirements | 2.13.1 | The scope of service shall include any working times for all fault calls including travelling times and costs. | 1 |  |  |  | 1 | Unclear: We do not understand your proposal, please detail your proposal. Especially confirm that you are compliant with our requested criteria. | not completely described
Zte | JUE | Fault Calls | O&M | Specific Requirements | 2.13.2 | The minimum response time in case of failure must meet the EPA requirements | 1 |  |  | 1 |  | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing
Zte | JUE | Fault Calls | O&M | Specific Requirements | 2.13.2 | --> Time Model: Response Times for Priorities 1-3 (12h / 24h / 1 week) | 1 |  |  | 1 |  | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing
Zte | JUE | Fault Calls | O&M | Specific Requirements | 2.13.3 | failure time response does not match the response time of EPA >> failure time response does not match the response time of EPA | 3 |  |  | 1 |  | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing
Zte | JUE | Fault Calls | O&M | Specific Requirements | 2.13.4 | The fault call shall include the fault diagnosis on site as well as an immediate error correction if possible. The fault shall have to be corrected within the response time and, failing this, a diagnosis of the fault has to be effect indicating further measures. | 2 |  |  | 1 |  | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing
Zte | JUE | Fault Calls | O&M | Specific Requirements | 2.13.5 | Fault calls can be performed without prior consent of the Employer. | 3 |  |  | 1 |  | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing
Zte | JUE | Fault Calls | O&M | Specific Requirements | 2.13.6 | If the elimination of faults is not possible within the response time / and additional travelling, this is Repair Work | 3 |  |  | 1 |  | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing
Zte | JUE | Spare Parts and Tools | O&M | Specific Requirements | 2.14 | provide the necessary set of spare parts and maintenance tools as required to perform the services | 1 |  |  | 1 |  | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing
Zte | JUE | Spare Parts and Tools | O&M | Specific Requirements | 2.14.1 | cover all cost for supply and re-stocking of spare parts from his annual remuneration. | 1 |  |  | 1 |  | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing
Zte | JUE | Spare Parts and Tools | O&M | Specific Requirements | 2.14.2 | refill spare parts immediately after consumption | 2 |  |  | 1 |  | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing
Zte | JUE | Reduced Output of the Plant | O&M | Specific Requirements | 2.15 | Monthly comparison of the specific performance of all measuring channels among each other. 5% reduced output results in general check of all the channels and shall be documented. | 1 |  |  | 1 |  | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing
Zte | JUE | Reduced Output of the Plant | O&M | Specific Requirements | 2.15.1 | Identified reduced output shall be justified. Reduced output shall be recovered and liquidated damages determined. | 1 |  |  | 1 |  |  | missing liquidated --> means --> performance
Zte | JUE | Repair time and cost | O&M | Specific Requirements | 2.16 | Repair times are considered as part of the availability guaranty of the Bidder. All cost of repair shall be part of the Bidders annual remuneration. For the avoidance of doubt that includes any repairs due to lightening, theft and vandalism. | 1 |  |  | 1 |  | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing
Zte | JUE | Working Time | O&M | Specific Requirements | 2.17 | All working times of Bidders personnel shall be included in the Bidders annual remuneration. | 1 |  |  | 1 |  | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing
Zte | JUE | Approval | O&M | Specific Requirements | 2.18 | Extensive repairs have to be approved by the Employer. | 2 |  |  | 1 |  | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing
Zte | JUE | Documentation | O&M | Specific Requirements | 2.19 | All repair works and compensations shall have to be documented and to be submitted to the Employer within two weeks. | 2 |  |  | 1 |  | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing
Zte | JUE | Inspection of Repair Works | O&M | Specific Requirements | 2.20 | The Employer can inspect the repair works within one month (30 days) after receiving the documentation | 2 |  |  | 1 |  | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing
Zte | JUE | Ground Maintenance | O&M | Specific Requirements | 2.21 | Ground maintenance shall include all procedures that are necessary to avoid module shading and an incorrect operation of the trackers. This shall include the levelling of sand drifts. Necessary switching operations shall be coordinated by the Bidder with responsible authorities | 2 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing
Zte | JUE | Person in Control of PV plant | O&M | Specific Requirements | 2.22 | The Bidder shall propose an organigram for the O& M personnel with one main responsible | 2 |  |  | 1 |  | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing
Zte | JUE | Reporting | O&M | Specific Requirements | 2.23 | The Bidder shall deliver to the Employer regular reports on monthly, quarterly and annual basis. | 1 |  |  | 1 |  | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing
Tbea | JUE | Scope of the Bid | O&M | General Requirements | 2.1.2 | Responsibility to keep Performance Ratio and Availability at highest levels | 1 |  | 1
Tbea | JUE | Scope of the Bid | O&M | General Requirements | 2.1.2 | Preventive maintenance | 2 |  | 1
Tbea | JUE | Scope of the Bid | O&M | General Requirements | 2.1.2 | Provision and Installation of spare parts, keeping of spare parts stock (refill of used spares). Reporting of status and consumption to be continuously updated | 2 |  | 1
Tbea | JUE | Scope of the Bid | O&M | General Requirements | 2.1.2 | Corrective maintenance with guaranteed response times | 1 |  | 1
Tbea | JUE | Scope of the Bid | O&M | General Requirements | 2.1.2 | Daily, monthly and yearly performance and production reporting | 1 |  | 1
Tbea | JUE | Scope of the Bid | O&M | General Requirements | 2.1.2 | Operation of the Plant (including 24/7 presence of O&M and security staff on the project site). | 1 |  | 1
Tbea | JUE | Scope of the Bid | O&M | General Requirements | 2.1.2 | Cleaning of the Plant, preventive and corrective maintenance of the civil works and the fences. | 1 |  | 1
Tbea | JUE | Scope of the Bid | O&M | General Requirements | 2.1.2 | Cleaning of Modules and irradiation sensors to prevent dust accumulation to undesirable level. | 1 |  | 1
Tbea | JUE | Scope of the Bid | O&M | General Requirements | 2.1.2 | Ordinary road and land maintenance to the extent required for proper maintenance of the Plant. | 3 |  | 1
Tbea | JUE | Scope of the Bid | O&M | General Requirements | 2.1.2 | Smooth functioning of all interconnections and data communications of the system performance | 2 |  | 1
Tbea | JUE | Scope of the Bid | O&M | General Requirements | 2.1.2 | Optimal level of SCADA monitoring | 1 |  | 1
Tbea | JUE | Scope of the Bid | O&M | General Requirements | 2.1.2 | Coordination and compliance with NTDC requirements | 1 |  | 1
Tbea | JUE | Scope of the Bid | O&M | General Requirements | 2.1.2 | Maintaining a customer support hotline for the Employer/NTDC | 3 |  | 1
Tbea | JUE | Scope of the Bid | O&M | General Requirements | 2.1.2 | Providing regular reports of repairs, maintenance, and tests | 3 |  | 1
Tbea | JUE | Scope of the Bid | O&M | General Requirements | 2.1.2 | Performance variance analysis of the module strings and inverters | 1 |  | 1
Tbea | JUE | Scope of the Bid | O&M | General Requirements | 2.1.2 | Periodic maintenance of inverter, transformer, combiner boxes etc., according manufacturer's requirements | 1 |  | 1
Tbea | JUE | Scope of the Bid | O&M | General Requirements | 2.1.2 | Scheduled maintenance routines: e.g., inspections of modules with polarized sunglasses to check for discolouration, the first signs of de-lamination, loose wires in the electronics, corrosion of mounting structures, erosion | 1 |  | 1
Tbea | JUE | Scope of the Bid | O&M | General Requirements | 2.1.2 | Track chronic negative deviations in the module string output, i.e., power tolerances consistently in the negative | 3 |  | 1
Tbea | JUE | Scope of the Bid | O&M | General Requirements | 2.1.2 | Negotiating a warranty reserve for replacements with the suppliers | 3 |  | 1
Tbea | JUE | Scope of the Bid | O&M | General Requirements | 2.1.2 | Maintaining adequate reserves for timely replacement | 2 |  | 1
Tbea | JUE | Scope of the Bid | O&M | General Requirements | 2.1.2 | Insuring products at different levels but for sensible costs; the insurance policy shall not become expensive compared to the replacement cost of the item | 3 |  | 1
Tbea | JUE | Scope of the Bid | O&M | General Requirements | 2.1.2 | Warranties and insurance policies should be assignable/transferrable to the Employer in case it decides to take over the O&M | 1 |  | 1
Tbea | JUE | Scope of the Bid | O&M | General Requirements | 2.1.2 | Reporting the monitoring and surveillance system. | 3 |  | 1
Tbea | JUE | Scope of the Bid | O&M | General Requirements | 2.1.2 | Technical report elaboration. | 3 |  | 1
Tbea | JUE | Scope of the Bid | O&M | General Requirements | 2.1.2 | On site Security services. | 3 |  | 1
Tbea | JUE | Scope of the Bid | O&M | General Requirements | 2.1.2 | Provide all O&M Staff, trained and certified as far as applicable. For security reasons, a 24 h/ 7 days a week staffing of security and maintenance shall be provided. The staffing concept and selected key employees shall be presented to the Employer for approval. | 1 |  |  |  | 1 | Second criteria / sentence is missing.
Tbea | JUE | Initial Inspection | O&M | General Requirements | 2.2.1 | familiarize himself with the specific plant equipment and specific maintenance requirements / training of staff | 1 |  |  |  | 1 | first criteria / sentence is missing.
Tbea | JUE | Initial Inspection | O&M | General Requirements | 2.2.2 | Maintenance routines, inspection check-lists, working files, | 1 |  | 1
Tbea | JUE | Initial Inspection | O&M | General Requirements | 2.2.3 | coordinate with the Employer and keep him updated regarding his progress of preparation, status of construction, pending issues of Construction, Commissioning and testing. | 2 |  | 1 |  |  |  | Cannot be evaluated at this stage
Tbea | JUE | Bi-annual inspection | O&M | PV Generator | 2.3.1 | 100% visual inspection of modules regarding damage in spring | 1 |  | 1
Tbea | JUE | Bi-annual inspection | O&M | PV Generator | 2.3.1 | Random visual inspection of modules regarding damage in autumn | 2 |  | 1 |  |  |  | Cannot be evaluated at this stage
Tbea | JUE | Bi-annual inspection | O&M | PV Generator | 2.3.1 | Random check of module clip with respect to loosening; if necessary replacement of clips (min. 10%, documentation of location, during 5 years inspection of whole PV plant) | 2 |  | 1 |  |  |  | Cannot be evaluated at this stage
Tbea | JUE | Bi-annual inspection | O&M | PV Generator | 2.3.1 | Random testing of the steadiness of the mounting foundation/system and random inspection regarding corrosion at substructure (min. 10%, documentation of location, during 10 years inspection of whole PV plant) | 1 |  | 1
Tbea | JUE | Bi-annual inspection | O&M | PV Generator | 2.3.1 | Documentation of wear and tear of moving components, monitoring of dust intrusion and corrosion. | 2 |  | 1
Tbea | JUE | Bi-annual inspection | O&M | PV Generator | 2.3.1 | Cleaning of sensors and switches | 1 |  | 1 |  |  |  | sensors shall be done by independent Meteo Station Operator
Tbea | JUE | Bi-annual inspection | O&M | PV Generator | 2.3.1 | Cleaning of all modules | 1 |  | 1
Tbea | JUE | Bi-annual inspection | O&M | Inverter (100%) | 2.3.2 | Functional check of ventilator system of inverter station | 1 |  | 1
Tbea | JUE | Bi-annual inspection | O&M | Inverter (100%) | 2.3.2 | Cleaning of the filter mats in the air leaks | 2 |  | 1
Tbea | JUE | Bi-annual inspection | O&M | Inverter (100%) | 2.3.2 | Replacement of dirty filter mats | 2 |  | 1
Tbea | JUE | Bi-annual inspection | O&M | Inverter (100%) | 2.3.2 | Inspection of the interior of the electrical cabinet regarding dust deposit, dirtiness, humidity, water penetration from outside. If necessary the cabinet has to be cleaned. | 1 |  | 1
Tbea | JUE | Bi-annual inspection | O&M | Inverter (100%) | 2.3.2 | Testing of inverter features according to maintenance schedule of manufacturer. | 1 |  | 1
Tbea | JUE | Bi-annual inspection | O&M | Inverter (100%) | 2.3.2 | Maintenance of inverters according to manufacturer's instruction. | 1 |  | 1
Tbea | JUE | Bi-annual inspection | O&M | Monitoring | 2.3.3 | Functionality testing of the monitoring system | 3 |  | 1
Tbea | JUE | Bi-annual inspection | O&M | Maintenance | 2.3.3 | Maintenance of all Power plant components according to manufacturer's instructions | 1 |  | 1
Tbea | JUE | Main Annual Inspection | O&M | PV Generator | 2.4.1 | Visual inspection of all accessible cable trenches and cable trays regarding damage | 1 |  | 1
Tbea | JUE | Main Annual Inspection | O&M | PV Generator | 2.4.1 | Visual inspection and random testing of string connector (min. 10% with Documentation of location , during 10 years testing of whole PV plant) | 1 |  | 1
Tbea | JUE | Main Annual Inspection | O&M | PV Generator | 2.4.1 | Inspection of DC distribution box: Visual inspection of all clamps and degree of pollution. Testing of over-voltage protection | 1 |  | 1
Tbea | JUE | Main Annual Inspection | O&M | PV Generator | 2.4.1 | Maintenance of sensors based on manufacturer’s instructions | 1 |  | 1
Tbea | JUE | Main Annual Inspection | O&M | Inverter (100%) | 2.4.2 | Test of the internal miniature circuit breakers and power switch, test of emergency shut-off | 1 |  | 1
Tbea | JUE | Main Annual Inspection | O&M | Inverter (100%) | 2.4.2 | Visual inspection of all fuses | 1 |  | 1
Tbea | JUE | Main Annual Inspection | O&M | Inverter (100%) | 2.4.2 | Inspection of over-voltage protection and upstream fuses regarding external damage | 1 |  | 1
Tbea | JUE | Main Annual Inspection | O&M | Inverter (100%) | 2.4.2 | Functional check of internal and external over- and under-voltage monitoring through operation of test terminal | 1 |  | 1
Tbea | JUE | Main Annual Inspection | O&M | Inverter (100%) | 2.4.2 | Functional check of insulation monitoring | 1 |  | 1
Tbea | JUE | Main Annual Inspection | O&M | Inverter (100%) | 2.4.2 | Check of control and auxiliary voltages | 2 |  | 1
Tbea | JUE | Main Annual Inspection | O&M | Inverter (100%) | 2.4.2 | Check of the safety circuit for the interruption of the AC-grid protection in the case of failure (emergency shut-off, over-/ under-voltage, over temperature, etc.) based on the local conditions | 1 |  | 1
Tbea | JUE | Main Annual Inspection | O&M | Inverter (100%) | 2.4.2 | Visual inspection of AC and DC clamps regarding tightness and colouring, tightening of clamps | 1 |  | 1
Tbea | JUE | Main Annual Inspection | O&M | Inverter (100%) | 2.4.2 | Maintenance of inverters according to manufacturer instruction | 1 |  | 1
Tbea | JUE | Main Annual Inspection | O&M | Roads | 2.4.3 | Visual inspection of roads within the PV plant shall be carried out to ascertain that these are maintained in good condition for the intended purpose. | 2 |  | 1
Tbea | JUE | Main Annual Inspection | O&M | Substation and Transmission Line | 2.4.4 | Visual inspection of transformer and switchboard rooms and cleaning if necessary | 1 |  | 1
Tbea | JUE | Main Annual Inspection | O&M | Substation and Transmission Line | 2.4.4 | Visual inspection of Transmission Line and report of damage to the grid operator | 2 |  | 1
Tbea | JUE | Main Annual Inspection | O&M | Substation and Transmission Line | 2.4.4 | Maintenance of substation and transmission line according to manufacturer instruction | 1 |  | 1
Tbea | JUE | Main Annual Inspection | O&M | Auxiliary system | 2.4.5 | Inspection of security system inclusive fence, all gates, all cameras etc. Random test of the fence fastening, if necessary retightening of the screws | 2 |  | 1
Tbea | JUE | Main Annual Inspection | O&M | Auxiliary system | 2.4.5 | If existing: inspection of requirements out of the building permit | 2 |  | 1
Tbea | JUE | Main Annual Inspection | O&M | Auxiliary system | 2.4.5 | Maintenance of all components according to manufacturer instruction | 1 |  | 1
Tbea | JUE | Special inspection (every 4 years) | O&M | Specific Requirements | 2.5.1 | Measurement of inverters and generators according to recognized international standards and according to results from commissioning certificates (insulation, loop resistance, earthing, DC-open circuit voltage) | 2 |  | 1
Tbea | JUE | Special inspection (every 4 years) | O&M | Specific Requirements | 2.5.1 | Protection systems of medium voltage switching panels of the stations | 1 |  | 1
Tbea | JUE | Special inspection (every 4 years) | O&M | Specific Requirements | 2.5.1 | Oil check of transformers | 1 |  | 1
Tbea | JUE | Special inspection (every 4 years) | O&M | Specific Requirements | 2.5.1 | Control of station equipment | 2 |  | 1
Tbea | JUE | Deactivation | O&M | Allowed deactivation periods | 2.6.1 | Times with irradiation level < 300 W/m² | 2 |  | 1
Tbea | JUE | Deactivation | O&M | Allowed deactivation periods | 2.6.1 | Approved by The Employer to ensure consideration of Employer's obligations | 2 |  | 1
Tbea | JUE | Deactivation | O&M | Allowed deactivation periods | 2.6.1 | Approved from grid operator | 2 |  | 1
Tbea | JUE | Deactivation | O&M | Specific Requirements | 2.6.2 | All deactivations during maintenance works shall be completely documented. | 2 |  | 1
Tbea | JUE | Deactivation | O&M | Specific Requirements | 2.6.3 | Deactivation shall not be considered as permitted downtime. | 2 |  | 1
Tbea | JUE | Change of Inspection and Maintenance Work procedures | O&M | Specific Requirements | 2.7 | work in accordance with all applicable laws | 2 |  | 1
Tbea | JUE | Performance of maintenance and repair works | O&M | Specific Requirements | 2.8.1 | Corresponding regulations of the respective component manufacturer shall have to be followed during maintenance works | 1 |  | 1
Tbea | JUE | Performance of maintenance and repair works | O&M | Specific Requirements | 2.8.2 | Report document for maintenance works (blanc sample requiered for bid) | 1 |  |  |  | 1 | blanc sample is missing
Tbea | JUE | Performance of maintenance and repair works | O&M | Specific Requirements | 2.8.3 | Observe and respect the maintenance and operation specifications of the manufacturer of the components | 3 |  | 1
Tbea | JUE | Performance of maintenance and repair works | O&M | Specific Requirements | 2.8.4 | Observe and respect the local law, regulations and international PV standards. | 3 |  | 1
Tbea | JUE | Performance of maintenance and repair works | O&M | Specific Requirements | 2.8.5 | During his work the Bidder shall be held responsible for the public safety of the PV plant | 2 |  | 1
Tbea | JUE | On-site monitoring | O&M | Specific Requirements | 2.9.1 | Permanent (24/7) staffing of the Power Plant, consisting of security and O&M personnel. | 1 |  | 1
Tbea | JUE | On-site monitoring | O&M | Specific Requirements | 2.9.2 | Bidder shall arrange service contracts with specialized sub-contractors | 2 |  | 1
Tbea | JUE | On-site monitoring | O&M | Specific Requirements | 2.9.3 | All operational data shall be logged on-site in parallel to the remote data storage | 2 |  | 1
Tbea | JUE | On-site monitoring | O&M | Specific Requirements | 2.9.4 | The data of irradiation sensors shall be monitored by an independent expert on a continuous basis | 2 |  | 1
Tbea | JUE | Remote Supervision | O&M | Specific Requirements | 2.10.1 | On-call service provided for the Employer for availability outside business hours and during weekends (24/7). | 1 |  | 1
Tbea | JUE | Remote Supervision | O&M | Specific Requirements | 2.10.2 | Any reductions in performance shall have to be logged. | 1 |  | 1
Tbea | JUE | Remote Supervision | O&M | Specific Requirements | 2.10.3 | The data will comprise, apart from electrical parameters of the PV plant: currents, voltages, irradiation values, kind and period of reductions in performance such as curtailment by the grid operator | 2 |  | 1
Tbea | JUE | Remote Supervision | O&M | Specific Requirements | 2.10.4 | The data shall present the status of the plant such as the performance ratio annual overview and the current feed-in power | 2 |  | 1
Tbea | JUE | Remote Supervision | O&M | Specific Requirements | 2.10.5 | The remote supervision shall also control the operation of the PV plant. | 2 |  | 1
Tbea | JUE | Remote Supervision | O&M | Specific Requirements | 2.10.6 | The remote supervision shall also include the taking of measures for removal of faults. | 2 |  | 1
Tbea | JUE | Remote Supervision | O&M | Specific Requirements | 2.10.7 | The Bidder shall provide to the Employer permanent online access to the power plant control system for parallel monitoring | 1 |  | 1
Tbea | JUE | Remote Supervision | O&M | Specific Requirements | 2.10.8 | Monthly / quarterly and annual reports based on the data of the remote supervision provided to the Employer 4 weeks after the last period of reporting at the latest. | 1 |  | 1
Tbea | JUE | Remote Supervision | O&M | Specific Requirements | 2.10.9 | The fees for telephone connection and/or data transfer services are included in the annual remuneration. | 2 |  | 1
Tbea | JUE | Reaction to Fault Messages / Response Times | O&M | Specific Requirements | 2.11.1 | Every fault message has to be registered in the monitoring software. According to the fault message, the Bidder shall issue a fault diagnosis within a response time of 2 hours (24/7) | 1 |  | 1
Tbea | JUE | Reaction to Fault Messages / Response Times | O&M | Specific Requirements | 2.11.2 | profit relevant Fault Events: Downtime registration/ reasons/ repair/ in monthly report (blanc of monthly report?) | 1 |  | 1
Tbea | JUE | Fault Management / Warranty defects | O&M | Specific Requirements | 2.12.1 | Fault Management: all handling and communication | 2 |  | 1
Tbea | JUE | Fault Management / Warranty defects | O&M | Specific Requirements | 2.12.2 | Fault Management: Handling / correspondence with third parties | 2 |  | 1
Tbea | JUE | Fault Management / Warranty defects | O&M | Specific Requirements | 2.12.3 | Fault Management = without repair works | 3 |  | 1
Tbea | JUE | Fault Management / Warranty defects | O&M | Specific Requirements | 2.12.4 | Product warranties in favour of contractor / Bidder (responsible) to claim all warranties for at least 5 years | 1 |  |  |  | 1 | we cant find the first criteria. please explaine. | the first criteria is missing, please explaine.
Tbea | JUE | Fault Management / Warranty defects | O&M | Specific Requirements | 2.12.5 | Operational defects, which are not considered as warranty defects - see repair works section below | 1 |  |  | 1 | 1 | rectified at the soonest occasion by TBEA? | Failure Response Time Model not not accepted
Tbea | JUE | Fault Management / Warranty defects | O&M | Specific Requirements | 2.12.6 | All defects shall be documented within the same day of detection, | 2 |  | 1
Tbea | JUE | Fault Calls | O&M | Specific Requirements | 2.13.1 | The scope of service shall include any working times for all fault calls including travelling times and costs. | 1 |  | 1
Tbea | JUE | Fault Calls | O&M | Specific Requirements | 2.13.2 | The minimum response time in case of failure must meet the EPA requirements | 1 |  | 1 |  | 1 |  | EPA has to accept
Tbea | JUE | Fault Calls | O&M | Specific Requirements | 2.13.2 | --> Time Model: Response Times for Priorities 1-3 (12h / 24h / 1 week) | 1 |  |  | 1 | 1 | rectified at the soonest occasion by TBEA? look at 2.12.5 | look at 2.12.5
Tbea | JUE | Fault Calls | O&M | Specific Requirements | 2.13.3 | failure time response does not match the response time of EPA >> failure time response does not match the response time of EPA | 3 |  | 1 |  | 1 |  | EPA has to accept
Tbea | JUE | Fault Calls | O&M | Specific Requirements | 2.13.4 | The fault call shall include the fault diagnosis on site as well as an immediate error correction if possible. The fault shall have to be corrected within the response time and, failing this, a diagnosis of the fault has to be effect indicating further measures. | 2 |  | 1 |  | 1 | General understanding: expressions like "shall", "shall be supplied with", "has to be", "must be" have the meaning of "will be delivered"? Please confirm. | (shall) have to --> or --> will be corrected?
Tbea | JUE | Fault Calls | O&M | Specific Requirements | 2.13.5 | Fault calls can be performed without prior consent of the Employer. | 3 |  | 1
Tbea | JUE | Fault Calls | O&M | Specific Requirements | 2.13.6 | If the elimination of faults is not possible within the response time / and additional travelling, this is Repair Work | 3 |  | 1
Tbea | JUE | Spare Parts and Tools | O&M | Specific Requirements | 2.14 | provide the necessary set of spare parts and maintenance tools as required to perform the services | 1 |  | 1
Tbea | JUE | Spare Parts and Tools | O&M | Specific Requirements | 2.14.1 | cover all cost for supply and re-stocking of spare parts from his annual remuneration. | 1 |  | 1
Tbea | JUE | Spare Parts and Tools | O&M | Specific Requirements | 2.14.2 | refill spare parts immediately after consumption | 2 |  | 1
Tbea | JUE | Reduced Output of the Plant | O&M | Specific Requirements | 2.15 | Monthly comparison of the specific performance of all measuring channels among each other. 5% reduced output results in general check of all the channels and shall be documented. | 1 |  | 1
Tbea | JUE | Reduced Output of the Plant | O&M | Specific Requirements | 2.15.1 | Identified reduced output shall be justified. Reduced output shall be recovered and liquidated damages determined. | 1 |  | 1 |  |  |  | liquidated --> means --> performance
Tbea | JUE | Repair time and cost | O&M | Specific Requirements | 2.16 | Repair times are considered as part of the availability guaranty of the Bidder. All cost of repair shall be part of the Bidders annual remuneration. For the avoidance of doubt that includes any repairs due to lightening, theft and vandalism. | 1 |  | 1
Tbea | JUE | Working Time | O&M | Specific Requirements | 2.17 | All working times of Bidders personnel shall be included in the Bidders annual remuneration. | 1 |  | 1
Tbea | JUE | Approval | O&M | Specific Requirements | 2.18 | Extensive repairs have to be approved by the Employer. | 2 |  |  | 1 | 1 | please confirm: No exemptions are allowed
Tbea | JUE | Documentation | O&M | Specific Requirements | 2.19 | All repair works and compensations shall have to be documented and to be submitted to the Employer within two weeks. | 2 |  | 1
Tbea | JUE | Inspection of Repair Works | O&M | Specific Requirements | 2.20 | The Employer can inspect the repair works within one month (30 days) after receiving the documentation | 2 |  | 1
Tbea | JUE | Ground Maintenance | O&M | Specific Requirements | 2.21 | Ground maintenance shall include all procedures that are necessary to avoid module shading and an incorrect operation of the trackers. This shall include the levelling of sand drifts. Necessary switching operations shall be coordinated by the Bidder with responsible authorities | 2 |  | 1
Tbea | JUE | Person in Control of PV plant | O&M | Specific Requirements | 2.22 | The Bidder shall propose an organigram for the O& M personnel with one main responsible | 2 |  |  |  | 1 | "and shall be approved by the Employer. Any replacement or substitute of this person shall be subject to approval by the Employer." we can not find. Please confirm.
Tbea | JUE | Reporting | O&M | Specific Requirements | 2.23 | The Bidder shall deliver to the Employer regular reports on monthly, quarterly and annual basis. | 1 |  | 1
Juwi | JUE | Scope of the Bid | O&M | General Requirements | 2.1.2 | Responsibility to keep Performance Ratio and Availability at highest levels | 1 |  |  |  | 1 | L | missing
Juwi | JUE | Scope of the Bid | O&M | General Requirements | 2.1.2 | Corrective maintenance with guaranteed response times | 1 |  | 1
Juwi | JUE | Scope of the Bid | O&M | General Requirements | 2.1.2 | Daily, monthly and yearly performance and production reporting | 1 |  |  |  | 1 | L | not completely described
Juwi | JUE | Scope of the Bid | O&M | General Requirements | 2.1.2 | Operation of the Plant (including 24/7 presence of O&M and security staff on the project site). | 1 |  |  |  | 1 |  | only day time
Juwi | JUE | Scope of the Bid | O&M | General Requirements | 2.1.2 | Cleaning of the Plant, preventive and corrective maintenance of the civil works and the fences. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing
Juwi | JUE | Scope of the Bid | O&M | General Requirements | 2.1.2 | Cleaning of Modules and irradiation sensors to prevent dust accumulation to undesirable level. | 1 |  |  |  | 1 | additional bid for cleaning can be issued is required!! | additional bid for cleaning can be issued
Juwi | JUE | Scope of the Bid | O&M | General Requirements | 2.1.2 | Optimal level of SCADA monitoring | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing
Juwi | JUE | Scope of the Bid | O&M | General Requirements | 2.1.2 | Coordination and compliance with NTDC requirements | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing
Juwi | JUE | Scope of the Bid | O&M | General Requirements | 2.1.2 | Performance variance analysis of the module strings and inverters | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing
Juwi | JUE | Scope of the Bid | O&M | General Requirements | 2.1.2 | Periodic maintenance of inverter, transformer, combiner boxes etc., according manufacturer's requirements | 1 |  |  |  | 1 | according manufacturer's requirements is confirmable | missing
Juwi | JUE | Scope of the Bid | O&M | General Requirements | 2.1.2 | Scheduled maintenance routines: e.g., inspections of modules with polarized sunglasses to check for discolouration, the first signs of de-lamination, loose wires in the electronics, corrosion of mounting structures, erosion | 1 |  | 1
Juwi | JUE | Scope of the Bid | O&M | General Requirements | 2.1.2 | Warranties and insurance policies should be assignable/transferrable to the Employer in case it decides to take over the O&M | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing
Juwi | JUE | Scope of the Bid | O&M | General Requirements | 2.1.2 | Provide all O&M Staff, trained and certified as far as applicable. For security reasons, a 24 h/ 7 days a week staffing of security and maintenance shall be provided. The staffing concept and selected key employees shall be presented to the Employer for approval. | 1 | Schedule F 1.1 |  |  | 1 | 5 days or 24/7 ? | additional
Juwi | JUE | Initial Inspection | O&M | General Requirements | 2.2.1 | familiarize himself with the specific plant equipment and specific maintenance requirements / training of staff | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing
Juwi | JUE | Initial Inspection | O&M | General Requirements | 2.2.2 | Maintenance routines, inspection check-lists, working files, | 1 |  | 1
Juwi | JUE | Bi-annual inspection | O&M | PV Generator | 2.3.1 | 100% visual inspection of modules regarding damage in spring | 1 |  |  |  | 1 | 100% visual inspection of modules regarding damage in spring is confirmable
Juwi | JUE | Bi-annual inspection | O&M | PV Generator | 2.3.1 | Random testing of the steadiness of the mounting foundation/system and random inspection regarding corrosion at substructure (min. 10%, documentation of location, during 10 years inspection of whole PV plant) | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing
Juwi | JUE | Bi-annual inspection | O&M | PV Generator | 2.3.1 | Cleaning of sensors and switches | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | sensors shall be done by independent Meteo Station Operator
Juwi | JUE | Bi-annual inspection | O&M | PV Generator | 2.3.1 | Cleaning of all modules | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | additional bid for cleaning can be issued is required!!
Juwi | JUE | Bi-annual inspection | O&M | Inverter (100%) | 2.3.2 | Functional check of ventilator system of inverter station | 1 |  | 1
Juwi | JUE | Bi-annual inspection | O&M | Inverter (100%) | 2.3.2 | Inspection of the interior of the electrical cabinet regarding dust deposit, dirtiness, humidity, water penetration from outside. If necessary the cabinet has to be cleaned. | 1 |  | 1
Juwi | JUE | Bi-annual inspection | O&M | Inverter (100%) | 2.3.2 | Testing of inverter features according to maintenance schedule of manufacturer. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | L according manufacturer's instruction is confirmable
Juwi | JUE | Bi-annual inspection | O&M | Inverter (100%) | 2.3.2 | Maintenance of inverters according to manufacturer's instruction. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | L according manufacturer's instruction is confirmable
Juwi | JUE | Bi-annual inspection | O&M | Maintenance | 2.3.3 | Maintenance of all Power plant components according to manufacturer's instructions | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | L according manufacturer's instruction is confirmable
Juwi | JUE | Main Annual Inspection | O&M | PV Generator | 2.4.1 | Visual inspection of all accessible cable trenches and cable trays regarding damage | 1 |  | 1
Juwi | JUE | Main Annual Inspection | O&M | PV Generator | 2.4.1 | Visual inspection and random testing of string connector (min. 10% with Documentation of location , during 10 years testing of whole PV plant) | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | not completely described
Juwi | JUE | Main Annual Inspection | O&M | PV Generator | 2.4.1 | Inspection of DC distribution box: Visual inspection of all clamps and degree of pollution. Testing of over-voltage protection | 1 |  | 1
Juwi | JUE | Main Annual Inspection | O&M | PV Generator | 2.4.1 | Maintenance of sensors based on manufacturer’s instructions | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | L according manufacturer's instruction is confirmable
Juwi | JUE | Main Annual Inspection | O&M | Inverter (100%) | 2.4.2 | Test of the internal miniature circuit breakers and power switch, test of emergency shut-off | 1 |  | 1
Juwi | JUE | Main Annual Inspection | O&M | Inverter (100%) | 2.4.2 | Visual inspection of all fuses | 1 |  |  |  | 1 |  | missing
Juwi | JUE | Main Annual Inspection | O&M | Inverter (100%) | 2.4.2 | Inspection of over-voltage protection and upstream fuses regarding external damage | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | not completely described
Juwi | JUE | Main Annual Inspection | O&M | Inverter (100%) | 2.4.2 | Functional check of internal and external over- and under-voltage monitoring through operation of test terminal | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | not completely described
Juwi | JUE | Main Annual Inspection | O&M | Inverter (100%) | 2.4.2 | Functional check of insulation monitoring | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | not completely described
Juwi | JUE | Main Annual Inspection | O&M | Inverter (100%) | 2.4.2 | Check of the safety circuit for the interruption of the AC-grid protection in the case of failure (emergency shut-off, over-/ under-voltage, over temperature, etc.) based on the local conditions | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | not completely described
Juwi | JUE | Main Annual Inspection | O&M | Inverter (100%) | 2.4.2 | Visual inspection of AC and DC clamps regarding tightness and colouring, tightening of clamps | 1 |  | 1 |  |  | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Juwi | JUE | Main Annual Inspection | O&M | Inverter (100%) | 2.4.2 | Maintenance of inverters according to manufacturer instruction | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing
Juwi | JUE | Main Annual Inspection | O&M | Substation and Transmission Line | 2.4.4 | Visual inspection of transformer and switchboard rooms and cleaning if necessary | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing
Juwi | JUE | Main Annual Inspection | O&M | Substation and Transmission Line | 2.4.4 | Maintenance of substation and transmission line according to manufacturer instruction | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing
Juwi | JUE | Main Annual Inspection | O&M | Auxiliary system | 2.4.5 | Maintenance of all components according to manufacturer instruction | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing
Juwi | JUE | Special inspection (every 4 years) | O&M | Specific Requirements | 2.5.1 | Protection systems of medium voltage switching panels of the stations | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing
Juwi | JUE | Special inspection (every 4 years) | O&M | Specific Requirements | 2.5.1 | Oil check of transformers | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing
Juwi | JUE | Performance of maintenance and repair works | O&M | Specific Requirements | 2.8.1 | Corresponding regulations of the respective component manufacturer shall have to be followed during maintenance works | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing
Juwi | JUE | Performance of maintenance and repair works | O&M | Specific Requirements | 2.8.2 | Report document for maintenance works (blanc sample requiered for bid) | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | Report document for maintenance works is missing
Juwi | JUE | On-site monitoring | O&M | Specific Requirements | 2.9.1 | Permanent (24/7) staffing of the Power Plant, consisting of security and O&M personnel. | 1 |  |  |  | 1 | Unclear: We do not understand your proposal, please detail your proposal. Especially confirm that you are compliant with our requested criteria.
Juwi | JUE | Remote Supervision | O&M | Specific Requirements | 2.10.1 | On-call service provided for the Employer for availability outside business hours and during weekends (24/7). | 1 |  |  |  | 1 | Unclear: We do not understand your proposal, please detail your proposal. Especially confirm that you are compliant with our requested criteria.
Juwi | JUE | Remote Supervision | O&M | Specific Requirements | 2.10.2 | Any reductions in performance shall have to be logged. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing
Juwi | JUE | Remote Supervision | O&M | Specific Requirements | 2.10.7 | The Bidder shall provide to the Employer permanent online access to the power plant control system for parallel monitoring | 1 |  | 1
Juwi | JUE | Remote Supervision | O&M | Specific Requirements | 2.10.8 | Monthly / quarterly and annual reports based on the data of the remote supervision provided to the Employer 4 weeks after the last period of reporting at the latest. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing
Juwi | JUE | Reaction to Fault Messages / Response Times | O&M | Specific Requirements | 2.11.1 | Every fault message has to be registered in the monitoring software. According to the fault message, the Bidder shall issue a fault diagnosis within a response time of 2 hours (24/7) | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing
Juwi | JUE | Reaction to Fault Messages / Response Times | O&M | Specific Requirements | 2.11.2 | profit relevant Fault Events: Downtime registration/ reasons/ repair/ in monthly report (blanc of monthly report?) | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing
Juwi | JUE | Fault Management / Warranty defects | O&M | Specific Requirements | 2.12.4 | Product warranties in favour of contractor / Bidder (responsible) to claim all warranties for at least 5 years | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing
Juwi | JUE | Fault Management / Warranty defects | O&M | Specific Requirements | 2.12.5 | Operational defects, which are not considered as warranty defects - see repair works section below | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | Failure Response Time Model not not accepted
Juwi | JUE | Fault Calls | O&M | Specific Requirements | 2.13.1 | The scope of service shall include any working times for all fault calls including travelling times and costs. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing
Juwi | JUE | Fault Calls | O&M | Specific Requirements | 2.13.2 | The minimum response time in case of failure must meet the EPA requirements | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing
Juwi | JUE | Fault Calls | O&M | Specific Requirements | 2.13.2 | --> Time Model: Response Times for Priorities 1-3 (12h / 24h / 1 week) | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | look at 2.12.5
Juwi | JUE | Spare Parts and Tools | O&M | Specific Requirements | 2.14 | provide the necessary set of spare parts and maintenance tools as required to perform the services | 1 |  | 1
Juwi | JUE | Spare Parts and Tools | O&M | Specific Requirements | 2.14.1 | cover all cost for supply and re-stocking of spare parts from his annual remuneration. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing
Juwi | JUE | Reduced Output of the Plant | O&M | Specific Requirements | 2.15 | Monthly comparison of the specific performance of all measuring channels among each other. 5% reduced output results in general check of all the channels and shall be documented. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing
Juwi | JUE | Reduced Output of the Plant | O&M | Specific Requirements | 2.15.1 | Identified reduced output shall be justified. Reduced output shall be recovered and liquidated damages determined. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing liquidated --> means --> performance
Juwi | JUE | Repair time and cost | O&M | Specific Requirements | 2.16 | Repair times are considered as part of the availability guaranty of the Bidder. All cost of repair shall be part of the Bidders annual remuneration. For the avoidance of doubt that includes any repairs due to lightening, theft and vandalism. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing
Juwi | JUE | Working Time | O&M | Specific Requirements | 2.17 | All working times of Bidders personnel shall be included in the Bidders annual remuneration. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing
Juwi | JUE | Reporting | O&M | Specific Requirements | 2.23 | The Bidder shall deliver to the Employer regular reports on monthly, quarterly and annual basis. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | missing
Juwi | GD | Scope of the Bid | General items | Specific Requirements | 1.1.2 | The Offer shall include a list of all vendors and/or sub-contractors for major equipment. | 1 |  |  |  | 1 |  |  |  |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | 1 |  | Open
Juwi | GD | Scope of the Bid | General items | Quality Assurance | 1.1.3 | Defect components consequences: If one tested sample fails in one criterion, all items of the same category will be regarded as failed and rejected. | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  | Only to be checked in list of deviations. | yes, we need to be sure that they comply as for most of the critera | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 1 | 1 | Open
Juwi | GD | Scope of the Bid | General items | Guarantees | 1.1.5 | Energy Purchase Agreement (EPA) practices are followed | 1 |  |  |  | 1 | Important reasons: due to current uncertainty of the criteria we accept an open status. Please clarify that yo acknowledge the criteria and comply unless a reason of high importance will not allow you you to comply. In such a situation the parties will seek to agree a compromise. |  | This cannot be evaluated at this stage. | we need a sentence that it should and can only be disregarded for important reasons | Unclear: We do not understand your proposal, please detail your proposal. Especially confirm that you are compliant with our requested criteria. | 1 |  | Open
Juwi | GD | Scope of the Bid | Layout | Guarantees | 1.1.6 | The bidder confirms that the system complies with all applicable requirements of the NEPRA Grid Code of Pakistan and its Draft Amendment no. 2 for Solar Power Projects. | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  | Only to be checked in list of deviations. |  | Important reasons: due to current uncertainty of the criteria we accept an open status. Please clarify that yo acknowledge the criteria and comply unless a reason of high importance will not allow you you to comply. In such a situation the parties will seek to agree a compromise. | 1 |  | Open
Juwi | GD | Scope of the Bid | Credentials | EPC | 1.1.9 | The bid includes professional experience of the Bidders in ground mounted utility-scale PV and financial information about their long-term stability | 3 |  | 1 | [7 empty] | 1 |  | Pass
Juwi | GD | Scope of the Bid | General items | Specific Requirements | 1.1.9 | The bid covers the planning of the System design, the required functionality of the System in terms of its sub-systems and components, detailed feature-wise descriptions of the components to be used in the System, the planning of the System installation, its integration, testing, monitoring, commissioning and O&M of the System | 1 |  |  | 1 |  | We can not find all of the requested criteria in your documents. Please confirm that your bid is compliant with all expectations and requirements of Section 6 of the RFP and provide a list with ALL exeptions or alterations. This applies to both, the EOPC And the O&M part. |  | This question should be removed as detailed design of every component/sub-system will be checked and evaluated thoroughly in technical evaluation | no, its an overall critera an need to be met |  | 1 | 1 | Fail
Juwi | GD | Scope of the Bid | Credentials | EPC | 1.1.10 | The Bidder, or the Lead company in case of JV is a EPC contractor | 1 |  | 1 |  |  |  |  | This is a non-technical question. We suggest such question should be separated from technical questions and placed in checklist for "General/Substantive Responsiveness of Bid" | a question of reliability and experience of solid understanding of the task/System Technology. See also 1.1.10 |  | 1 |  | Pass
Juwi | GD | Conditions for Disqualification and Additional Information Required | Credentials | EPC | 1.2.6 | Detailed list of all the sites with the affirmation that the bidder played the leading EPC role in the turnkey installation of these systems. | 3 |  | 1 | [7 empty] | 1 |  | Pass
Juwi | GD | Conditions for Disqualification and Additional Information Required | Credentials | EPC | 1.2.6 | Cumulative MWp of ground mounted PV turnkey installations >5 MWp with stating of actual MWp per project, project location, date of commissioning, module type and Inverter type. | 1 |  | 1 | [5 empty] | experience of Bidder / EPC |  | 1 | 1 | Pass
Juwi | GD | Conditions for Disqualification and Additional Information Required | Credentials | EPC | 1.2.6 | References and contact data (mail and phone) from owners of all installations > 5 MW with quotes of the corresponding system Performance Ratios, as well as system performance vs. initial yield assessment per year since the installation. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  | for selection of referenz objects |  | 1 | 1 | Open
Juwi | GD | Conditions for Disqualification and Additional Information Required | Credentials | EPC | 1.2.6 | Approval from bidder to owners or owner representatives to answer questions freely regarding the past performance of the bidder and performance of the system against contractual obligations. | 2 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  |  | 1 |  | Open
Juwi | GD | Conditions for Disqualification and Additional Information Required | Credentials | O&M | 1.2.6 | Cumulative MWp of ground mounted PV installations for which O&M services have been delivered by the bidder or his O&M subcontractor. | 2 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  |  | 1 |  | Open
Juwi | GD | Conditions for Disqualification and Additional Information Required | Credentials | O&M | 1.2.6 | References, contact data and approval from owners or owner representatives of all installations > 5 MW from bidder or his O&M subcontractor to answer questions freely regarding the past performance of the bidder and performance of the system against contractual obligations. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  |  | 1 | 1 | Open
Juwi | GD | Technical Bid Evaluation Criteria | Credentials | Guarantees | 1.3.1 | To have met the contractual requirements of the EPC and O&M deliverables including certificate to the effect that the entire equipment is brand new as required vide notification number NEPRA/UTS-01/777-779 dated Jan 21 ,2014, | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Only to be checked in list of deviations. |  |  | 1 | 1 | Open
Juwi | GD | Technical Bid Evaluation Criteria | Credentials | EPC | 1.3.1 | the systems have been completed on time and within budget, | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  |  | 1 | 1 | Open
Juwi | GD | Technical Bid Evaluation Criteria | Credentials | O&M | 1.3.1 | that they have started supplying electricity to the grid and are still operating satisfactorily in 9 out of 10 MW for all the cases | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  |  | 1 | 1 | Open
Juwi | GD | Technical Bid Evaluation Criteria | Credentials | O&M | 1.3.1 | In case of a non-performance, comprehensible evidence has to be given why this case will not affect this project. | 3 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  |  | 1 |  | Open
Juwi | GD | Technical Bid Evaluation Criteria | Credentials | O&M | 1.3.2 | Prove at least 100 MW of EPC experience and 50 MW of full O&M experience for a period longer than 24 months. | 1 |  | 1 | [7 empty] | 1 |  | Pass
Juwi | GD | Technical Bid Evaluation Criteria | Due Diligence | Quality Assurance | 1.3.5 | The cost of the due diligence to be carried out by the Employer through an independent technical consultant before contract signature will be taken over by the successful bidder up to an amount of 50,000 USD independent of the result. The due diligence will cover a module factory visit, an inverter factory inspection and a due diligence on the provided financial, EPC and O&M credentials including up to three site visits. | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  | Only to be checked in list of deviations. |  |  | 1 |  | Open
Juwi | GD | PR and System Performance Guarantee | System PR | Guarantees | 1.4.1 | A 25 years commitment, in the form of a whole System performance guarantee, is required. The performance guarantee is based on measuring the PR with the actual kWh-AC delivery per year adjusted for the actual POA irradiation for the same period | 1 |  |  | 1 |  | Unclear: We do not understand your proposal, please detail your proposal. Especially confirm that you are compliant with our requested criteria. |  | Only to be checked in list of deviations. |  |  | 1 | 1 | Fail
Juwi | GD | PR and System Performance Guarantee | System PR | System PR | 1.4.1 | The billing system/metering system will be installed at interconnection point of 132 kV bus bar of HV substation to be installed by the EPC Contractor and the 132 kV Transmission line of NTDC existing at site. | 2 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  | Only to be checked in list of deviations. |  |  | 1 |  | Open
Juwi | GD | PR and System Performance Guarantee | System PR | System PR | 1.4.2 | Guaranteed PR values in the form of the Table in 1.4.1 for the acceptance phase and annual output of the PV system shall be specified. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Link to table in Documents sheet |  |  | 1 | 1 | Open
Juwi | GD | PR and System Performance Guarantee | System PR | System PR | 1.4.4 | The initial PR will be first measured after the time of commissioning of the completed PV System during the acceptance phase of 30 days. | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  | Cannot be evaluated at this stage. Only to be checked in list of deviations. |  |  | 1 | 1 | Open
Juwi | GD | PR and System Performance Guarantee | Compensations | System PR | 1.4.4 | The successful Bidder shall conduct the initial PR test for the daylight hours of at least 30 consecutive days, recording data at a frequency of fifteen minute intervals or less, to validate the guaranteed PR value for acceptance. Any excused downtime (e.g., from Grid Operator ordered shutdowns, grid failure, theft, force majeure) will be excluded from that calculation by an independent consultant (Auditing Body). That day will be taken out and another day added, if the initial PR falls short of the guaranteed PR value, the successful Bidder shall be obliged to identify and rectify the causes for the performance shortfall at their own cost. | 2 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  | Cannot be evaluated at this stage. Only to be checked in list of deviations. |  |  | 1 |  | Open
Juwi | GD | PR and System Performance Guarantee | Compensations | System PR | 1.4.4 | If the measured PR within further 30 days does not reach the guaranteed PR, the Employer can demand that the price of the system will be reduced by the percentage of shortfall times 1.2 for liquidated damages or the contractor will have to install more power at its own cost or combination of both. | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  | Cannot be evaluated at this stage. Only to be checked in list of deviations. |  |  | 1 | 1 | Open
Juwi | GD | PR and System Performance Guarantee | Compensations | O&M | 1.4.5 | If the annual measured PR falls below the guaranteed PR value according to Table 1.4.1, the liquidated damages will be levied on the successful Bidder at the rate of USD 0.20-per-kWh or the kWh Value the Employer receives for each kWh of shortfall – whichever is higher. Adjustments shall be made for any events outside the control of the O&M operator as grid outages, from grid operator ordered shutdowns, or force majeure events during the year. | 2 |  |  |  | 1 |  |  | Cannot be evaluated at this stage. Only to be checked in list of deviations. | Only to be checked in list of deviations. |  | 1 |  | Open
Juwi | GD | PR and System Performance Guarantee | Compensations | O&M | 1.4.5 | In case the PR is higher than the guaranteed PR value, the net value of this excess energy will be shared as follows: 50% towards the asset replacement fund, 25% towards the Employer, 25% towards the O&M contractor | 3 |  |  |  | 1 |  |  | Cannot be evaluated at this stage. Only to be checked in list of deviations. |  |  | 1 |  | Open
Juwi | GD | PR and System Performance Guarantee | Compensations | O&M | 1.4.5 | For timely compensation the PR Calculation will be carried out provisionally for each quarter whereby the contractor and employer might jointly agree on different PR values for each quarter. In the last quarter of each calendar year the annual PR compensation of the full year will be carried out and any provisions will be offset by the annual compensation. | 3 |  |  |  | 1 |  |  | Cannot be evaluated at this stage. Only to be checked in list of deviations. |  |  | 1 |  | Open
Juwi | GD | PR and System Performance Guarantee | Compensations | O&M | 1.4.6 | If the successful Bidder defaults in being able to provide the O&M services required for the Systems performance guarantee, then it will be liable to cover all costs – but at least in the amount of Liquidated Damages imposed to the Employer by its PPA agreements - incurred by the Employer, including the loss of the guaranteed electricity export to the grid (but at a minimum rate of USD 0.20-per-kWh) for the disrupted period, in finding and hiring a replacement for the purpose. | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  | Cannot be evaluated at this stage. Only to be checked in list of deviations. |  |  | 1 | 1 | Open

## MAW (hidden)
Bidder | Expert | Chapter in RfP | Topic | Subtopic | Clause | Criteria | 1 Vital 2 Valuable 3 Not Important | Link to Bidders Documents | Pass =1 | Fail =1 | Open =1 | Question to bidder for clarification | Comments | Comments QA on Criteria | Comment on "Comments" | Typical Questions to be send to bidders if Open status | Question to bidder for clarification | Sub-category
Tbea | MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Bills of Materials, BoMs: (glass, encapsulant, backsheet, ribbon, adhesives, cable, junction box, connector) | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Tbea | MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Maximum rated power | 1 | page 840 | 1
Tbea | MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Rated power tolerance | 1 | page 840 | 1
Tbea | MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Minimum efficiency at 200 W/m² (25°, AM 1.5) | 1 | page 840 | 1
Tbea | MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Materials and workmanship warranty of a minimum of 10 years | 1 | page 840 | 1
Tbea | MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Power warranty/performance guarantee of a minimum of 25 years: the power output should not fall below 90% within 10 years, and below 80% within 25 years; linear warranty mandatory | 1 | page 840 | 1
Tbea | MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Type of cells comprising the module, and number of cells in series | 1 | page 840 | 1 | [5 empty] | manufacturer
Tbea | MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Voltage at the maximum power point | 1 | page 840 | 1
Tbea | MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Current at the maximum current point | 1 | page 840 | 1
Tbea | MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Open-circuit voltage | 1 | page 840 | 1
Tbea | MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Short-circuit current | 1 | page 840 | 1
Tbea | MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Maximum system voltage | 1 | page 840 | 1 | [5 empty] | … at SK-II safety class
Tbea | MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Operating temperature range and nominal operating cell temperature NOCT | 1 | page 840 | 1 |  |  |  |  | What range is acceptable | There is as small range anyway Will result in the PR losses
Tbea | MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Tolerance to wind (maximum load) impact (mechanical load) | 1 | page 840 | 1 | [5 empty] | minimum 2400 Pa
Tbea | MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Manufacturers installation guidelines | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Tbea | MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Manufacturers confirmation for the suitability of module for specific weather conditions and the high UV-radiation | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  | especially reliability at high UV irridiance / Product warranty | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Tbea | MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Provide guarantees and data sheets (to be transferred to Employer upon COD) | 1 | page 840 | 1
Tbea | MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Specify number of modules and total MWp to be provided | 1 |  | 1
Tbea | MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Degradation Curve from Manufacturer | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Tbea | MAW | Modules | Modules | Standards (as applicable to crystalline silicion or thin-film) | 1.14.3 | IEC 61215 | 1 |  | 1 |  |  |  |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? | no, just a statement of compliance
Tbea | MAW | Modules | Modules | Standards (as applicable to crystalline silicion or thin-film) | 1.14.3 | IEC 61416 | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? | not existing | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Tbea | MAW | Modules | Modules | Standards (as applicable to crystalline silicion or thin-film) | 1.14.3 | IEC 61646 | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? | no, just a statement of compliance | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Tbea | MAW | Modules | Modules | Standards (as applicable to crystalline silicion or thin-film) | 1.14.3 | IEC 61730 | 1 |  | 1 |  |  |  |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? | no, just a statement of compliance
Tbea | MAW | Modules | Modules | Standards (as applicable to crystalline silicion or thin-film) | 1.14.3 | IEC 60364-4-41 | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? | no, just a statement of compliance 'protection against electric shock | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Tbea | MAW | Modules | Modules | Standards (as applicable to crystalline silicion or thin-film) | 1.14.3 | IEC 61701 | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? | no, just a statement of compliance | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Tbea | MAW | Modules | Modules | Standards (as applicable to crystalline silicion or thin-film) | 1.14.3 | IEC 60904-1, IEC 60904-3 | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? | no, just a statement of compliance | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Tbea | MAW | Modules | Modules | Pre-shipment quality assurance | 1.14.4 | Pre-shipment flash tested data Quality assurance for PV modules on-site and in laboratory simulator must meet the class AAA requirements of IEC 60904-9. The sun simulator must be calibrated with a reference cell, which itself was calibrated by a member of the WPVS scheme, with a maximum uncertainty of Isc of 1%. unique barcode (SNr) and labelled performance headlines (P(mpp), I(sc), U(oc), I(mpp), U(mpp) maximum current, maximum voltage Positive power sorting | 1 | page 93 |  |  | 1 |  |  | Cannot be evaluated at this stage. | compliance necessary | C
Tbea | MAW | Modules | Modules | Pre-shipment quality assurance | 1.14.4 | All modules must undergo Electroluminiscense (EL) inspection with a resolution of minimum 4 MPixel prior to shipment. | 1 | page 93 |  |  | 1 |  |  | Cannot be evaluated at this stage. | compliance necessary | C
Tbea | MAW | Modules | Modules | Pre-shipment quality assurance | 1.14.4 | A sufficient EVA cross linking has to be verified per production line through a gel content test supervised by an accredited (IEC 17025 or national pendant) independent certified module testing agency. | 1 | page 93 |  |  | 1 |  |  | Cannot be evaluated at this stage. | compliance necessary | C
Tbea | MAW | Modules | Modules | Quality assurance on site | 1.14.5 | The modules shall undergo an incoming inspection at arrival on construction site. | 1 | page 93 |  |  | 1 |  |  | Cannot be evaluated at this stage. | stated and accepted | C
Tbea | MAW | Modules | Due Diligence | Quality Assurance | 1.14.6 | The bidder will bear the cost of the Quality assurance for PV modules on-site and in laboratory to be carried out by the Employer through an independent technical consultant up to 150,000 USD. | 1 | page 93 | 1
Tbea | MAW | Modules | Modules | Pre-shipment quality assurance | 1.14.7 | Warranties and evidence shall be given by the bidder that their selected modules have been tested for susceptibility to Potential Induced Degradation (PID). | 1 | page 93 |  |  | 1 | Unclear: We do not understand your proposal, please detail your proposal. Especially confirm that you are compliant with our requested criteria. |  |  |  | C | Unclear: We do not understand your proposal, please detail your proposal. Especially confirm that you are compliant with our requested criteria.
Tbea | MAW | Modules | Credentials | Project references | 1.14.8 | To show the proven technology a minimum of 500MW of proposed product type series must be in operation and reference projects shall be named. | 1 | page 458 |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | many plants with 10-50MWp were realized, but with same proven technology? | Related to project references |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Tbea | MAW | DC Cables | DC Cables | Specific Requirements | 1.15.1 | Are Ohmic losses less than 1% at full power? | 1 | page 858 |  |  | 1 |  |  |  | DC+AC losses < 2% | C
Tbea | MAW | DC Cables | DC Cables | Design factors to be provided | 1.15.2 | String cable shall be of the following type: single conductor type, copper, 1000 V / Class II (according to protection class II / 1000V, IEC 61140, single core cable, tinned copper conductor, XLPE Insulation, double EVA jacket (resistant to heat and cold, resistant to ozone, UV, oil and chemicals), Temperature: 90 º C (Temperature Max. Allowable: 120 º C), Halogen free | 1 |  |  |  | 1 |  |  | It should be in accordance with the inverter values. | possibly 1500V for such system design | C
Tbea | MAW | DC Cables | DC Cables | Design factors to be provided | 1.15.2 | Connectors of Modules and string cables shall be connected of self-locking type, have IP65 rating and shall be from same manufacturer and type | 1 |  |  |  | 1 | Unclear: We do not understand your proposal, please detail your proposal. Especially confirm that you are compliant with our requested criteria. |  |  |  | C | Unclear: We do not understand your proposal, please detail your proposal. Especially confirm that you are compliant with our requested criteria.
Tbea | MAW | DC Cables | DC Cables | Design factors to be provided | 1.15.2 | The DC main (downstream of combiner box) wiring harness shall have the quality: Aluminum / Copper / 1000 V / Class II | 1 |  |  |  | 1 |  |  | It should be in accordance with the inverter values. | possibly 1500V for such system design | C
Tbea | MAW | DC Cables | DC Cables | Design factors to be provided | 1.15.2 | Balance of electrical potential | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Need to be disscussed | equipotential bonding earthing mesh | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Tbea | MAW | DC Cables | DC Cables | Design factors to be provided | 1.15.2 | Installation to be verified by measurement-protocols | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Cannot be evaluated at this stage. | blanc protocol | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Tbea | MAW | DC Cables | DC Cables | Design factors to be provided | 1.15.2 | Clear and systematic labelling required | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Tbea | MAW | DC Cables | DC Cables | Design factors to be provided | 1.15.2 | Lifetime of 30 years is assured | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | What proof is required. | Life time test of nonmetal materials IEC 60811-408:2012 / (DIN EN 60811-408; VDE 0473-811-408:2012-12) 30 y assurance never seen until today | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Tbea | MAW | DC Cables | DC Cables | Design factors to be provided | 1.15.2 | Sizing of cables shall be specified according to the number of modules and strings per array | 1 |  | 1 | [5 empty] | voltage drop calculation
Tbea | MAW | DC Cables | DC Cables | Standards | 1.15.3 | IEC 60364-1 | 1 | [6 empty] | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient?
Tbea | MAW | DC Connectors | DC Connectors | Standards | 1.16.2 | EN 50521 | 1 | [6 empty] | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? | PV Connectors no, just a statement of compliance
Tbea | MAW | DC Connectors | DC Connectors | Standards | 1.16.2 | IEC 60512 | 1 | [6 empty] | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? | Connectors E-Systems no, just a statement of compliance
Tbea | MAW | DC Junction Box | DC Junction Box | Design factors to be provided | 1.17.1 | At least IP54 | 1 |  | 1 |  |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  | DC Junction box is applicable in what conditions? | depending on DC Design |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria.
Tbea | MAW | DC Junction Box | DC Junction Box | Design factors to be provided | 1.17.1 | DC fuses shall permit up to maximum 1000 V (or 1500V if designed). String box design, including all operating elements shall satisfy safety requirements | 1 |  | 1 |  |  |  |  | Will inverter voltage(1500V) effect the maximum voltage(1000V)? | depends on spec of inverter.
Tbea | MAW | DC Junction Box | DC Junction Box | Design factors to be provided | 1.17.1 | Monitored input-couples | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | Monitoring on string level? |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Tbea | MAW | DC Junction Box | DC Junction Box | Design factors to be provided | 1.17.1 | Class 2 DC surge arrestor | 1 |  | 1
Tbea | MAW | DC Junction Box | DC Junction Box | Design factors to be provided | 1.17.1 | Dust and heat protection | 1 |  | 1
Tbea | MAW | DC Junction Box | DC Junction Box | Specifications | 1.17.2 | Current monitoring | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | Monitoring on string level? |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Tbea | MAW | DC Junction Box | DC Junction Box | Specifications | 1.17.2 | Touch-safe protective cover | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Tbea | MAW | DC Junction Box | DC Junction Box | Specifications | 1.17.2, 1.17.1 | Monitoring interface for SCADA | 1 |  | 1
Tbea | MAW | DC Junction Box | DC Junction Box | Standards | 1.17.3 | EN 61000-6 | 1 | [6 empty] | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? | EMV no, just a statement of compliance
Tbea | MAW | DC Junction Box | DC Junction Box | Standards | 1.17.3 | EN 60439-1 | 1 | [6 empty] | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? | arcing fault / Störlichtbogen Verhalten no, just a statement of compliance
Tbea | MAW | DC Junction Box | DC Junction Box | Standards | 1.17.3 | EN 50178 | 1 | [6 empty] | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? | High currat devices no, just a statement of compliance
Tbea | MAW | Inverters | Warranty | Warranty option | 1.18.1 | The Bidder shall arrange a full-service package for the selected inverters for a product warranty period of 5 years, with an option to cover additional 20 years including provisions for any necessary replacements including O&M service plan guaranteeing 99% availability. | 1 |  |  |  |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | Klaus? |  |  |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria.
Tbea | MAW | Inverters | Inverters | Strategic Reason for Inverter Selection | 1.18.2 | Balance of System (BOS) costs of inverter and labour | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  | financial bid | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Tbea | MAW | Inverters | Inverters | Strategic Reason for Inverter Selection | 1.18.2 | Dust and heat protection | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  | derating? | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Tbea | MAW | Inverters | Inverters | Strategic Reason for Inverter Selection | 1.18.2 | Timely and effective monitoring at a granular/zoomed-in level | 1 |  |  |  | 1 |  |  |  |  | C
Tbea | MAW | Inverters | Inverters | Strategic Reason for Inverter Selection | 1.18.2 | Available uptime | 1
Tbea | MAW | Inverters | Inverters | Strategic Reason for Inverter Selection | 1.18.2 | Concept of protection against overload, short-circuit, grid-failure, internal failure, over-temperature (de-rating), surge protection | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Its too general, needs to be reviewed. | failure codes and consquences (automatic/manual restart, throw away safety devices) | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Tbea | MAW | Inverters | O&M | Guarantees | 1.18.2 | For central inverters concept: the bidder shall ensure with an undertaking from the manufacturer that the concerned skilled staff will be made available at the site within 24 hours of reporting the defect to the manufacturer. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | Klaus? |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Tbea | MAW | Inverters | Inverters | Functionalities | 1.18.3 | Maximum Power Point Tracking (MPPT) and string/sub-array management | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Tbea | MAW | Inverters | Inverters | Functionalities | 1.18.3 | Matching grid voltage and frequency at point-of-coupling | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Tbea | MAW | Inverters | Inverters | Functionalities | 1.18.3 | Anti-islanding protection | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Tbea | MAW | Inverters | Inverters | Functionalities | 1.18.3 | Voltage regulation through reactive power support: remotely set point control for voltage stability | 1 |  | 1 |  |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  | 8.2 needs to ensure these questions are answered in the bids. |  |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria.
Tbea | MAW | Inverters | Inverters | Functionalities | 1.18.3 | Frequency regulation | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | 8.2 needs to ensure these questions are answered in the bids. |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Tbea | MAW | Inverters | Inverters | Functionalities | 1.18.3 | Voltage and frequency fault ride-through: no disconnection of the connection through voltage dip and change of active power generation, feed-in of reactive power during the fault for voltage stabilisation | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | 8.2 needs to ensure these questions are answered in the bids. |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Tbea | MAW | Inverters | Inverters | Functionalities | 1.18.3 | Limitation of voltage fluctuation due to switching operations and long-term flicker | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | 8.2 needs to ensure these questions are answered in the bids. |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Tbea | MAW | Inverters | Inverters | Functionalities | 1.18.3 | Limitation of short-circuit current | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | 8.2 needs to ensure these questions are answered in the bids. |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Tbea | MAW | Inverters | Inverters | Functionalities | 1.18.3 | Limitation of steady-stage voltage changes to 2% of the nominal value | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Tbea | MAW | Inverters | Inverters | Functionalities | 1.18.3 | Limitation of current harmonics and higher frequency components up to 9 kHz | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Tbea | MAW | Inverters | Inverters | Functionalities | 1.18.3 | Active power control reduction: remotely set point of control in case of network congestions or risk of system collapse, if deemed necessary | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | 8.2 needs to ensure these questions are answered in the bids. |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Tbea | MAW | Inverters | Monitoring | Functionalities | 1.18.3 | Advanced communication, with intelligent alerts/warnings, to the SCADA server | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Tbea | MAW | Inverters | Inverters | Specific Requirements | 1.18.6 | Specifications of table in Schedule C shall be met | 1 |  | 1 |  |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  | Link to table |  |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria.
Tbea | MAW | Inverters | Inverters | Design factors to be provided | 1.18.7 | Input voltage range (The voltage window for MPP tracking shall accommodate the expected degradation of the modules.) | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Tbea | MAW | Inverters | Inverters | Design factors to be provided | 1.18.7 | PV array configuration options: positive ground, negative ground | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Tbea | MAW | Inverters | Inverters | Design factors to be provided | 1.18.7 | Integrated transformer/transformerless / Outside Dry Type Transformer | 1 |  | 1 |  |  |  | transformerless
Tbea | MAW | Inverters | Inverters | Design factors to be provided | 1.18.7 | Peak efficiency/ Weighted efficiency | 1 |  | 1
Tbea | MAW | Inverters | Inverters | Design factors to be provided | 1.18.7 | Nominal power | 1 |  | 1
Tbea | MAW | Inverters | Inverters | Design factors to be provided | 1.18.7 | Nominal output voltage | 1 |  | 1
Tbea | MAW | Inverters | Inverters | Design factors to be provided | 1.18.7 | Output voltage range | 1 |  | 1
Tbea | MAW | Inverters | Inverters | Design factors to be provided | 1.18.7 | Maximum output current | 1 |  | 1
Tbea | MAW | Inverters | Inverters | Design factors to be provided | 1.18.7 | Nominal output frequency, 3-phase | 1 |  | 1
Tbea | MAW | Inverters | Inverters | Design factors to be provided | 1.18.7 | Operating temperature range | 1 |  | 1 |  |  |  |  | What is the acceptable range? | 60°C Derating?
Tbea | MAW | Inverters | Inverters | Design factors to be provided | 1.18.7 | Cooling method | 1 |  | 1
Tbea | MAW | Inverters | Inverters | Design factors to be provided | 1.18.7 | Detection of insulation faults | 1 |  |  |  |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  |  |  |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria.
Tbea | MAW | Inverters | Inverters | Design factors to be provided | 1.18.7 | Protection rating: NEMA 3R, IP54/IP55/IP60 | 1 |  | 1 |  |  | Unclear: We do not understand your proposal, please detail your proposal. Especially confirm that you are compliant with our requested criteria. | IP54 |  |  |  | Unclear: We do not understand your proposal, please detail your proposal. Especially confirm that you are compliant with our requested criteria.
Tbea | MAW | Inverters | Inverters | Standards | 1.18.8 | IEEE 1547 | 1 |  | 1 |  |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? | no, just a statement of compliance Interconnecting Distributed Resources |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria.
Tbea | MAW | Inverters | Inverters | Standards | 1.18.8 | TUV, VDE, or equivalent certification of passing the relevant standards | 1 |  | 1 |  |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  |  |  |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria.
Tbea | MAW | Inverters | Inverters | Manufacturers confirmation | 1.18.9 | The Bidder shall deliver a manufacturer's confirmation in his Bid for the suitability of the inverter for the specific weather conditions applicable in Bahawalpur Pakistan. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Tbea | MAW | Inverters | Credentials | Project references | 1.18.10 | A minimum of 100 MWp of similar product/type must be in operation and reference projects shall be named. | 1 |  | 1
Tbea | MAW | Inverters | Inverters | Quality Assurance | 1.18.11 | Check of protection against overload, short-circuit, grid-failure, internal failure, over-temperature (de-rating), surge protection, detection of insulation faults of AC Cables. Bidder shall firmly specify the manufacturer, types and length of cables to be installed | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | shall? | 8.2 needs to ensure these questions are answered in the bids. |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Tbea | MAW | Inverters | Inverters | Quality Assurance | 1.18.11 | Test run in the field for maximum and EU-efficiency of all Inverters | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | shall? | 8.2 needs to ensure these questions are answered in the bids. |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Tbea | MAW | Inverters | Inverters | Quality Assurance | 1.18.11 | Test run and check of MPP tracking of all inverters | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | shall? | 8.2 needs to ensure these questions are answered in the bids. |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Tbea | MAW | Inverters | Inverters | Quality Assurance | 1.18.11 | The Bidder shall deliver detailed protocols of performance test run (warm power test) for every single inverter | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | shall? | Cannot be evaluated at this stage |  | C | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria.
Tbea | MAW | Inverters | Inverters | Quality Assurance | 1.18.11 | After commissioning, 1 of 10 inverters will be measured on site (power curve and efficiency) by an approved independent technical consultant on behalf of the Employer. The on-site measurements shall be accepted by the Bidder as average values for all inverters | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  | Cannot be evaluated at this stage | compliance! | C | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria.
Tbea | MAW | Inverters | Due diligence | Quality Assurance | 1.18.12 | The Bidder accepts that the cost of the Quality assurance for Inverters to be carried by the Employer through an independent technical consultant shall be taken over by the successful bidder up to an amount of 100,000 USD. | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  |  |  | C | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria.
Zte | MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Bills of Materials, BoMs: (glass, encapsulant, backsheet, ribbon, adhesives, cable, junction box, connector) | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Zte | MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Maximum rated power | 1 | \3-Response to Section 2\2-Schedules to Bid\Schedule F - Specific Operation Plant and Equipment Detail\3-Data Sheets, Instructions, Manuals\Module | 1 |  |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  |  |  |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria.
Zte | MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Rated power tolerance | 1 | \3-Response to Section 2\2-Schedules to Bid\Schedule F - Specific Operation Plant and Equipment Detail\3-Data Sheets, Instructions, Manuals\Module | 1 |  |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  |  |  |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria.
Zte | MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Minimum efficiency at 200 W/m² (25°, AM 1.5) | 1 | \3-Response to Section 2\2-Schedules to Bid\Schedule F - Specific Operation Plant and Equipment Detail\3-Data Sheets, Instructions, Manuals\Module | 1 |  |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  |  |  |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria.
Zte | MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Materials and workmanship warranty of a minimum of 10 years | 1 | \3-Response to Section 2\2-Schedules to Bid\Schedule F - Specific Operation Plant and Equipment Detail\3-Data Sheets, Instructions, Manuals\Module | 1 |  |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  |  |  |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria.
Zte | MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Power warranty/performance guarantee of a minimum of 25 years: the power output should not fall below 90% within 10 years, and below 80% within 25 years; linear warranty mandatory | 1 | \3-Response to Section 2\2-Schedules to Bid\Schedule F - Specific Operation Plant and Equipment Detail\3-Data Sheets, Instructions, Manuals\Module | 1 |  |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  |  |  |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria.
Zte | MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Type of cells comprising the module, and number of cells in series | 1 | \3-Response to Section 2\2-Schedules to Bid\Schedule F - Specific Operation Plant and Equipment Detail\3-Data Sheets, Instructions, Manuals\Module | 1 |  |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  |  | manufacturer |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria.
Zte | MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Voltage at the maximum power point | 1 | \3-Response to Section 2\2-Schedules to Bid\Schedule F - Specific Operation Plant and Equipment Detail\3-Data Sheets, Instructions, Manuals\Module | 1 |  |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  |  |  |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria.
Zte | MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Current at the maximum current point | 1 | \3-Response to Section 2\2-Schedules to Bid\Schedule F - Specific Operation Plant and Equipment Detail\3-Data Sheets, Instructions, Manuals\Module | 1 |  |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  |  |  |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria.
Zte | MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Open-circuit voltage | 1 | \3-Response to Section 2\2-Schedules to Bid\Schedule F - Specific Operation Plant and Equipment Detail\3-Data Sheets, Instructions, Manuals\Module | 1 |  |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  |  |  |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria.
Zte | MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Short-circuit current | 1 | \3-Response to Section 2\2-Schedules to Bid\Schedule F - Specific Operation Plant and Equipment Detail\3-Data Sheets, Instructions, Manuals\Module | 1 |  |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  |  |  |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria.
Zte | MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Maximum system voltage | 1 | \3-Response to Section 2\2-Schedules to Bid\Schedule F - Specific Operation Plant and Equipment Detail\3-Data Sheets, Instructions, Manuals\Module | 1 | [5 empty] | … at SK-II safety class
Zte | MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Operating temperature range and nominal operating cell temperature NOCT | 1 | \3-Response to Section 2\2-Schedules to Bid\Schedule F - Specific Operation Plant and Equipment Detail\3-Data Sheets, Instructions, Manuals\Module | 1 |  |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  | What range is acceptable | There is as small range anyway Will result in the PR losses |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria.
Zte | MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Tolerance to wind (maximum load) impact (mechanical load) | 1 | \3-Response to Section 2\2-Schedules to Bid\Schedule F - Specific Operation Plant and Equipment Detail\3-Data Sheets, Instructions, Manuals\Module | 1 |  |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  |  | minimum 2400 Pa |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria.
Zte | MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Manufacturers installation guidelines | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | only LDK, not Suntech |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Zte | MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Manufacturers confirmation for the suitability of module for specific weather conditions and the high UV-radiation | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  | especially reliability at high UV irridiance / Product warranty | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Zte | MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Provide guarantees and data sheets (to be transferred to Employer upon COD) | 1 | \3-Response to Section 2\2-Schedules to Bid\Schedule F - Specific Operation Plant and Equipment Detail\3-Data Sheets, Instructions, Manuals\Module | 1
Zte | MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Specify number of modules and total MWp to be provided | 1 |  | 1
Zte | MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Degradation Curve from Manufacturer | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Zte | MAW | Modules | Modules | Standards (as applicable to crystalline silicion or thin-film) | 1.14.3 | IEC 61215 | 1 | \3-Response to Section 2\2-Schedules to Bid\Schedule F - Specific Operation Plant and Equipment Detail\3-Data Sheets, Instructions, Manuals\Module |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | Suntech: ok, LDK: missing | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? | no, just a statement of compliance | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Zte | MAW | Modules | Modules | Standards (as applicable to crystalline silicion or thin-film) | 1.14.3 | IEC 61416 | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? | not existing | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Zte | MAW | Modules | Modules | Standards (as applicable to crystalline silicion or thin-film) | 1.14.3 | IEC 61646 | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? | no, just a statement of compliance | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Zte | MAW | Modules | Modules | Standards (as applicable to crystalline silicion or thin-film) | 1.14.3 | IEC 61730 | 1 |  | 1 |  |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? | no, just a statement of compliance |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria.
Zte | MAW | Modules | Modules | Standards (as applicable to crystalline silicion or thin-film) | 1.14.3 | IEC 60364-4-41 | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? | no, just a statement of compliance 'protection against electric shock | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Zte | MAW | Modules | Modules | Standards (as applicable to crystalline silicion or thin-film) | 1.14.3 | IEC 61701 | 1 | \3-Response to Section 2\2-Schedules to Bid\Schedule F - Specific Operation Plant and Equipment Detail\3-Data Sheets, Instructions, Manuals\Module | 1 |  |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? | no, just a statement of compliance |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria.
Zte | MAW | Modules | Modules | Standards (as applicable to crystalline silicion or thin-film) | 1.14.3 | IEC 60904-1, IEC 60904-3 | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? | no, just a statement of compliance | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Zte | MAW | Modules | Modules | Pre-shipment quality assurance | 1.14.4 | Pre-shipment flash tested data Quality assurance for PV modules on-site and in laboratory simulator must meet the class AAA requirements of IEC 60904-9. The sun simulator must be calibrated with a reference cell, which itself was calibrated by a member of the WPVS scheme, with a maximum uncertainty of Isc of 1%. unique barcode (SNr) and labelled performance headlines (P(mpp), I(sc), U(oc), I(mpp), U(mpp) maximum current, maximum voltage Positive power sorting | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Cannot be evaluated at this stage. | compliance necessary | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Zte | MAW | Modules | Modules | Pre-shipment quality assurance | 1.14.4 | All modules must undergo Electroluminiscense (EL) inspection with a resolution of minimum 4 MPixel prior to shipment. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Cannot be evaluated at this stage. | compliance necessary | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Zte | MAW | Modules | Modules | Pre-shipment quality assurance | 1.14.4 | A sufficient EVA cross linking has to be verified per production line through a gel content test supervised by an accredited (IEC 17025 or national pendant) independent certified module testing agency. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Cannot be evaluated at this stage. | compliance necessary | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Zte | MAW | Modules | Modules | Quality assurance on site | 1.14.5 | The modules shall undergo an incoming inspection at arrival on construction site. | 1 |  |  |  | 1 |  |  | Cannot be evaluated at this stage. | stated and accepted | C
Zte | MAW | Modules | Due Diligence | Quality Assurance | 1.14.6 | The bidder will bear the cost of the Quality assurance for PV modules on-site and in laboratory to be carried out by the Employer through an independent technical consultant up to 150,000 USD. | 1 |  |  |  | 1 |  |  |  |  | C
Zte | MAW | Modules | Modules | Pre-shipment quality assurance | 1.14.7 | Warranties and evidence shall be given by the bidder that their selected modules have been tested for susceptibility to Potential Induced Degradation (PID). | 1 |  | 1 |  |  |  | LDK and Suntech
Zte | MAW | Modules | Credentials | Project references | 1.14.8 | To show the proven technology a minimum of 500MW of proposed product type series must be in operation and reference projects shall be named. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Related to project references |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Zte | MAW | DC Cables | DC Cables | Specific Requirements | 1.15.1 | Are Ohmic losses less than 1% at full power? | 1 |  | 1 | [5 empty] | DC+AC losses < 2%
Zte | MAW | DC Cables | DC Cables | Design factors to be provided | 1.15.2 | String cable shall be of the following type: single conductor type, copper, 1000 V / Class II (according to protection class II / 1000V, IEC 61140, single core cable, tinned copper conductor, XLPE Insulation, double EVA jacket (resistant to heat and cold, resistant to ozone, UV, oil and chemicals), Temperature: 90 º C (Temperature Max. Allowable: 120 º C), Halogen free | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | It should be in accordance with the inverter values. | possibly 1500V for such system design | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Zte | MAW | DC Cables | DC Cables | Design factors to be provided | 1.15.2 | Connectors of Modules and string cables shall be connected of self-locking type, have IP65 rating and shall be from same manufacturer and type | 1 |  | 1 |  |  |  | MC4
Zte | MAW | DC Cables | DC Cables | Design factors to be provided | 1.15.2 | The DC main (downstream of combiner box) wiring harness shall have the quality: Aluminum / Copper / 1000 V / Class II | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | It should be in accordance with the inverter values. | possibly 1500V for such system design | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Zte | MAW | DC Cables | DC Cables | Design factors to be provided | 1.15.2 | Balance of electrical potential | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Need to be disscussed | equipotential bonding earthing mesh | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Zte | MAW | DC Cables | DC Cables | Design factors to be provided | 1.15.2 | Installation to be verified by measurement-protocols | 1 |  |  |  | 1 |  |  | Cannot be evaluated at this stage. | blanc protocol | C
Zte | MAW | DC Cables | DC Cables | Design factors to be provided | 1.15.2 | Clear and systematic labelling required | 1 |  |  |  | 1 |  |  |  |  | C
Zte | MAW | DC Cables | DC Cables | Design factors to be provided | 1.15.2 | Lifetime of 30 years is assured | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | What proof is required. | Life time test of nonmetal materials IEC 60811-408:2012 / (DIN EN 60811-408; VDE 0473-811-408:2012-12) 30 y assurance never seen until today | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Zte | MAW | DC Cables | DC Cables | Design factors to be provided | 1.15.2 | Sizing of cables shall be specified according to the number of modules and strings per array | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  | voltage drop calculation | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Zte | MAW | DC Cables | DC Cables | Standards | 1.15.3 | IEC 60364-1 | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Zte | MAW | DC Connectors | DC Connectors | Standards | 1.16.2 | EN 50521 | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? | PV Connectors no, just a statement of compliance | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Zte | MAW | DC Connectors | DC Connectors | Standards | 1.16.2 | IEC 60512 | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? | Connectors E-Systems no, just a statement of compliance | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Zte | MAW | DC Junction Box | DC Junction Box | Design factors to be provided | 1.17.1 | At least IP54 | 1 | \3-Response to Section 2\2-Schedules to Bid\Schedule A - Specific Works Data\1. Technical Proposal | 1 |  |  |  | IP65 | DC Junction box is applicable in what conditions? | depending on DC Design
Zte | MAW | DC Junction Box | DC Junction Box | Design factors to be provided | 1.17.1 | DC fuses shall permit up to maximum 1000 V (or 1500V if designed). String box design, including all operating elements shall satisfy safety requirements | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | equipotential connection? | Will inverter voltage(1500V) effect the maximum voltage(1000V)? | depends on spec of inverter. | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Zte | MAW | DC Junction Box | DC Junction Box | Design factors to be provided | 1.17.1 | Monitored input-couples | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Zte | MAW | DC Junction Box | DC Junction Box | Design factors to be provided | 1.17.1 | Class 2 DC surge arrestor | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Zte | MAW | DC Junction Box | DC Junction Box | Design factors to be provided | 1.17.1 | Dust and heat protection | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Zte | MAW | DC Junction Box | DC Junction Box | Specifications | 1.17.2 | Current monitoring | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Zte | MAW | DC Junction Box | DC Junction Box | Specifications | 1.17.2 | Touch-safe protective cover | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | no cover, just small boxes |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Zte | MAW | DC Junction Box | DC Junction Box | Specifications | 1.17.2, 1.17.1 | Monitoring interface for SCADA | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Zte | MAW | DC Junction Box | DC Junction Box | Standards | 1.17.3 | EN 61000-6 | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? | EMV no, just a statement of compliance | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Zte | MAW | DC Junction Box | DC Junction Box | Standards | 1.17.3 | EN 60439-1 | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? | arcing fault / Störlichtbogen Verhalten no, just a statement of compliance | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Zte | MAW | DC Junction Box | DC Junction Box | Standards | 1.17.3 | EN 50178 | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? | High currat devices no, just a statement of compliance | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Zte | MAW | Inverters | Warranty | Warranty option | 1.18.1 | The Bidder shall arrange a full-service package for the selected inverters for a product warranty period of 5 years, with an option to cover additional 20 years including provisions for any necessary replacements including O&M service plan guaranteeing 99% availability. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Zte | MAW | Inverters | Inverters | Strategic Reason for Inverter Selection | 1.18.2 | Balance of System (BOS) costs of inverter and labour | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  | financial bid | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Zte | MAW | Inverters | Inverters | Strategic Reason for Inverter Selection | 1.18.2 | Dust and heat protection | 1 | \3-Response to Section 2\2-Schedules to Bid\Schedule F - Specific Operation Plant and Equipment Detail\3-Data Sheets, Instructions, Manuals\Inverter\Datasheet |  |  | 1 |  |  |  | derating?
Zte | MAW | Inverters | Inverters | Strategic Reason for Inverter Selection | 1.18.2 | Timely and effective monitoring at a granular/zoomed-in level | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Zte | MAW | Inverters | Inverters | Strategic Reason for Inverter Selection | 1.18.2 | Available uptime | 1 | \3-Response to Section 2\2-Schedules to Bid\Schedule F - Specific Operation Plant and Equipment Detail\3-Data Sheets, Instructions, Manuals\Inverter\Datasheet |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Zte | MAW | Inverters | Inverters | Strategic Reason for Inverter Selection | 1.18.2 | Concept of protection against overload, short-circuit, grid-failure, internal failure, over-temperature (de-rating), surge protection | 1 | \3-Response to Section 2\2-Schedules to Bid\Schedule F - Specific Operation Plant and Equipment Detail\3-Data Sheets, Instructions, Manuals\Inverter\Datasheet |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | partly confirmed | Its too general, needs to be reviewed. | failure codes and consquences (automatic/manual restart, throw away safety devices) | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Zte | MAW | Inverters | O&M | Guarantees | 1.18.2 | For central inverters concept: the bidder shall ensure with an undertaking from the manufacturer that the concerned skilled staff will be made available at the site within 24 hours of reporting the defect to the manufacturer. | 1 | \3-Response to Section 2\2-Schedules to Bid\Schedule F - Specific Operation Plant and Equipment Detail\3-Data Sheets, Instructions, Manuals\Inverter\Datasheet |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Zte | MAW | Inverters | Inverters | Functionalities | 1.18.3 | Maximum Power Point Tracking (MPPT) and string/sub-array management | 1 | \3-Response to Section 2\2-Schedules to Bid\Schedule F - Specific Operation Plant and Equipment Detail\3-Data Sheets, Instructions, Manuals\Inverter\Datasheet |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Zte | MAW | Inverters | Inverters | Functionalities | 1.18.3 | Matching grid voltage and frequency at point-of-coupling | 1 | \3-Response to Section 2\2-Schedules to Bid\Schedule F - Specific Operation Plant and Equipment Detail\3-Data Sheets, Instructions, Manuals\Inverter\Datasheet |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Zte | MAW | Inverters | Inverters | Functionalities | 1.18.3 | Anti-islanding protection | 1 | \3-Response to Section 2\2-Schedules to Bid\Schedule F - Specific Operation Plant and Equipment Detail\3-Data Sheets, Instructions, Manuals\Inverter\Datasheet | 1
Zte | MAW | Inverters | Inverters | Functionalities | 1.18.3 | Voltage regulation through reactive power support: remotely set point control for voltage stability | 1 | \3-Response to Section 2\2-Schedules to Bid\Schedule F - Specific Operation Plant and Equipment Detail\3-Data Sheets, Instructions, Manuals\Inverter\Datasheet | 1 |  |  |  |  | 8.2 needs to ensure these questions are answered in the bids.
Zte | MAW | Inverters | Inverters | Functionalities | 1.18.3 | Frequency regulation | 1 | \3-Response to Section 2\2-Schedules to Bid\Schedule F - Specific Operation Plant and Equipment Detail\3-Data Sheets, Instructions, Manuals\Inverter\Datasheet |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | 8.2 needs to ensure these questions are answered in the bids. |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Zte | MAW | Inverters | Inverters | Functionalities | 1.18.3 | Voltage and frequency fault ride-through: no disconnection of the connection through voltage dip and change of active power generation, feed-in of reactive power during the fault for voltage stabilisation | 1 | \3-Response to Section 2\2-Schedules to Bid\Schedule F - Specific Operation Plant and Equipment Detail\3-Data Sheets, Instructions, Manuals\Inverter\Datasheet | 1 |  |  |  |  | 8.2 needs to ensure these questions are answered in the bids.
Zte | MAW | Inverters | Inverters | Functionalities | 1.18.3 | Limitation of voltage fluctuation due to switching operations and long-term flicker | 1 | \3-Response to Section 2\2-Schedules to Bid\Schedule F - Specific Operation Plant and Equipment Detail\3-Data Sheets, Instructions, Manuals\Inverter\Datasheet |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | 8.2 needs to ensure these questions are answered in the bids. |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Zte | MAW | Inverters | Inverters | Functionalities | 1.18.3 | Limitation of short-circuit current | 1 | \3-Response to Section 2\2-Schedules to Bid\Schedule F - Specific Operation Plant and Equipment Detail\3-Data Sheets, Instructions, Manuals\Inverter\Datasheet |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | 8.2 needs to ensure these questions are answered in the bids. |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Zte | MAW | Inverters | Inverters | Functionalities | 1.18.3 | Limitation of steady-stage voltage changes to 2% of the nominal value | 1 | \3-Response to Section 2\2-Schedules to Bid\Schedule F - Specific Operation Plant and Equipment Detail\3-Data Sheets, Instructions, Manuals\Inverter\Datasheet |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Zte | MAW | Inverters | Inverters | Functionalities | 1.18.3 | Limitation of current harmonics and higher frequency components up to 9 kHz | 1 | \3-Response to Section 2\2-Schedules to Bid\Schedule F - Specific Operation Plant and Equipment Detail\3-Data Sheets, Instructions, Manuals\Inverter\Datasheet |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Zte | MAW | Inverters | Inverters | Functionalities | 1.18.3 | Active power control reduction: remotely set point of control in case of network congestions or risk of system collapse, if deemed necessary | 1 | \3-Response to Section 2\2-Schedules to Bid\Schedule F - Specific Operation Plant and Equipment Detail\3-Data Sheets, Instructions, Manuals\Inverter\Datasheet |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | 8.2 needs to ensure these questions are answered in the bids. |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Zte | MAW | Inverters | Monitoring | Functionalities | 1.18.3 | Advanced communication, with intelligent alerts/warnings, to the SCADA server | 1 | \3-Response to Section 2\2-Schedules to Bid\Schedule F - Specific Operation Plant and Equipment Detail\3-Data Sheets, Instructions, Manuals\Inverter\Datasheet |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Zte | MAW | Inverters | Inverters | Specific Requirements | 1.18.6 | Specifications of table in Schedule C shall be met | 1 | \3-Response to Section 2\2-Schedules to Bid\Schedule F - Specific Operation Plant and Equipment Detail\3-Data Sheets, Instructions, Manuals\Inverter\Datasheet | 1 |  |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  | Link to table |  |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria.
Zte | MAW | Inverters | Inverters | Design factors to be provided | 1.18.7 | Input voltage range (The voltage window for MPP tracking shall accommodate the expected degradation of the modules.) | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Zte | MAW | Inverters | Inverters | Design factors to be provided | 1.18.7 | PV array configuration options: positive ground, negative ground | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Zte | MAW | Inverters | Inverters | Design factors to be provided | 1.18.7 | Integrated transformer/transformerless / Outside Dry Type Transformer | 1 |  | 1 |  |  |  | no transformer
Zte | MAW | Inverters | Inverters | Design factors to be provided | 1.18.7 | Peak efficiency/ Weighted efficiency | 1 |  | 1
Zte | MAW | Inverters | Inverters | Design factors to be provided | 1.18.7 | Nominal power | 1 |  | 1
Zte | MAW | Inverters | Inverters | Design factors to be provided | 1.18.7 | Nominal output voltage | 1 |  | 1
Zte | MAW | Inverters | Inverters | Design factors to be provided | 1.18.7 | Output voltage range | 1 |  | 1
Zte | MAW | Inverters | Inverters | Design factors to be provided | 1.18.7 | Maximum output current | 1 |  | 1
Zte | MAW | Inverters | Inverters | Design factors to be provided | 1.18.7 | Nominal output frequency, 3-phase | 1 |  | 1
Zte | MAW | Inverters | Inverters | Design factors to be provided | 1.18.7 | Operating temperature range | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | -25℃~+55℃(>45℃derating) | What is the acceptable range? | 60°C Derating? | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Zte | MAW | Inverters | Inverters | Design factors to be provided | 1.18.7 | Cooling method | 1 |  | 1 |  |  | Unclear: We do not understand your proposal, please detail your proposal. Especially confirm that you are compliant with our requested criteria. |  |  |  |  | Unclear: We do not understand your proposal, please detail your proposal. Especially confirm that you are compliant with our requested criteria.
Zte | MAW | Inverters | Inverters | Design factors to be provided | 1.18.7 | Detection of insulation faults | 1 |  | 1 |  |  | Unclear: We do not understand your proposal, please detail your proposal. Especially confirm that you are compliant with our requested criteria. |  |  |  |  | Unclear: We do not understand your proposal, please detail your proposal. Especially confirm that you are compliant with our requested criteria.
Zte | MAW | Inverters | Inverters | Design factors to be provided | 1.18.7 | Protection rating: NEMA 3R, IP54/IP55/IP60 | 1 |  | 1 |  |  | Unclear: We do not understand your proposal, please detail your proposal. Especially confirm that you are compliant with our requested criteria. | IP54 |  |  |  | Unclear: We do not understand your proposal, please detail your proposal. Especially confirm that you are compliant with our requested criteria.
Zte | MAW | Inverters | Inverters | Standards | 1.18.8 | IEEE 1547 | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? | no, just a statement of compliance Interconnecting Distributed Resources | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Zte | MAW | Inverters | Inverters | Standards | 1.18.8 | TUV, VDE, or equivalent certification of passing the relevant standards | 1 | \3-Response to Section 2\2-Schedules to Bid\Schedule F - Specific Operation Plant and Equipment Detail\3-Data Sheets, Instructions, Manuals\Inverter\Datasheet | 1
Zte | MAW | Inverters | Inverters | Manufacturers confirmation | 1.18.9 | The Bidder shall deliver a manufacturer's confirmation in his Bid for the suitability of the inverter for the specific weather conditions applicable in Bahawalpur Pakistan. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Zte | MAW | Inverters | Credentials | Project references | 1.18.10 | A minimum of 100 MWp of similar product/type must be in operation and reference projects shall be named. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Zte | MAW | Inverters | Inverters | Quality Assurance | 1.18.11 | Check of protection against overload, short-circuit, grid-failure, internal failure, over-temperature (de-rating), surge protection, detection of insulation faults of AC Cables. Bidder shall firmly specify the manufacturer, types and length of cables to be installed | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | 8.2 needs to ensure these questions are answered in the bids. |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Zte | MAW | Inverters | Inverters | Quality Assurance | 1.18.11 | Test run in the field for maximum and EU-efficiency of all Inverters | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | 8.2 needs to ensure these questions are answered in the bids. |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Zte | MAW | Inverters | Inverters | Quality Assurance | 1.18.11 | Test run and check of MPP tracking of all inverters | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | 8.2 needs to ensure these questions are answered in the bids. |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Zte | MAW | Inverters | Inverters | Quality Assurance | 1.18.11 | The Bidder shall deliver detailed protocols of performance test run (warm power test) for every single inverter | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Cannot be evaluated at this stage |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Zte | MAW | Inverters | Inverters | Quality Assurance | 1.18.11 | After commissioning, 1 of 10 inverters will be measured on site (power curve and efficiency) by an approved independent technical consultant on behalf of the Employer. The on-site measurements shall be accepted by the Bidder as average values for all inverters | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Cannot be evaluated at this stage | compliance! | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Zte | MAW | Inverters | Due diligence | Quality Assurance | 1.18.12 | The Bidder accepts that the cost of the Quality assurance for Inverters to be carried by the Employer through an independent technical consultant shall be taken over by the successful bidder up to an amount of 100,000 USD. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Juwi | MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Bills of Materials, BoMs: (glass, encapsulant, backsheet, ribbon, adhesives, cable, junction box, connector) | 1 |  | 1
Juwi | MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Maximum rated power | 1 | page 59 | 1
Juwi | MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Rated power tolerance | 1 | page 59 | 1
Juwi | MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Minimum efficiency at 200 W/m² (25°, AM 1.5) | 1 | page 59 | 1
Juwi | MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Materials and workmanship warranty of a minimum of 10 years | 1 | page 59 | 1 |  |  |  | 12 years
Juwi | MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Power warranty/performance guarantee of a minimum of 25 years: the power output should not fall below 90% within 10 years, and below 80% within 25 years; linear warranty mandatory | 1 | page 59 | 1
Juwi | MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Type of cells comprising the module, and number of cells in series | 1 | page 59 | 1 | [5 empty] | manufacturer
Juwi | MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Voltage at the maximum power point | 1 | page 59 | 1
Juwi | MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Current at the maximum current point | 1 | page 59 | 1
Juwi | MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Open-circuit voltage | 1 | page 59 | 1
Juwi | MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Short-circuit current | 1 | page 59 | 1
Juwi | MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Maximum system voltage | 1 | page 59 | 1 | [5 empty] | … at SK-II safety class
Juwi | MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Operating temperature range and nominal operating cell temperature NOCT | 1 | page 59 | 1 |  |  |  |  | What range is acceptable | There is as small range anyway Will result in the PR losses
Juwi | MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Tolerance to wind (maximum load) impact (mechanical load) | 1 | page 59 | 1 | [5 empty] | minimum 2400 Pa
Juwi | MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Manufacturers installation guidelines | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Juwi | MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Manufacturers confirmation for the suitability of module for specific weather conditions and the high UV-radiation | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  | especially reliability at high UV irridiance / Product warranty | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Juwi | MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Provide guarantees and data sheets (to be transferred to Employer upon COD) | 1 |  | 1
Juwi | MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Specify number of modules and total MWp to be provided | 1 | page 392 | 1
Juwi | MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Degradation Curve from Manufacturer | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Juwi | MAW | Modules | Modules | Standards (as applicable to crystalline silicion or thin-film) | 1.14.3 | IEC 61215 | 1 | page 59 | 1 |  |  |  |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? | no, just a statement of compliance
Juwi | MAW | Modules | Modules | Standards (as applicable to crystalline silicion or thin-film) | 1.14.3 | IEC 61416 | 1 | page 59 |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? | not existing | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Juwi | MAW | Modules | Modules | Standards (as applicable to crystalline silicion or thin-film) | 1.14.3 | IEC 61646 | 1 | page 59 |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? | no, just a statement of compliance | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Juwi | MAW | Modules | Modules | Standards (as applicable to crystalline silicion or thin-film) | 1.14.3 | IEC 61730 | 1 | page 59 | 1 |  |  |  |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? | no, just a statement of compliance
Juwi | MAW | Modules | Modules | Standards (as applicable to crystalline silicion or thin-film) | 1.14.3 | IEC 60364-4-41 | 1 | page 59 |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? | no, just a statement of compliance 'protection against electric shock | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Juwi | MAW | Modules | Modules | Standards (as applicable to crystalline silicion or thin-film) | 1.14.3 | IEC 61701 | 1 | page 59 |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? | no, just a statement of compliance | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Juwi | MAW | Modules | Modules | Standards (as applicable to crystalline silicion or thin-film) | 1.14.3 | IEC 60904-1, IEC 60904-3 | 1 | page 59 |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? | no, just a statement of compliance | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Juwi | MAW | Modules | Modules | Pre-shipment quality assurance | 1.14.4 | Pre-shipment flash tested data Quality assurance for PV modules on-site and in laboratory simulator must meet the class AAA requirements of IEC 60904-9. The sun simulator must be calibrated with a reference cell, which itself was calibrated by a member of the WPVS scheme, with a maximum uncertainty of Isc of 1%. unique barcode (SNr) and labelled performance headlines (P(mpp), I(sc), U(oc), I(mpp), U(mpp) maximum current, maximum voltage Positive power sorting | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Cannot be evaluated at this stage. | compliance necessary | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Juwi | MAW | Modules | Modules | Pre-shipment quality assurance | 1.14.4 | All modules must undergo Electroluminiscense (EL) inspection with a resolution of minimum 4 MPixel prior to shipment. | 1 | page 89 | 1 |  |  |  |  | Cannot be evaluated at this stage. | compliance necessary
Juwi | MAW | Modules | Modules | Pre-shipment quality assurance | 1.14.4 | A sufficient EVA cross linking has to be verified per production line through a gel content test supervised by an accredited (IEC 17025 or national pendant) independent certified module testing agency. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Cannot be evaluated at this stage. | compliance necessary | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Juwi | MAW | Modules | Modules | Quality assurance on site | 1.14.5 | The modules shall undergo an incoming inspection at arrival on construction site. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Cannot be evaluated at this stage. | stated and accepted | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Juwi | MAW | Modules | Due Diligence | Quality Assurance | 1.14.6 | The bidder will bear the cost of the Quality assurance for PV modules on-site and in laboratory to be carried out by the Employer through an independent technical consultant up to 150,000 USD. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Juwi | MAW | Modules | Modules | Pre-shipment quality assurance | 1.14.7 | Warranties and evidence shall be given by the bidder that their selected modules have been tested for susceptibility to Potential Induced Degradation (PID). | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | Additional Tests available |  |  | C | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria.
Juwi | MAW | Modules | Credentials | Project references | 1.14.8 | To show the proven technology a minimum of 500MW of proposed product type series must be in operation and reference projects shall be named. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Related to project references |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Juwi | MAW | DC Connectors | DC Connectors | Standards | 1.16.2 | EN 50521 | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? | PV Connectors no, just a statement of compliance | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Juwi | MAW | DC Connectors | DC Connectors | Standards | 1.16.2 | IEC 60512 | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? | Connectors E-Systems no, just a statement of compliance | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Juwi | MAW | Inverters | Warranty | Warranty option | 1.18.1 | The Bidder shall arrange a full-service package for the selected inverters for a product warranty period of 5 years, with an option to cover additional 20 years including provisions for any necessary replacements including O&M service plan guaranteeing 99% availability. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Juwi | MAW | Inverters | Inverters | Strategic Reason for Inverter Selection | 1.18.2 | Balance of System (BOS) costs of inverter and labour | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  | financial bid | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Juwi | MAW | Inverters | Inverters | Strategic Reason for Inverter Selection | 1.18.2 | Dust and heat protection | 1 |  | 1 | [5 empty] | derating?
Juwi | MAW | Inverters | Inverters | Strategic Reason for Inverter Selection | 1.18.2 | Timely and effective monitoring at a granular/zoomed-in level | 1 |  | 1
Juwi | MAW | Inverters | Inverters | Strategic Reason for Inverter Selection | 1.18.2 | Available uptime | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Juwi | MAW | Inverters | Inverters | Strategic Reason for Inverter Selection | 1.18.2 | Concept of protection against overload, short-circuit, grid-failure, internal failure, over-temperature (de-rating), surge protection | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Its too general, needs to be reviewed. | failure codes and consquences (automatic/manual restart, throw away safety devices) | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Juwi | MAW | Inverters | O&M | Guarantees | 1.18.2 | For central inverters concept: the bidder shall ensure with an undertaking from the manufacturer that the concerned skilled staff will be made available at the site within 24 hours of reporting the defect to the manufacturer. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Juwi | MAW | Inverters | Inverters | Functionalities | 1.18.3 | Maximum Power Point Tracking (MPPT) and string/sub-array management | 1 | page 291 | 1
Juwi | MAW | Inverters | Inverters | Functionalities | 1.18.3 | Matching grid voltage and frequency at point-of-coupling | 1 | page 291 | 1
Juwi | MAW | Inverters | Inverters | Functionalities | 1.18.3 | Anti-islanding protection | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Juwi | MAW | Inverters | Inverters | Functionalities | 1.18.3 | Voltage regulation through reactive power support: remotely set point control for voltage stability | 1 | page 291 | 1 |  |  |  |  | 8.2 needs to ensure these questions are answered in the bids.
Juwi | MAW | Inverters | Inverters | Functionalities | 1.18.3 | Frequency regulation | 1 | page 291 | 1 |  |  |  |  | 8.2 needs to ensure these questions are answered in the bids.
Juwi | MAW | Inverters | Inverters | Functionalities | 1.18.3 | Voltage and frequency fault ride-through: no disconnection of the connection through voltage dip and change of active power generation, feed-in of reactive power during the fault for voltage stabilisation | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | 8.2 needs to ensure these questions are answered in the bids. |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Juwi | MAW | Inverters | Inverters | Functionalities | 1.18.3 | Limitation of voltage fluctuation due to switching operations and long-term flicker | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | 8.2 needs to ensure these questions are answered in the bids. |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Juwi | MAW | Inverters | Inverters | Functionalities | 1.18.3 | Limitation of short-circuit current | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | 8.2 needs to ensure these questions are answered in the bids. |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Juwi | MAW | Inverters | Inverters | Functionalities | 1.18.3 | Limitation of steady-stage voltage changes to 2% of the nominal value | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Juwi | MAW | Inverters | Inverters | Functionalities | 1.18.3 | Limitation of current harmonics and higher frequency components up to 9 kHz | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Juwi | MAW | Inverters | Inverters | Functionalities | 1.18.3 | Active power control reduction: remotely set point of control in case of network congestions or risk of system collapse, if deemed necessary | 1 | page 291 | 1 |  |  |  |  | 8.2 needs to ensure these questions are answered in the bids.
Juwi | MAW | Inverters | Monitoring | Functionalities | 1.18.3 | Advanced communication, with intelligent alerts/warnings, to the SCADA server | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Juwi | MAW | Inverters | Inverters | Specific Requirements | 1.18.6 | Specifications of table in Schedule C shall be met | 1 | page 291 | 1 |  |  |  |  | Link to table
Juwi | MAW | Inverters | Inverters | Design factors to be provided | 1.18.7 | Input voltage range (The voltage window for MPP tracking shall accommodate the expected degradation of the modules.) | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Juwi | MAW | Inverters | Inverters | Design factors to be provided | 1.18.7 | PV array configuration options: positive ground, negative ground | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Juwi | MAW | Inverters | Inverters | Design factors to be provided | 1.18.7 | Integrated transformer/transformerless / Outside Dry Type Transformer | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Juwi | MAW | Inverters | Inverters | Design factors to be provided | 1.18.7 | Peak efficiency/ Weighted efficiency | 1 | page 291 | 1
Juwi | MAW | Inverters | Inverters | Design factors to be provided | 1.18.7 | Nominal power | 1 | page 291 | 1
Juwi | MAW | Inverters | Inverters | Design factors to be provided | 1.18.7 | Nominal output voltage | 1 | page 291 | 1
Juwi | MAW | Inverters | Inverters | Design factors to be provided | 1.18.7 | Output voltage range | 1 | page 291 | 1
Juwi | MAW | Inverters | Inverters | Design factors to be provided | 1.18.7 | Maximum output current | 1 | page 291 | 1
Juwi | MAW | Inverters | Inverters | Design factors to be provided | 1.18.7 | Nominal output frequency, 3-phase | 1 | page 291 | 1
Juwi | MAW | Inverters | Inverters | Design factors to be provided | 1.18.7 | Operating temperature range | 1 | page 291 | 1 |  |  |  |  | What is the acceptable range? | 60°C Derating?
Juwi | MAW | Inverters | Inverters | Design factors to be provided | 1.18.7 | Cooling method | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Juwi | MAW | Inverters | Inverters | Design factors to be provided | 1.18.7 | Detection of insulation faults | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Juwi | MAW | Inverters | Inverters | Design factors to be provided | 1.18.7 | Protection rating: NEMA 3R, IP54/IP55/IP60 | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Juwi | MAW | Inverters | Inverters | Standards | 1.18.8 | IEEE 1547 | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? | no, just a statement of compliance Interconnecting Distributed Resources | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Juwi | MAW | Inverters | Inverters | Standards | 1.18.8 | TUV, VDE, or equivalent certification of passing the relevant standards | 1 | page 291 | 1
Juwi | MAW | Inverters | Inverters | Manufacturers confirmation | 1.18.9 | The Bidder shall deliver a manufacturer's confirmation in his Bid for the suitability of the inverter for the specific weather conditions applicable in Bahawalpur Pakistan. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Juwi | MAW | Inverters | Credentials | Project references | 1.18.10 | A minimum of 100 MWp of similar product/type must be in operation and reference projects shall be named. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Juwi | MAW | Inverters | Inverters | Quality Assurance | 1.18.11 | Check of protection against overload, short-circuit, grid-failure, internal failure, over-temperature (de-rating), surge protection, detection of insulation faults of AC Cables. Bidder shall firmly specify the manufacturer, types and length of cables to be installed | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | 8.2 needs to ensure these questions are answered in the bids. |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Juwi | MAW | Inverters | Inverters | Quality Assurance | 1.18.11 | Test run in the field for maximum and EU-efficiency of all Inverters | 1 |  |  |  | 1 |  |  | 8.2 needs to ensure these questions are answered in the bids. |  | C
Juwi | MAW | Inverters | Inverters | Quality Assurance | 1.18.11 | Test run and check of MPP tracking of all inverters | 1 |  |  |  | 1 |  |  | 8.2 needs to ensure these questions are answered in the bids. |  | C
Juwi | MAW | Inverters | Inverters | Quality Assurance | 1.18.11 | The Bidder shall deliver detailed protocols of performance test run (warm power test) for every single inverter | 1 |  |  |  | 1 |  |  | Cannot be evaluated at this stage |  | C
Juwi | MAW | Inverters | Inverters | Quality Assurance | 1.18.11 | After commissioning, 1 of 10 inverters will be measured on site (power curve and efficiency) by an approved independent technical consultant on behalf of the Employer. The on-site measurements shall be accepted by the Bidder as average values for all inverters | 1 |  |  |  | 1 |  |  | Cannot be evaluated at this stage | compliance! | C
Juwi | MAW | Inverters | Due diligence | Quality Assurance | 1.18.12 | The Bidder accepts that the cost of the Quality assurance for Inverters to be carried by the Employer through an independent technical consultant shall be taken over by the successful bidder up to an amount of 100,000 USD. | 1 |  |  |  | 1 |  |  |  |  | C
Juwi | JBU MAW | DC Cables | DC Cables | Specific Requirements | 1.15.1 | Are Ohmic losses less than 1% at full power? | 1 |  |  | 1 | 1 |  | page 392, 2%; page 395, 1,4% |  | DC+AC losses < 2% | U
Juwi | JBU MAW | DC Cables | DC Cables | Design factors to be provided | 1.15.2 | String cable shall be of the following type: single conductor type, copper, 1000 V / Class II (according to protection class II / 1000V, IEC 61140, single core cable, tinned copper conductor, XLPE Insulation, double EVA jacket (resistant to heat and cold, resistant to ozone, UV, oil and chemicals), Temperature: 90 º C (Temperature Max. Allowable: 120 º C), Halogen free | 1 |  | 1 |  |  |  |  | It should be in accordance with the inverter values. | possibly 1500V for such system design
Juwi | JBU MAW | DC Cables | DC Cables | Design factors to be provided | 1.15.2 | Connectors of Modules and string cables shall be connected of self-locking type, have IP65 rating and shall be from same manufacturer and type | 1 |  | 1
Juwi | JBU MAW | DC Cables | DC Cables | Design factors to be provided | 1.15.2 | The DC main (downstream of combiner box) wiring harness shall have the quality: Aluminum / Copper / 1000 V / Class II | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | It should be in accordance with the inverter values. | possibly 1500V for such system design | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Juwi | JBU MAW | DC Cables | DC Cables | Design factors to be provided | 1.15.2 | Balance of electrical potential | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Need to be disscussed | equipotential bonding earthing mesh | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Juwi | JBU MAW | DC Cables | DC Cables | Design factors to be provided | 1.15.2 | Installation to be verified by measurement-protocols | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Cannot be evaluated at this stage. | blanc protocol | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Juwi | JBU MAW | DC Cables | DC Cables | Design factors to be provided | 1.15.2 | Clear and systematic labelling required | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Juwi | JBU MAW | DC Cables | DC Cables | Design factors to be provided | 1.15.2 | Lifetime of 30 years is assured | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | What proof is required. | Life time test of nonmetal materials IEC 60811-408:2012 / (DIN EN 60811-408; VDE 0473-811-408:2012-12) 30 y assurance never seen until today | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Juwi | JBU MAW | DC Cables | DC Cables | Design factors to be provided | 1.15.2 | Sizing of cables shall be specified according to the number of modules and strings per array | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  | voltage drop calculation | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Juwi | JBU MAW | DC Cables | DC Cables | Standards | 1.15.3 | IEC 60364-1 | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Juwi | JBU MAW | DC Junction Box | DC Junction Box | Design factors to be provided | 1.17.1 | At least IP54 | 1 |  | 1 |  |  |  |  | DC Junction box is applicable in what conditions? | depending on DC Design
Juwi | JBU MAW | DC Junction Box | DC Junction Box | Design factors to be provided | 1.17.1 | DC fuses shall permit up to maximum 1000 V (or 1500V if designed). String box design, including all operating elements shall satisfy safety requirements | 1 |  | 1 |  |  |  |  | Will inverter voltage(1500V) effect the maximum voltage(1000V)? | depends on spec of inverter.
Juwi | JBU MAW | DC Junction Box | DC Junction Box | Design factors to be provided | 1.17.1 | Monitored input-couples | 1 |  | 1
Juwi | JBU MAW | DC Junction Box | DC Junction Box | Design factors to be provided | 1.17.1 | Class 2 DC surge arrestor | 1 |  | 1
Juwi | JBU MAW | DC Junction Box | DC Junction Box | Design factors to be provided | 1.17.1 | Dust and heat protection | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Juwi | JBU MAW | DC Junction Box | DC Junction Box | Specifications | 1.17.2 | Current monitoring | 1 |  | 1
Juwi | JBU MAW | DC Junction Box | DC Junction Box | Specifications | 1.17.2 | Touch-safe protective cover | 1 |  |  |  | 1 |  |  |  |  | C
Juwi | JBU MAW | DC Junction Box | DC Junction Box | Specifications | 1.17.2, 1.17.1 | Monitoring interface for SCADA | 1 |  | 1
Juwi | JBU MAW | DC Junction Box | DC Junction Box | Standards | 1.17.3 | EN 61000-6 | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? | EMV no, just a statement of compliance | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Juwi | JBU MAW | DC Junction Box | DC Junction Box | Standards | 1.17.3 | EN 60439-1 | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? | arcing fault / Störlichtbogen Verhalten no, just a statement of compliance | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Juwi | JBU MAW | DC Junction Box | DC Junction Box | Standards | 1.17.3 | EN 50178 | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? | High currat devices no, just a statement of compliance | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Chint | MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Bills of Materials, BoMs: (glass, encapsulant, backsheet, ribbon, adhesives, cable, junction box, connector) | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Chint | MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Maximum rated power | 1 | Doc 3&4 page 109 | 1
Chint | MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Rated power tolerance | 1 | Doc 3&4 page 109 | 1
Chint | MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Minimum efficiency at 200 W/m² (25°, AM 1.5) | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Chint | MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Materials and workmanship warranty of a minimum of 10 years | 1 | Doc 3&4 page 109 |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | Extended product warranty --> materials and workmanship? |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Chint | MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Power warranty/performance guarantee of a minimum of 25 years: the power output should not fall below 90% within 10 years, and below 80% within 25 years; linear warranty mandatory | 1 | Doc 3&4 page 109 | 1
Chint | MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Type of cells comprising the module, and number of cells in series | 1 | Doc 3&4 page 109 | 1 | [5 empty] | manufacturer
Chint | MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Voltage at the maximum power point | 1 | Doc 3&4 page 109 | 1
Chint | MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Current at the maximum current point | 1 | Doc 3&4 page 109 | 1
Chint | MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Open-circuit voltage | 1 | Doc 3&4 page 109 | 1
Chint | MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Short-circuit current | 1 | Doc 3&4 page 109 | 1
Chint | MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Maximum system voltage | 1 | Doc 3&4 page 109 | 1 | [5 empty] | … at SK-II safety class
Chint | MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Operating temperature range and nominal operating cell temperature NOCT | 1 | Doc 3&4 page 109 | 1 |  |  |  |  | What range is acceptable | There is as small range anyway Will result in the PR losses
Chint | MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Tolerance to wind (maximum load) impact (mechanical load) | 1 | Doc 3&4 page 109 | 1 | [5 empty] | minimum 2400 Pa
Chint | MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Manufacturers installation guidelines | 1 |  |  |  | 1 |  |  |  |  | C
Chint | MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Manufacturers confirmation for the suitability of module for specific weather conditions and the high UV-radiation | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  | especially reliability at high UV irridiance / Product warranty | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Chint | MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Provide guarantees and data sheets (to be transferred to Employer upon COD) | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Chint | MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Specify number of modules and total MWp to be provided | 1 | Doc 3&4 page 447 |  |  | 1 |  | Pvsyst: 100MWp + 800kWp (403200 modules) |  |  | U
Chint | MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Degradation Curve from Manufacturer | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Chint | MAW | Modules | Modules | Standards (as applicable to crystalline silicion or thin-film) | 1.14.3 | IEC 61215 | 1 | doc 1&2 page 198, 209 | 1 |  |  |  |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? | no, just a statement of compliance
Chint | MAW | Modules | Modules | Standards (as applicable to crystalline silicion or thin-film) | 1.14.3 | IEC 61416 | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? | not existing | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Chint | MAW | Modules | Modules | Standards (as applicable to crystalline silicion or thin-film) | 1.14.3 | IEC 61646 | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? | no, just a statement of compliance | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Chint | MAW | Modules | Modules | Standards (as applicable to crystalline silicion or thin-film) | 1.14.3 | IEC 61730 | 1 |  | 1 |  |  |  |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? | no, just a statement of compliance
Chint | MAW | Modules | Modules | Standards (as applicable to crystalline silicion or thin-film) | 1.14.3 | IEC 60364-4-41 | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? | no, just a statement of compliance 'protection against electric shock | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Chint | MAW | Modules | Modules | Standards (as applicable to crystalline silicion or thin-film) | 1.14.3 | IEC 61701 | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? | no, just a statement of compliance | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Chint | MAW | Modules | Modules | Standards (as applicable to crystalline silicion or thin-film) | 1.14.3 | IEC 60904-1, IEC 60904-3 | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? | no, just a statement of compliance | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Chint | MAW | Modules | Modules | Pre-shipment quality assurance | 1.14.4 | Pre-shipment flash tested data Quality assurance for PV modules on-site and in laboratory simulator must meet the class AAA requirements of IEC 60904-9. The sun simulator must be calibrated with a reference cell, which itself was calibrated by a member of the WPVS scheme, with a maximum uncertainty of Isc of 1%. unique barcode (SNr) and labelled performance headlines (P(mpp), I(sc), U(oc), I(mpp), U(mpp) maximum current, maximum voltage Positive power sorting | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Cannot be evaluated at this stage. | compliance necessary | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Chint | MAW | Modules | Modules | Pre-shipment quality assurance | 1.14.4 | All modules must undergo Electroluminiscense (EL) inspection with a resolution of minimum 4 MPixel prior to shipment. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Cannot be evaluated at this stage. | compliance necessary | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Chint | MAW | Modules | Modules | Pre-shipment quality assurance | 1.14.4 | A sufficient EVA cross linking has to be verified per production line through a gel content test supervised by an accredited (IEC 17025 or national pendant) independent certified module testing agency. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Cannot be evaluated at this stage. | compliance necessary | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Chint | MAW | Modules | Modules | Quality assurance on site | 1.14.5 | The modules shall undergo an incoming inspection at arrival on construction site. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Cannot be evaluated at this stage. | stated and accepted | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Chint | MAW | Modules | Due Diligence | Quality Assurance | 1.14.6 | The bidder will bear the cost of the Quality assurance for PV modules on-site and in laboratory to be carried out by the Employer through an independent technical consultant up to 150,000 USD. | 1 |  |  |  | 1 |  |  |  |  | C | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria.
Chint | MAW | Modules | Modules | Pre-shipment quality assurance | 1.14.7 | Warranties and evidence shall be given by the bidder that their selected modules have been tested for susceptibility to Potential Induced Degradation (PID). | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Chint | MAW | Modules | Credentials | Project references | 1.14.8 | To show the proven technology a minimum of 500MW of proposed product type series must be in operation and reference projects shall be named. | 1 | Doc 1&2 page 417, doc 3&4 page 105 |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | approx. 450 MWp named | Related to project references |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Chint | MAW | DC Cables | DC Cables | Specific Requirements | 1.15.1 | Are Ohmic losses less than 1% at full power? | 1 |  |  |  | 1 |  | Pvsyst: DC losses at 0.9%, AC losses not considered? |  | DC+AC losses < 2% | U
Chint | MAW | DC Cables | DC Cables | Design factors to be provided | 1.15.2 | String cable shall be of the following type: single conductor type, copper, 1000 V / Class II (according to protection class II / 1000V, IEC 61140, single core cable, tinned copper conductor, XLPE Insulation, double EVA jacket (resistant to heat and cold, resistant to ozone, UV, oil and chemicals), Temperature: 90 º C (Temperature Max. Allowable: 120 º C), Halogen free | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | PV1-F 1*4 | It should be in accordance with the inverter values. | possibly 1500V for such system design | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Chint | MAW | DC Cables | DC Cables | Design factors to be provided | 1.15.2 | Connectors of Modules and string cables shall be connected of self-locking type, have IP65 rating and shall be from same manufacturer and type | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Chint | MAW | DC Cables | DC Cables | Design factors to be provided | 1.15.2 | The DC main (downstream of combiner box) wiring harness shall have the quality: Aluminum / Copper / 1000 V / Class II | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | It should be in accordance with the inverter values. | possibly 1500V for such system design | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Chint | MAW | DC Cables | DC Cables | Design factors to be provided | 1.15.2 | Balance of electrical potential | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Need to be disscussed | equipotential bonding earthing mesh | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Chint | MAW | DC Cables | DC Cables | Design factors to be provided | 1.15.2 | Installation to be verified by measurement-protocols | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Cannot be evaluated at this stage. | blanc protocol | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Chint | MAW | DC Cables | DC Cables | Design factors to be provided | 1.15.2 | Clear and systematic labelling required | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Chint | MAW | DC Cables | DC Cables | Design factors to be provided | 1.15.2 | Lifetime of 30 years is assured | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | What proof is required. | Life time test of nonmetal materials IEC 60811-408:2012 / (DIN EN 60811-408; VDE 0473-811-408:2012-12) 30 y assurance never seen until today | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Chint | MAW | DC Cables | DC Cables | Design factors to be provided | 1.15.2 | Sizing of cables shall be specified according to the number of modules and strings per array | 1 | doc 1&2 page 454 | 1 | [5 empty] | voltage drop calculation
Chint | MAW | DC Cables | DC Cables | Standards | 1.15.3 | IEC 60364-1 | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Chint | MAW | DC Connectors | DC Connectors | Standards | 1.16.2 | EN 50521 | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? | PV Connectors no, just a statement of compliance | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Chint | MAW | DC Connectors | DC Connectors | Standards | 1.16.2 | IEC 60512 | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? | Connectors E-Systems no, just a statement of compliance | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Chint | MAW | DC Junction Box | DC Junction Box | Design factors to be provided | 1.17.1 | At least IP54 | 1 | Doc 1&2 page 19 | 1 |  |  |  |  | DC Junction box is applicable in what conditions? | depending on DC Design
Chint | MAW | DC Junction Box | DC Junction Box | Design factors to be provided | 1.17.1 | DC fuses shall permit up to maximum 1000 V (or 1500V if designed). String box design, including all operating elements shall satisfy safety requirements | 1 | Doc 3&4 page 84 | 1 |  |  |  |  | Will inverter voltage(1500V) effect the maximum voltage(1000V)? | depends on spec of inverter.
Chint | MAW | DC Junction Box | DC Junction Box | Design factors to be provided | 1.17.1 | Monitored input-couples | 1 | Doc 1&2 page 19 | 1
Chint | MAW | DC Junction Box | DC Junction Box | Design factors to be provided | 1.17.1 | Class 2 DC surge arrestor | 1 | Doc 1&2 page 19 | 1
Chint | MAW | DC Junction Box | DC Junction Box | Design factors to be provided | 1.17.1 | Dust and heat protection | 1 | Doc 1&2 page 19 | 1
Chint | MAW | DC Junction Box | DC Junction Box | Specifications | 1.17.2 | Current monitoring | 1 | Doc 3&4 page 84 | 1
Chint | MAW | DC Junction Box | DC Junction Box | Specifications | 1.17.2 | Touch-safe protective cover | 1 | Doc 3&4 page 83 | 1 |  |  |  | transparent cover
Chint | MAW | DC Junction Box | DC Junction Box | Specifications | 1.17.2, 1.17.1 | Monitoring interface for SCADA | 1 | Doc 1&2 page 19 | 1
Chint | MAW | DC Junction Box | DC Junction Box | Standards | 1.17.3 | EN 61000-6 | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? | EMV no, just a statement of compliance | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Chint | MAW | DC Junction Box | DC Junction Box | Standards | 1.17.3 | EN 60439-1 | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? | arcing fault / Störlichtbogen Verhalten no, just a statement of compliance | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Chint | MAW | DC Junction Box | DC Junction Box | Standards | 1.17.3 | EN 50178 | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? | High currat devices no, just a statement of compliance | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Chint | MAW | Inverters | Warranty | Warranty option | 1.18.1 | The Bidder shall arrange a full-service package for the selected inverters for a product warranty period of 5 years, with an option to cover additional 20 years including provisions for any necessary replacements including O&M service plan guaranteeing 99% availability. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 5 years standard warranty; optional up to 20 years |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Chint | MAW | Inverters | Inverters | Strategic Reason for Inverter Selection | 1.18.2 | Balance of System (BOS) costs of inverter and labour | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  | financial bid | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Chint | MAW | Inverters | Inverters | Strategic Reason for Inverter Selection | 1.18.2 | Dust and heat protection | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  | derating? | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Chint | MAW | Inverters | Inverters | Strategic Reason for Inverter Selection | 1.18.2 | Timely and effective monitoring at a granular/zoomed-in level | 1 |  | 1
Chint | MAW | Inverters | Inverters | Strategic Reason for Inverter Selection | 1.18.2 | Available uptime | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Chint | MAW | Inverters | Inverters | Strategic Reason for Inverter Selection | 1.18.2 | Concept of protection against overload, short-circuit, grid-failure, internal failure, over-temperature (de-rating), surge protection | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Its too general, needs to be reviewed. | failure codes and consquences (automatic/manual restart, throw away safety devices) | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Chint | MAW | Inverters | O&M | Guarantees | 1.18.2 | For central inverters concept: the bidder shall ensure with an undertaking from the manufacturer that the concerned skilled staff will be made available at the site within 24 hours of reporting the defect to the manufacturer. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Chint | MAW | Inverters | Inverters | Functionalities | 1.18.3 | Maximum Power Point Tracking (MPPT) and string/sub-array management | 1 | Doc 3&4 page 53 | 1
Chint | MAW | Inverters | Inverters | Functionalities | 1.18.3 | Matching grid voltage and frequency at point-of-coupling | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Chint | MAW | Inverters | Inverters | Functionalities | 1.18.3 | Anti-islanding protection | 1 | doc 3&4 page 6 | 1
Chint | MAW | Inverters | Inverters | Functionalities | 1.18.3 | Voltage regulation through reactive power support: remotely set point control for voltage stability | 1 | Doc 3&4 page 53 | 1 |  |  |  | Reactive power adjustable and the power factor range from -0.8 to +0.8, Reactive power compensation at night | 8.2 needs to ensure these questions are answered in the bids.
Chint | MAW | Inverters | Inverters | Functionalities | 1.18.3 | Frequency regulation | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | 8.2 needs to ensure these questions are answered in the bids. |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Chint | MAW | Inverters | Inverters | Functionalities | 1.18.3 | Voltage and frequency fault ride-through: no disconnection of the connection through voltage dip and change of active power generation, feed-in of reactive power during the fault for voltage stabilisation | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | 8.2 needs to ensure these questions are answered in the bids. |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Chint | MAW | Inverters | Inverters | Functionalities | 1.18.3 | Limitation of voltage fluctuation due to switching operations and long-term flicker | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | 8.2 needs to ensure these questions are answered in the bids. |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Chint | MAW | Inverters | Inverters | Functionalities | 1.18.3 | Limitation of short-circuit current | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | 8.2 needs to ensure these questions are answered in the bids. |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Chint | MAW | Inverters | Inverters | Functionalities | 1.18.3 | Limitation of steady-stage voltage changes to 2% of the nominal value | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Chint | MAW | Inverters | Inverters | Functionalities | 1.18.3 | Limitation of current harmonics and higher frequency components up to 9 kHz | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Chint | MAW | Inverters | Inverters | Functionalities | 1.18.3 | Active power control reduction: remotely set point of control in case of network congestions or risk of system collapse, if deemed necessary | 1 | Doc 3&4 page 53 | 1 |  |  |  | Active power continuously adjustable | 8.2 needs to ensure these questions are answered in the bids.
Chint | MAW | Inverters | Monitoring | Functionalities | 1.18.3 | Advanced communication, with intelligent alerts/warnings, to the SCADA server | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Chint | MAW | Inverters | Inverters | Specific Requirements | 1.18.6 | Specifications of table in Schedule C shall be met | 1 |  | 1 |  |  |  |  | Link to table
Chint | MAW | Inverters | Inverters | Design factors to be provided | 1.18.7 | Input voltage range (The voltage window for MPP tracking shall accommodate the expected degradation of the modules.) | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Chint | MAW | Inverters | Inverters | Design factors to be provided | 1.18.7 | PV array configuration options: positive ground, negative ground | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Chint | MAW | Inverters | Inverters | Design factors to be provided | 1.18.7 | Integrated transformer/transformerless / Outside Dry Type Transformer | 1 | Doc 3&4 page 53 | 1 |  |  |  | transformerless
Chint | MAW | Inverters | Inverters | Design factors to be provided | 1.18.7 | Peak efficiency/ Weighted efficiency | 1 | Doc 3&4 page 53 | 1
Chint | MAW | Inverters | Inverters | Design factors to be provided | 1.18.7 | Nominal power | 1 | Doc 3&4 page 53 | 1
Chint | MAW | Inverters | Inverters | Design factors to be provided | 1.18.7 | Nominal output voltage | 1 | Doc 3&4 page 53 | 1
Chint | MAW | Inverters | Inverters | Design factors to be provided | 1.18.7 | Output voltage range | 1 | Doc 3&4 page 53 | 1
Chint | MAW | Inverters | Inverters | Design factors to be provided | 1.18.7 | Maximum output current | 1 | Doc 3&4 page 53 | 1
Chint | MAW | Inverters | Inverters | Design factors to be provided | 1.18.7 | Nominal output frequency, 3-phase | 1 | Doc 3&4 page 53 | 1
Chint | MAW | Inverters | Inverters | Design factors to be provided | 1.18.7 | Operating temperature range | 1 | Doc 3&4 page 53 | 1 |  |  |  |  | What is the acceptable range? | 60°C Derating?
Chint | MAW | Inverters | Inverters | Design factors to be provided | 1.18.7 | Cooling method | 1 | Doc 3&4 page 53 | 1 |  |  |  | Variable speed cooling fans
Chint | MAW | Inverters | Inverters | Design factors to be provided | 1.18.7 | Detection of insulation faults | 1 | Doc 3&4 page 53 |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Chint | MAW | Inverters | Inverters | Design factors to be provided | 1.18.7 | Protection rating: NEMA 3R, IP54/IP55/IP60 | 1 |  | 1 |  |  |  | IP20 indoor, installed in a station
Chint | MAW | Inverters | Inverters | Standards | 1.18.8 | IEEE 1547 | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? | no, just a statement of compliance Interconnecting Distributed Resources | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Chint | MAW | Inverters | Inverters | Standards | 1.18.8 | TUV, VDE, or equivalent certification of passing the relevant standards | 1 | Doc 3&4 page 4 | 1
Chint | MAW | Inverters | Inverters | Manufacturers confirmation | 1.18.9 | The Bidder shall deliver a manufacturer's confirmation in his Bid for the suitability of the inverter for the specific weather conditions applicable in Bahawalpur Pakistan. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Chint | MAW | Inverters | Credentials | Project references | 1.18.10 | A minimum of 100 MWp of similar product/type must be in operation and reference projects shall be named. | 1 | Doc 3&4 page 26 | 1
Chint | MAW | Inverters | Inverters | Quality Assurance | 1.18.11 | Check of protection against overload, short-circuit, grid-failure, internal failure, over-temperature (de-rating), surge protection, detection of insulation faults of AC Cables. Bidder shall firmly specify the manufacturer, types and length of cables to be installed | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | 8.2 needs to ensure these questions are answered in the bids. |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Chint | MAW | Inverters | Inverters | Quality Assurance | 1.18.11 | Test run in the field for maximum and EU-efficiency of all Inverters | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | 8.2 needs to ensure these questions are answered in the bids. |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Chint | MAW | Inverters | Inverters | Quality Assurance | 1.18.11 | Test run and check of MPP tracking of all inverters | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | 8.2 needs to ensure these questions are answered in the bids. |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Chint | MAW | Inverters | Inverters | Quality Assurance | 1.18.11 | The Bidder shall deliver detailed protocols of performance test run (warm power test) for every single inverter | 1 |  |  |  | 1 |  |  | Cannot be evaluated at this stage |  | C
Chint | MAW | Inverters | Inverters | Quality Assurance | 1.18.11 | After commissioning, 1 of 10 inverters will be measured on site (power curve and efficiency) by an approved independent technical consultant on behalf of the Employer. The on-site measurements shall be accepted by the Bidder as average values for all inverters | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Cannot be evaluated at this stage | compliance! | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Chint | MAW | Inverters | Due diligence | Quality Assurance | 1.18.12 | The Bidder accepts that the cost of the Quality assurance for Inverters to be carried by the Employer through an independent technical consultant shall be taken over by the successful bidder up to an amount of 100,000 USD. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Sumec | MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Bills of Materials, BoMs: (glass, encapsulant, backsheet, ribbon, adhesives, cable, junction box, connector) | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Sumec | MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Maximum rated power | 1 |  | 1
Sumec | MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Rated power tolerance | 1 |  | 1
Sumec | MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Minimum efficiency at 200 W/m² (25°, AM 1.5) | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Sumec | MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Materials and workmanship warranty of a minimum of 10 years | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Sumec | MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Power warranty/performance guarantee of a minimum of 25 years: the power output should not fall below 90% within 10 years, and below 80% within 25 years; linear warranty mandatory | 1 |  | 1
Sumec | MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Type of cells comprising the module, and number of cells in series | 1 | Vol I page 270 | 1 | [5 empty] | manufacturer
Sumec | MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Voltage at the maximum power point | 1 | Vol I page 270 | 1
Sumec | MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Current at the maximum current point | 1 | Vol I page 270 | 1
Sumec | MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Open-circuit voltage | 1 | Vol I page 270 | 1
Sumec | MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Short-circuit current | 1 | Vol I page 270 | 1
Sumec | MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Maximum system voltage | 1 | Vol I page 270 | 1 | [5 empty] | … at SK-II safety class
Sumec | MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Operating temperature range and nominal operating cell temperature NOCT | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | What range is acceptable | There is as small range anyway Will result in the PR losses | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Sumec | MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Tolerance to wind (maximum load) impact (mechanical load) | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  | minimum 2400 Pa | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Sumec | MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Manufacturers installation guidelines | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Sumec | MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Manufacturers confirmation for the suitability of module for specific weather conditions and the high UV-radiation | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  | especially reliability at high UV irridiance / Product warranty | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Sumec | MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Provide guarantees and data sheets (to be transferred to Employer upon COD) | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Sumec | MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Specify number of modules and total MWp to be provided | 1 |  | 1 |  |  |  | taken from Pvsyst Reports
Sumec | MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Degradation Curve from Manufacturer | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Sumec | MAW | Modules | Modules | Standards (as applicable to crystalline silicion or thin-film) | 1.14.3 | IEC 61215 | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? | no, just a statement of compliance | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Sumec | MAW | Modules | Modules | Standards (as applicable to crystalline silicion or thin-film) | 1.14.3 | IEC 61416 | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? | not existing | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Sumec | MAW | Modules | Modules | Standards (as applicable to crystalline silicion or thin-film) | 1.14.3 | IEC 61646 | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? | no, just a statement of compliance | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Sumec | MAW | Modules | Modules | Standards (as applicable to crystalline silicion or thin-film) | 1.14.3 | IEC 61730 | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? | no, just a statement of compliance | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Sumec | MAW | Modules | Modules | Standards (as applicable to crystalline silicion or thin-film) | 1.14.3 | IEC 60364-4-41 | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? | no, just a statement of compliance 'protection against electric shock | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Sumec | MAW | Modules | Modules | Standards (as applicable to crystalline silicion or thin-film) | 1.14.3 | IEC 61701 | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? | no, just a statement of compliance | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Sumec | MAW | Modules | Modules | Standards (as applicable to crystalline silicion or thin-film) | 1.14.3 | IEC 60904-1, IEC 60904-3 | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? | no, just a statement of compliance | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Sumec | MAW | Modules | Modules | Pre-shipment quality assurance | 1.14.4 | Pre-shipment flash tested data Quality assurance for PV modules on-site and in laboratory simulator must meet the class AAA requirements of IEC 60904-9. The sun simulator must be calibrated with a reference cell, which itself was calibrated by a member of the WPVS scheme, with a maximum uncertainty of Isc of 1%. unique barcode (SNr) and labelled performance headlines (P(mpp), I(sc), U(oc), I(mpp), U(mpp) maximum current, maximum voltage Positive power sorting | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Cannot be evaluated at this stage. | compliance necessary | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Sumec | MAW | Modules | Modules | Pre-shipment quality assurance | 1.14.4 | All modules must undergo Electroluminiscense (EL) inspection with a resolution of minimum 4 MPixel prior to shipment. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Cannot be evaluated at this stage. | compliance necessary | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Sumec | MAW | Modules | Modules | Pre-shipment quality assurance | 1.14.4 | A sufficient EVA cross linking has to be verified per production line through a gel content test supervised by an accredited (IEC 17025 or national pendant) independent certified module testing agency. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Cannot be evaluated at this stage. | compliance necessary | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Sumec | MAW | Modules | Modules | Quality assurance on site | 1.14.5 | The modules shall undergo an incoming inspection at arrival on construction site. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Cannot be evaluated at this stage. | stated and accepted | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Sumec | MAW | Modules | Due Diligence | Quality Assurance | 1.14.6 | The bidder will bear the cost of the Quality assurance for PV modules on-site and in laboratory to be carried out by the Employer through an independent technical consultant up to 150,000 USD. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Sumec | MAW | Modules | Modules | Pre-shipment quality assurance | 1.14.7 | Warranties and evidence shall be given by the bidder that their selected modules have been tested for susceptibility to Potential Induced Degradation (PID). | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Sumec | MAW | Modules | Credentials | Project references | 1.14.8 | To show the proven technology a minimum of 500MW of proposed product type series must be in operation and reference projects shall be named. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Related to project references |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Sumec | MAW | DC Cables | DC Cables | Specific Requirements | 1.15.1 | Are Ohmic losses less than 1% at full power? | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | DC: 1.4%, AC: no considered |  | DC+AC losses < 2% | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Sumec | MAW | DC Cables | DC Cables | Design factors to be provided | 1.15.2 | String cable shall be of the following type: single conductor type, copper, 1000 V / Class II (according to protection class II / 1000V, IEC 61140, single core cable, tinned copper conductor, XLPE Insulation, double EVA jacket (resistant to heat and cold, resistant to ozone, UV, oil and chemicals), Temperature: 90 º C (Temperature Max. Allowable: 120 º C), Halogen free | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | It should be in accordance with the inverter values. | possibly 1500V for such system design | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Sumec | MAW | DC Cables | DC Cables | Design factors to be provided | 1.15.2 | Connectors of Modules and string cables shall be connected of self-locking type, have IP65 rating and shall be from same manufacturer and type | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Sumec | MAW | DC Cables | DC Cables | Design factors to be provided | 1.15.2 | The DC main (downstream of combiner box) wiring harness shall have the quality: Aluminum / Copper / 1000 V / Class II | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | It should be in accordance with the inverter values. | possibly 1500V for such system design | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Sumec | MAW | DC Cables | DC Cables | Design factors to be provided | 1.15.2 | Balance of electrical potential | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Need to be disscussed | equipotential bonding earthing mesh | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Sumec | MAW | DC Cables | DC Cables | Design factors to be provided | 1.15.2 | Installation to be verified by measurement-protocols | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Cannot be evaluated at this stage. | blanc protocol | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Sumec | MAW | DC Cables | DC Cables | Design factors to be provided | 1.15.2 | Clear and systematic labelling required | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Sumec | MAW | DC Cables | DC Cables | Design factors to be provided | 1.15.2 | Lifetime of 30 years is assured | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | What proof is required. | Life time test of nonmetal materials IEC 60811-408:2012 / (DIN EN 60811-408; VDE 0473-811-408:2012-12) 30 y assurance never seen until today | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Sumec | MAW | DC Cables | DC Cables | Design factors to be provided | 1.15.2 | Sizing of cables shall be specified according to the number of modules and strings per array | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  | voltage drop calculation | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Sumec | MAW | DC Cables | DC Cables | Standards | 1.15.3 | IEC 60364-1 | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Sumec | MAW | DC Connectors | DC Connectors | Standards | 1.16.2 | EN 50521 | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? | PV Connectors no, just a statement of compliance | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Sumec | MAW | DC Connectors | DC Connectors | Standards | 1.16.2 | IEC 60512 | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? | Connectors E-Systems no, just a statement of compliance | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Sumec | MAW | DC Junction Box | DC Junction Box | Design factors to be provided | 1.17.1 | At least IP54 | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | DC Junction box is applicable in what conditions? | depending on DC Design | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Sumec | MAW | DC Junction Box | DC Junction Box | Design factors to be provided | 1.17.1 | DC fuses shall permit up to maximum 1000 V (or 1500V if designed). String box design, including all operating elements shall satisfy safety requirements | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Will inverter voltage(1500V) effect the maximum voltage(1000V)? | depends on spec of inverter. | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Sumec | MAW | DC Junction Box | DC Junction Box | Design factors to be provided | 1.17.1 | Monitored input-couples | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Sumec | MAW | DC Junction Box | DC Junction Box | Design factors to be provided | 1.17.1 | Class 2 DC surge arrestor | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Sumec | MAW | DC Junction Box | DC Junction Box | Design factors to be provided | 1.17.1 | Dust and heat protection | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Sumec | MAW | DC Junction Box | DC Junction Box | Specifications | 1.17.2 | Current monitoring | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Sumec | MAW | DC Junction Box | DC Junction Box | Specifications | 1.17.2 | Touch-safe protective cover | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Sumec | MAW | DC Junction Box | DC Junction Box | Specifications | 1.17.2, 1.17.1 | Monitoring interface for SCADA | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Sumec | MAW | DC Junction Box | DC Junction Box | Standards | 1.17.3 | EN 61000-6 | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? | EMV no, just a statement of compliance | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Sumec | MAW | DC Junction Box | DC Junction Box | Standards | 1.17.3 | EN 60439-1 | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? | arcing fault / Störlichtbogen Verhalten no, just a statement of compliance | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Sumec | MAW | DC Junction Box | DC Junction Box | Standards | 1.17.3 | EN 50178 | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? | High currat devices no, just a statement of compliance | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Sumec | MAW | Inverters | Warranty | Warranty option | 1.18.1 | The Bidder shall arrange a full-service package for the selected inverters for a product warranty period of 5 years, with an option to cover additional 20 years including provisions for any necessary replacements including O&M service plan guaranteeing 99% availability. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Sumec | MAW | Inverters | Inverters | Strategic Reason for Inverter Selection | 1.18.2 | Balance of System (BOS) costs of inverter and labour | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  | financial bid | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Sumec | MAW | Inverters | Inverters | Strategic Reason for Inverter Selection | 1.18.2 | Dust and heat protection | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  | derating? | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Sumec | MAW | Inverters | Inverters | Strategic Reason for Inverter Selection | 1.18.2 | Timely and effective monitoring at a granular/zoomed-in level | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Sumec | MAW | Inverters | Inverters | Strategic Reason for Inverter Selection | 1.18.2 | Available uptime | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Sumec | MAW | Inverters | Inverters | Strategic Reason for Inverter Selection | 1.18.2 | Concept of protection against overload, short-circuit, grid-failure, internal failure, over-temperature (de-rating), surge protection | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Its too general, needs to be reviewed. | failure codes and consquences (automatic/manual restart, throw away safety devices) | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Sumec | MAW | Inverters | O&M | Guarantees | 1.18.2 | For central inverters concept: the bidder shall ensure with an undertaking from the manufacturer that the concerned skilled staff will be made available at the site within 24 hours of reporting the defect to the manufacturer. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Sumec | MAW | Inverters | Inverters | Functionalities | 1.18.3 | Maximum Power Point Tracking (MPPT) and string/sub-array management | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Sumec | MAW | Inverters | Inverters | Functionalities | 1.18.3 | Matching grid voltage and frequency at point-of-coupling | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Sumec | MAW | Inverters | Inverters | Functionalities | 1.18.3 | Anti-islanding protection | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Sumec | MAW | Inverters | Inverters | Functionalities | 1.18.3 | Voltage regulation through reactive power support: remotely set point control for voltage stability | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | 8.2 needs to ensure these questions are answered in the bids. |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Sumec | MAW | Inverters | Inverters | Functionalities | 1.18.3 | Frequency regulation | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | 8.2 needs to ensure these questions are answered in the bids. |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Sumec | MAW | Inverters | Inverters | Functionalities | 1.18.3 | Voltage and frequency fault ride-through: no disconnection of the connection through voltage dip and change of active power generation, feed-in of reactive power during the fault for voltage stabilisation | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | 8.2 needs to ensure these questions are answered in the bids. |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Sumec | MAW | Inverters | Inverters | Functionalities | 1.18.3 | Limitation of voltage fluctuation due to switching operations and long-term flicker | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | 8.2 needs to ensure these questions are answered in the bids. |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Sumec | MAW | Inverters | Inverters | Functionalities | 1.18.3 | Limitation of short-circuit current | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | 8.2 needs to ensure these questions are answered in the bids. |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Sumec | MAW | Inverters | Inverters | Functionalities | 1.18.3 | Limitation of steady-stage voltage changes to 2% of the nominal value | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Sumec | MAW | Inverters | Inverters | Functionalities | 1.18.3 | Limitation of current harmonics and higher frequency components up to 9 kHz | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Sumec | MAW | Inverters | Inverters | Functionalities | 1.18.3 | Active power control reduction: remotely set point of control in case of network congestions or risk of system collapse, if deemed necessary | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | 8.2 needs to ensure these questions are answered in the bids. |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Sumec | MAW | Inverters | Monitoring | Functionalities | 1.18.3 | Advanced communication, with intelligent alerts/warnings, to the SCADA server | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Sumec | MAW | Inverters | Inverters | Specific Requirements | 1.18.6 | Specifications of table in Schedule C shall be met | 1 |  |  |  | 1 |  |  | Link to table |  | C
Sumec | MAW | Inverters | Inverters | Design factors to be provided | 1.18.7 | Input voltage range (The voltage window for MPP tracking shall accommodate the expected degradation of the modules.) | 1 | Vol I page 283 | 1
Sumec | MAW | Inverters | Inverters | Design factors to be provided | 1.18.7 | PV array configuration options: positive ground, negative ground | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Sumec | MAW | Inverters | Inverters | Design factors to be provided | 1.18.7 | Integrated transformer/transformerless / Outside Dry Type Transformer | 1 | Vol I page 283 | 1
Sumec | MAW | Inverters | Inverters | Design factors to be provided | 1.18.7 | Peak efficiency/ Weighted efficiency | 1 | Vol I page 283 | 1
Sumec | MAW | Inverters | Inverters | Design factors to be provided | 1.18.7 | Nominal power | 1 | Vol I page 283 | 1
Sumec | MAW | Inverters | Inverters | Design factors to be provided | 1.18.7 | Nominal output voltage | 1 | Vol I page 283 | 1
Sumec | MAW | Inverters | Inverters | Design factors to be provided | 1.18.7 | Output voltage range | 1 | Vol I page 283 | 1
Sumec | MAW | Inverters | Inverters | Design factors to be provided | 1.18.7 | Maximum output current | 1 | Vol I page 283 | 1
Sumec | MAW | Inverters | Inverters | Design factors to be provided | 1.18.7 | Nominal output frequency, 3-phase | 1 | Vol I page 283 | 1
Sumec | MAW | Inverters | Inverters | Design factors to be provided | 1.18.7 | Operating temperature range | 1 | Vol I page 283 | 1 |  |  |  |  | What is the acceptable range? | 60°C Derating?
Sumec | MAW | Inverters | Inverters | Design factors to be provided | 1.18.7 | Cooling method | 1 | Vol I page 283 | 1 |  |  |  | Adaptive forced-air cooling
Sumec | MAW | Inverters | Inverters | Design factors to be provided | 1.18.7 | Detection of insulation faults | 1 | Vol I page 283 | 1
Sumec | MAW | Inverters | Inverters | Design factors to be provided | 1.18.7 | Protection rating: NEMA 3R, IP54/IP55/IP60 | 1 | Vol I page 283 |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | Datenblatt IP-Wert 20 |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Sumec | MAW | Inverters | Inverters | Standards | 1.18.8 | IEEE 1547 | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? | no, just a statement of compliance Interconnecting Distributed Resources | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Sumec | MAW | Inverters | Inverters | Standards | 1.18.8 | TUV, VDE, or equivalent certification of passing the relevant standards | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Sumec | MAW | Inverters | Inverters | Manufacturers confirmation | 1.18.9 | The Bidder shall deliver a manufacturer's confirmation in his Bid for the suitability of the inverter for the specific weather conditions applicable in Bahawalpur Pakistan. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Sumec | MAW | Inverters | Credentials | Project references | 1.18.10 | A minimum of 100 MWp of similar product/type must be in operation and reference projects shall be named. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Sumec | MAW | Inverters | Inverters | Quality Assurance | 1.18.11 | Check of protection against overload, short-circuit, grid-failure, internal failure, over-temperature (de-rating), surge protection, detection of insulation faults of AC Cables. Bidder shall firmly specify the manufacturer, types and length of cables to be installed | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | 8.2 needs to ensure these questions are answered in the bids. |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Sumec | MAW | Inverters | Inverters | Quality Assurance | 1.18.11 | Test run in the field for maximum and EU-efficiency of all Inverters | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | 8.2 needs to ensure these questions are answered in the bids. |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Sumec | MAW | Inverters | Inverters | Quality Assurance | 1.18.11 | Test run and check of MPP tracking of all inverters | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | 8.2 needs to ensure these questions are answered in the bids. |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Sumec | MAW | Inverters | Inverters | Quality Assurance | 1.18.11 | The Bidder shall deliver detailed protocols of performance test run (warm power test) for every single inverter | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Cannot be evaluated at this stage |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Sumec | MAW | Inverters | Inverters | Quality Assurance | 1.18.11 | After commissioning, 1 of 10 inverters will be measured on site (power curve and efficiency) by an approved independent technical consultant on behalf of the Employer. The on-site measurements shall be accepted by the Bidder as average values for all inverters | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Cannot be evaluated at this stage | compliance! | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Sumec | MAW | Inverters | Due diligence | Quality Assurance | 1.18.12 | The Bidder accepts that the cost of the Quality assurance for Inverters to be carried by the Employer through an independent technical consultant shall be taken over by the successful bidder up to an amount of 100,000 USD. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Zte | GD | Scope of the Bid | General items | Specific Requirements | 1.1.2 | The Offer shall include a list of all vendors and/or sub-contractors for major equipment. | 1 |  |  |  | 1 |  |  |  |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  | 1 |  | Open
Zte | GD | Scope of the Bid | General items | Quality Assurance | 1.1.3 | Defect components consequences: If one tested sample fails in one criterion, all items of the same category will be regarded as failed and rejected. | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  | Only to be checked in list of deviations. | yes, we need to be sure that they comply as for most of the critera | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | 1 | 1 | Open
Zte | GD | Scope of the Bid | General items | Guarantees | 1.1.5 | Energy Purchase Agreement (EPA) practices are followed | 1 |  |  |  | 1 | Important reasons: due to current uncertainty of the criteria we accept an open status. Please clarify that yo acknowledge the criteria and comply unless a reason of high importance will not allow you you to comply. In such a situation the parties will seek to agree a compromise. |  | This cannot be evaluated at this stage. | we need a sentence that it should and can only be disregarded for important reasons | Unclear: We do not understand your proposal, please detail your proposal. Especially confirm that you are compliant with our requested criteria. |  | 1 |  | Open
Zte | GD | Scope of the Bid | Layout | Guarantees | 1.1.6 | The bidder confirms that the system complies with all applicable requirements of the NEPRA Grid Code of Pakistan and its Draft Amendment no. 2 for Solar Power Projects. | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  | Only to be checked in list of deviations. |  | Important reasons: due to current uncertainty of the criteria we accept an open status. Please clarify that yo acknowledge the criteria and comply unless a reason of high importance will not allow you you to comply. In such a situation the parties will seek to agree a compromise. |  | 1 |  | Open
Zte | GD | Scope of the Bid | Credentials | EPC | 1.1.9 | The bid includes professional experience of the Bidders in ground mounted utility-scale PV and financial information about their long-term stability | 3 |  | 1 | [8 empty] | 1 |  | Pass
Zte | GD | Scope of the Bid | General items | Specific Requirements | 1.1.9 | The bid covers the planning of the System design, the required functionality of the System in terms of its sub-systems and components, detailed feature-wise descriptions of the components to be used in the System, the planning of the System installation, its integration, testing, monitoring, commissioning and O&M of the System | 1 |  |  |  | 1 | We can not find all of the requested criteria in your documents. Please confirm that your bid is compliant with all expectations and requirements of Section 6 of the RFP and provide a list with ALL exeptions or alterations. This applies to both, the EOPC And the O&M part. |  | This question should be removed as detailed design of every component/sub-system will be checked and evaluated thoroughly in technical evaluation | no, its an overall critera an need to be met |  |  | 1 | 1 | Open
Zte | GD | Scope of the Bid | Credentials | EPC | 1.1.10 | The Bidder, or the Lead company in case of JV is a EPC contractor | 1 |  | 1 |  |  |  |  | This is a non-technical question. We suggest such question should be separated from technical questions and placed in checklist for "General/Substantive Responsiveness of Bid" | a question of reliability and experience of solid understanding of the task/System Technology. See also 1.1.10 |  |  | 1 |  | Pass
Zte | GD | Conditions for Disqualification and Additional Information Required | Credentials | EPC | 1.2.6 | Detailed list of all the sites with the affirmation that the bidder played the leading EPC role in the turnkey installation of these systems. | 3 |  | 1 | [8 empty] | 1 |  | Pass
Zte | GD | Conditions for Disqualification and Additional Information Required | Credentials | EPC | 1.2.6 | Cumulative MWp of ground mounted PV turnkey installations >5 MWp with stating of actual MWp per project, project location, date of commissioning, module type and Inverter type. | 1 |  | 1 | [5 empty] | experience of Bidder / EPC |  |  | 1 | 1 | Pass
Zte | GD | Conditions for Disqualification and Additional Information Required | Credentials | EPC | 1.2.6 | References and contact data (mail and phone) from owners of all installations > 5 MW with quotes of the corresponding system Performance Ratios, as well as system performance vs. initial yield assessment per year since the installation. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  | for selection of referenz objects |  |  | 1 | 1 | Open
Zte | GD | Conditions for Disqualification and Additional Information Required | Credentials | EPC | 1.2.6 | Approval from bidder to owners or owner representatives to answer questions freely regarding the past performance of the bidder and performance of the system against contractual obligations. | 2 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | [5 empty] | 1 |  | Open
Zte | GD | Conditions for Disqualification and Additional Information Required | Credentials | O&M | 1.2.6 | Cumulative MWp of ground mounted PV installations for which O&M services have been delivered by the bidder or his O&M subcontractor. | 2 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | [5 empty] | 1 |  | Open
Zte | GD | Conditions for Disqualification and Additional Information Required | Credentials | O&M | 1.2.6 | References, contact data and approval from owners or owner representatives of all installations > 5 MW from bidder or his O&M subcontractor to answer questions freely regarding the past performance of the bidder and performance of the system against contractual obligations. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | [5 empty] | 1 | 1 | Open
Zte | GD | Technical Bid Evaluation Criteria | Credentials | Guarantees | 1.3.1 | To have met the contractual requirements of the EPC and O&M deliverables including certificate to the effect that the entire equipment is brand new as required vide notification number NEPRA/UTS-01/777-779 dated Jan 21 ,2014, | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Only to be checked in list of deviations. |  |  |  | 1 | 1 | Open
Zte | GD | Technical Bid Evaluation Criteria | Credentials | EPC | 1.3.1 | the systems have been completed on time and within budget, | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | [5 empty] | 1 | 1 | Open
Zte | GD | Technical Bid Evaluation Criteria | Credentials | O&M | 1.3.1 | that they have started supplying electricity to the grid and are still operating satisfactorily in 9 out of 10 MW for all the cases | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | [5 empty] | 1 | 1 | Open
Zte | GD | Technical Bid Evaluation Criteria | Credentials | O&M | 1.3.1 | In case of a non-performance, comprehensible evidence has to be given why this case will not affect this project. | 3 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | [5 empty] | 1 |  | Open
Zte | GD | Technical Bid Evaluation Criteria | Credentials | O&M | 1.3.2 | Prove at least 100 MW of EPC experience and 50 MW of full O&M experience for a period longer than 24 months. | 1 |  | 1 | [8 empty] | 1 |  | Pass
Zte | GD | Technical Bid Evaluation Criteria | Due Diligence | Quality Assurance | 1.3.5 | The cost of the due diligence to be carried out by the Employer through an independent technical consultant before contract signature will be taken over by the successful bidder up to an amount of 50,000 USD independent of the result. The due diligence will cover a module factory visit, an inverter factory inspection and a due diligence on the provided financial, EPC and O&M credentials including up to three site visits. | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  | Only to be checked in list of deviations. |  |  |  | 1 |  | Open
Zte | GD | PR and System Performance Guarantee | System PR | Guarantees | 1.4.1 | A 25 years commitment, in the form of a whole System performance guarantee, is required. The performance guarantee is based on measuring the PR with the actual kWh-AC delivery per year adjusted for the actual POA irradiation for the same period | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  | Only to be checked in list of deviations. |  |  |  | 1 | 1 | Open
Zte | GD | PR and System Performance Guarantee | System PR | System PR | 1.4.1 | The billing system/metering system will be installed at interconnection point of 132 kV bus bar of HV substation to be installed by the EPC Contractor and the 132 kV Transmission line of NTDC existing at site. | 2 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  | Only to be checked in list of deviations. |  |  |  | 1 |  | Open
Zte | GD | PR and System Performance Guarantee | System PR | System PR | 1.4.2 | Guaranteed PR values in the form of the Table in 1.4.1 for the acceptance phase and annual output of the PV system shall be specified. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Link to table in Documents sheet |  |  |  | 1 | 1 | Open
Zte | GD | PR and System Performance Guarantee | System PR | System PR | 1.4.4 | The initial PR will be first measured after the time of commissioning of the completed PV System during the acceptance phase of 30 days. | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  | Cannot be evaluated at this stage. Only to be checked in list of deviations. |  |  |  | 1 | 1 | Open
Zte | GD | PR and System Performance Guarantee | Compensations | System PR | 1.4.4 | The successful Bidder shall conduct the initial PR test for the daylight hours of at least 30 consecutive days, recording data at a frequency of fifteen minute intervals or less, to validate the guaranteed PR value for acceptance. Any excused downtime (e.g., from Grid Operator ordered shutdowns, grid failure, theft, force majeure) will be excluded from that calculation by an independent consultant (Auditing Body). That day will be taken out and another day added, if the initial PR falls short of the guaranteed PR value, the successful Bidder shall be obliged to identify and rectify the causes for the performance shortfall at their own cost. | 2 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  | Cannot be evaluated at this stage. Only to be checked in list of deviations. |  |  |  | 1 |  | Open
Zte | GD | PR and System Performance Guarantee | Compensations | System PR | 1.4.4 | If the measured PR within further 30 days does not reach the guaranteed PR, the Employer can demand that the price of the system will be reduced by the percentage of shortfall times 1.2 for liquidated damages or the contractor will have to install more power at its own cost or combination of both. | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  | Cannot be evaluated at this stage. Only to be checked in list of deviations. |  |  |  | 1 | 1 | Open
Zte | GD | PR and System Performance Guarantee | Compensations | O&M | 1.4.5 | If the annual measured PR falls below the guaranteed PR value according to Table 1.4.1, the liquidated damages will be levied on the successful Bidder at the rate of USD 0.20-per-kWh or the kWh Value the Employer receives for each kWh of shortfall – whichever is higher. Adjustments shall be made for any events outside the control of the O&M operator as grid outages, from grid operator ordered shutdowns, or force majeure events during the year. | 2 |  |  |  | 1 |  |  | Cannot be evaluated at this stage. Only to be checked in list of deviations. | Only to be checked in list of deviations. |  |  | 1 |  | Open
Zte | GD | PR and System Performance Guarantee | Compensations | O&M | 1.4.5 | In case the PR is higher than the guaranteed PR value, the net value of this excess energy will be shared as follows: 50% towards the asset replacement fund, 25% towards the Employer, 25% towards the O&M contractor | 3 |  |  |  | 1 |  |  | Cannot be evaluated at this stage. Only to be checked in list of deviations. |  |  |  | 1 |  | Open
Zte | GD | PR and System Performance Guarantee | Compensations | O&M | 1.4.5 | For timely compensation the PR Calculation will be carried out provisionally for each quarter whereby the contractor and employer might jointly agree on different PR values for each quarter. In the last quarter of each calendar year the annual PR compensation of the full year will be carried out and any provisions will be offset by the annual compensation. | 3 |  |  |  | 1 |  |  | Cannot be evaluated at this stage. Only to be checked in list of deviations. |  |  |  | 1 |  | Open
Zte | GD | PR and System Performance Guarantee | Compensations | O&M | 1.4.6 | If the successful Bidder defaults in being able to provide the O&M services required for the Systems performance guarantee, then it will be liable to cover all costs – but at least in the amount of Liquidated Damages imposed to the Employer by its PPA agreements - incurred by the Employer, including the loss of the guaranteed electricity export to the grid (but at a minimum rate of USD 0.20-per-kWh) for the disrupted period, in finding and hiring a replacement for the purpose. | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  | Cannot be evaluated at this stage. Only to be checked in list of deviations. |  |  |  | 1 | 1 | Open

## JBU (hidden)
Bidder | Expert | Chapter in RfP | Topic | Subtopic | Clause | Criteria | 1 Vital 2 Valuable 3 Not Important | Link to Bidders Documents | Pass =1 | Fail =1 | Open =1 | Question to bidder for clarification | Comments | Comments QA on Criteria | Comment on "Comments" | Typical Questions to be send to bidders if Open status |  | Sub-category
Tbea | JBU | AC Cabling | AC Cabling | Design factors to be provided | 1.19.1 | AC cable shall be of Copper. Rated voltage, nominal voltage between phase and neutral and nominal voltage between phases to be specified by the Bidder | 1 |  |  |  | 1 | General understanding: expressions like "shall", "shall be supplied with", "has to be", "must be" have the meaning of "will be delivered"? Please confirm. |  |  |  | G | General understanding: expressions like "shall", "shall be supplied with", "has to be", "must be" have the meaning of "will be delivered"? Please confirm.
Tbea | JBU | AC Cabling | AC Cabling | Design factors to be provided | 1.19.1 | Appropriate sizing to minimise voltage drop and losses | 1 |  |  |  | 1 | General understanding: expressions like "shall", "shall be supplied with", "has to be", "must be" have the meaning of "will be delivered"? Please confirm. |  | What is the appropriate size? | leeway to allow MPP tracking when module voltage drops. At least 10%. Ralf, ist Vital kriterium. | G | General understanding: expressions like "shall", "shall be supplied with", "has to be", "must be" have the meaning of "will be delivered"? Please confirm.
Tbea | JBU | AC Cabling | AC Cabling | Design factors to be provided | 1.19.1 | Lifetime longer than 25 years | 1 |  |  |  | 1 | General understanding: expressions like "shall", "shall be supplied with", "has to be", "must be" have the meaning of "will be delivered"? Please confirm. |  |  |  | G | General understanding: expressions like "shall", "shall be supplied with", "has to be", "must be" have the meaning of "will be delivered"? Please confirm.
Tbea | JBU | AC Cabling | AC Cabling | Design factors to be provided | 1.19.1 | Rated voltage | 1 |  |  |  | 1 | General understanding: expressions like "shall", "shall be supplied with", "has to be", "must be" have the meaning of "will be delivered"? Please confirm. |  |  |  | G | General understanding: expressions like "shall", "shall be supplied with", "has to be", "must be" have the meaning of "will be delivered"? Please confirm.
Tbea | JBU | AC Cabling | AC Cabling | Design factors to be provided | 1.19.1 | Bending radius | 1 |  |  |  | 1 | General understanding: expressions like "shall", "shall be supplied with", "has to be", "must be" have the meaning of "will be delivered"? Please confirm. |  |  |  | G | General understanding: expressions like "shall", "shall be supplied with", "has to be", "must be" have the meaning of "will be delivered"? Please confirm.
Tbea | JBU | AC Cabling | AC Cabling | Design factors to be provided | 1.19.1 | Cables shall be suitable for the environmental conditions at the project site, including UV protection (The Bidder shall provide certification from manufacturer) | 1 |  |  |  | 1 | General understanding: expressions like "shall", "shall be supplied with", "has to be", "must be" have the meaning of "will be delivered"? Please confirm. |  |  |  | G | General understanding: expressions like "shall", "shall be supplied with", "has to be", "must be" have the meaning of "will be delivered"? Please confirm.
Tbea | JBU | AC Cabling | AC Cabling | Design factors to be provided | 1.19.1 | Installation to be verified by measurement-protocols | 1 |  |  |  | 1 | General understanding: expressions like "shall", "shall be supplied with", "has to be", "must be" have the meaning of "will be delivered"? Please confirm. |  |  |  | G | General understanding: expressions like "shall", "shall be supplied with", "has to be", "must be" have the meaning of "will be delivered"? Please confirm.
Tbea | JBU | AC Cabling | AC Cabling | Design factors to be provided | 1.19.1 | Cable installation shall ensure grounding and short-circuit protection | 1 |  | 1
Tbea | JBU | AC Cabling | AC Cabling | Design factors to be provided | 1.19.1 | Sufficient and effective cable protection against attacks of rodents for any cabling underground or above is required | 1 |  |  |  | 1 | General understanding: expressions like "shall", "shall be supplied with", "has to be", "must be" have the meaning of "will be delivered"? Please confirm. |  |  |  | G | General understanding: expressions like "shall", "shall be supplied with", "has to be", "must be" have the meaning of "will be delivered"? Please confirm.
Tbea | JBU | AC Cabling | AC Cabling | Standards | 1.19.2 | IEC 60502 | 1 |  |  |  | 1 | General understanding: expressions like "shall", "shall be supplied with", "has to be", "must be" have the meaning of "will be delivered"? Please confirm. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  | G | General understanding: expressions like "shall", "shall be supplied with", "has to be", "must be" have the meaning of "will be delivered"? Please confirm.
Tbea | JBU | AC Cabling | AC Cabling | Standards | 1.19.2 | IEC 60364 | 1 |  |  |  | 1 | General understanding: expressions like "shall", "shall be supplied with", "has to be", "must be" have the meaning of "will be delivered"? Please confirm. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  | G | General understanding: expressions like "shall", "shall be supplied with", "has to be", "must be" have the meaning of "will be delivered"? Please confirm.
Tbea | JBU | AC Cabling | AC Cabling | Standards | 1.19.2 | DIN-VDE-0276 | 1 |  |  |  | 1 | General understanding: expressions like "shall", "shall be supplied with", "has to be", "must be" have the meaning of "will be delivered"? Please confirm. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  | G | General understanding: expressions like "shall", "shall be supplied with", "has to be", "must be" have the meaning of "will be delivered"? Please confirm.
Tbea | JBU | AC Cabling | AC Cabling | Standards | 1.19.2 | EN 60332-1-1 and EN 60332-2-1 | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Tbea | JBU | AC Cabling | AC Cabling | Specific Requirements | 1.19.3 | The runs of both the main DC and AC cables, in the System layout, should be adjusted to keep power losses below <1% at STC (Design calculations through cable loss simulation to be provided for review & comment). | 1 |  | 1 |  |  |  |  | Part of system design | Kategorie ?
Tbea | JBU | AC Combiner Box | AC Combiner Box | Design factors to be provided | 1.20.1 | Rated voltage | 1 |  | 1 |  |  |  | not applicable
Tbea | JBU | AC Combiner Box | AC Combiner Box | Design factors to be provided | 1.20.1 | Rated current | 1 |  | 1 |  |  |  | not applicable
Tbea | JBU | AC Combiner Box | AC Combiner Box | Design factors to be provided | 1.20.1 | Class 2 AC surge arrestor | 1 |  | 1 |  |  |  | not applicable
Tbea | JBU | AC Combiner Box | AC Combiner Box | Design factors to be provided | 1.20.1 | Load breaker switch of adequate size | 1 |  | 1 |  |  |  | not applicable
Tbea | JBU | AC Combiner Box | AC Combiner Box | Design factors to be provided | 1.20.1 | Flame test | 1 |  | 1 |  |  |  | not applicable
Tbea | JBU | AC Combiner Box | AC Combiner Box | Design factors to be provided | 1.20.1 | Waterproof test | 1 |  | 1 |  |  |  | not applicable
Tbea | JBU | AC Combiner Box | AC Combiner Box | Design factors to be provided | 1.20.1 | Operating temperature range | 1 |  | 1 |  |  |  | not applicable
Tbea | JBU | AC Combiner Box | AC Combiner Box | Design factors to be provided | 1.20.1 | Stripping length of the individual wire | 1 |  | 1 |  |  |  | not applicable
Tbea | JBU | AC Combiner Box | AC Combiner Box | Standards | 1.20.2 | IP 67 | 1 |  | 1 |  |  |  | not applicable
Tbea | JBU | AC Combiner Box | AC Combiner Box | Standards | 1.20.2 | EN 60529, DIN-VDE-0472 | 1 |  | 1 |  |  |  | not applicable | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient?
Tbea | JBU | Step-up Transformers/MV Switchgear | Step-up Transformers/MV Switchgear | Guarantees | 1.21.1 | Compatibility with NTDC grid connection code must be ensured | 1 |  |  |  | 1 | General understanding: expressions like "shall", "shall be supplied with", "has to be", "must be" have the meaning of "will be delivered"? Please confirm. |  |  |  | G | General understanding: expressions like "shall", "shall be supplied with", "has to be", "must be" have the meaning of "will be delivered"? Please confirm.
Tbea | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Design factors to be provided | 1.21.2 | 3-phase, double wound, continuously rated, oil-cooled, enclosed transformers, use of low loss core steel and close coupled copper windings | 1 | page 902 |  | 1 | 1 | Unclear: We do not understand your proposal, please detail your proposal. Especially confirm that you are compliant with our requested criteria. | dry type transformer according to datasheet |  |  | U | Unclear: We do not understand your proposal, please detail your proposal. Especially confirm that you are compliant with our requested criteria.
Tbea | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Design factors to be provided | 1.21.2 | Incoming terminals | 1 |  | 1
Tbea | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Design factors to be provided | 1.21.2 | Outgoing terminals | 1 |  | 1
Tbea | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Design factors to be provided | 1.21.2 | kVA rating | 1 |  | 1
Tbea | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Design factors to be provided | 1.21.2 | Primary side voltage | 1 |  | 1
Tbea | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Design factors to be provided | 1.21.2 | Secondary side voltage | 1 |  | 1
Tbea | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Design factors to be provided | 1.21.2 | Insulation type | 1 |  |  | 1 | 1 | Unclear: We do not understand your proposal, please detail your proposal. Especially confirm that you are compliant with our requested criteria. | dry type transformer according to datasheet |  |  | U | Unclear: We do not understand your proposal, please detail your proposal. Especially confirm that you are compliant with our requested criteria.
Tbea | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Design factors to be provided | 1.21.2 | Short-circuit impedance | 1 |  | 1
Tbea | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Design factors to be provided | 1.21.2 | No-load losses | 1 |  | 1
Tbea | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Design factors to be provided | 1.21.2 | Efficiency | 1 |  | 1
Tbea | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Design factors to be provided | 1.21.2 | Operating temperature range | 1 | page 902 |  |  | 1 | Unclear: We do not understand your proposal, please detail your proposal. Especially confirm that you are compliant with our requested criteria. | -35°C up to +45°C |  |  | U | Unclear: We do not understand your proposal, please detail your proposal. Especially confirm that you are compliant with our requested criteria.
Tbea | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Design factors to be provided | 1.21.2 | Maximum ambient temperature and altitude | 1 |  | 1
Tbea | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Design factors to be provided | 1.21.2 | Humidity tolerance | 1 |  | 1
Tbea | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Design factors to be provided | 1.21.2 | Cooling method | 1 | page 902 |  | 1 | 1 | Unclear: We do not understand your proposal, please detail your proposal. Especially confirm that you are compliant with our requested criteria. | dry type transformer according to datasheet |  |  | U | Unclear: We do not understand your proposal, please detail your proposal. Especially confirm that you are compliant with our requested criteria.
Tbea | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Design factors to be provided | 1.21.2 | Protection system | 1 |  | 1
Tbea | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Design factors to be provided | 1.21.2 | Operational data shall be logged in central operating system (e.g. oil temperature, oil level, pressure, Temperature probes (one per phase): Alarm and trip of cell etc.) | 1 |  | 1
Tbea | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Standards | 1.21.3 | IEC 62446 | 1 |  | 1 |  |  |  |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient?
Tbea | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Standards | 1.21.3 | IEC 60076 | 1 |  | 1 |  |  |  |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient?
Tbea | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Standards | 1.21.3 | IEC 60085 | 1 |  | 1 |  |  |  |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient?
Tbea | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Standards | 1.21.3 | IEC 60214 | 1 |  | 1 |  |  |  |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient?
Tbea | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Standards | 1.21.3 | IEC 60137 | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  | C | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria.
Tbea | JBU | Step-up Transformers/MV Switchgear | Due Diligence | Quality Assurance | 1.21.3 | Factory witness testing will be required for MV transformer and switchgear to be installed at this project. The cost of the due diligence to be carried by the Employer through an independent technical consultant will be taken over by the successful bidder up to an amount of 30,000 USD. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Tbea | JBU | Step-up Transformers/MV Switchgear | MV Switchgear | Specific Requirements | 1.21.4 | MV Switchgears shall be SF6 gas insulated or VCB (Vacuum circuit breaker). | 1 |  | 1
Tbea | JBU | Step-up Transformers/MV Switchgear | MV Switchgear | Specific Requirements | 1.21.4 | The separating equipment shall be installed with visible disconnection (pivotable disconnectors). | 1 |  | 1 |  |  |  |  | Cannot be evaluated at this stage
Tbea | JBU | Step-up Transformers/MV Switchgear | MV Switchgear | Specific Requirements | 1.21.4 | Interlocks will also be mechanically interlocked between line MV switchgears. | 1 |  | 1
Tbea | JBU | Step-up Transformers/MV Switchgear | MV Switchgear | Design factors to be provided | 1.21.4 | System nominal voltage | 1 |  | 1
Tbea | JBU | Step-up Transformers/MV Switchgear | MV Switchgear | Design factors to be provided | 1.21.4 | System maximum voltage | 1 |  | 1
Tbea | JBU | Step-up Transformers/MV Switchgear | MV Switchgear | Design factors to be provided | 1.21.4 | Rated lightning impulse voltage | 1 |  | 1
Tbea | JBU | Step-up Transformers/MV Switchgear | MV Switchgear | Design factors to be provided | 1.21.4 | Rated power frequency withstand voltage | 1 |  | 1
Tbea | JBU | Step-up Transformers/MV Switchgear | MV Switchgear | Design factors to be provided | 1.21.4 | Rated short circuit current | 1 |  | 1
Tbea | JBU | Step-up Transformers/MV Switchgear | MV Switchgear | Standards | 1.21.5 | IEC 62446 | 1 |  | 1 |  |  |  |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient?
Tbea | JBU | Step-up Transformers/MV Switchgear | MV Switchgear | Standards | 1.21.5 | IEC 62271-200 | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  | C | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria.
Tbea | JBU | Step-up Transformers/MV Switchgear | MV Switchgear | Standards | 1.21.5 | IEC 60529 | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  | C | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria.
Tbea | JBU | Inverter/Transformer Station | Inverter/Transformer Station | Specific Requirements | 1.22 | Bidder shall firmly specify the number of stations, manufacturer, capacity and type of equipment. | 1 |  | 1
Tbea | JBU | Inverter/Transformer Station | Inverter/Transformer Station | Specific Requirements | 1.22 | All stations shall be equipped with fire and smoke detectors and alarm, connected to security and surveillance system | 1 |  |  |  | 1 | General understanding: expressions like "shall", "shall be supplied with", "has to be", "must be" have the meaning of "will be delivered"? Please confirm. |  |  |  | G | General understanding: expressions like "shall", "shall be supplied with", "has to be", "must be" have the meaning of "will be delivered"? Please confirm.
Tbea | JBU | Inverter/Transformer Station | Inverter/Transformer Station | Specific Requirements | 1.22 | Fine sand filters shall be installed | 1 |  |  |  | 1 | General understanding: expressions like "shall", "shall be supplied with", "has to be", "must be" have the meaning of "will be delivered"? Please confirm. |  |  |  | G | General understanding: expressions like "shall", "shall be supplied with", "has to be", "must be" have the meaning of "will be delivered"? Please confirm.
Tbea | JBU | Inverter/Transformer Station | Inverter/Transformer Station | Specific Requirements | 1.22 | The station shall enable the grounding of hardware and neutral will be left ground isolated | 1 |  |  |  | 1 | General understanding: expressions like "shall", "shall be supplied with", "has to be", "must be" have the meaning of "will be delivered"? Please confirm. |  |  |  | G | General understanding: expressions like "shall", "shall be supplied with", "has to be", "must be" have the meaning of "will be delivered"? Please confirm.
Tbea | JBU | Inverter/Transformer Station | Inverter/Transformer Station | Specific Requirements | 1.22 | Every ten (10) or lesser number of stations shall be equipped with an earthing and short-circuiting equipment | 1 |  |  |  | 1 | General understanding: expressions like "shall", "shall be supplied with", "has to be", "must be" have the meaning of "will be delivered"? Please confirm. |  |  |  | G | General understanding: expressions like "shall", "shall be supplied with", "has to be", "must be" have the meaning of "will be delivered"? Please confirm.
Zte | JBU | AC Cabling | AC Cabling | Design factors to be provided | 1.19.1 | AC cable shall be of Copper. Rated voltage, nominal voltage between phase and neutral and nominal voltage between phases to be specified by the Bidder | 1 | Technical Proposal of 100MW Solar Power Plant, page 85 |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | material is copper |  |  | C | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria.
Zte | JBU | AC Cabling | AC Cabling | Design factors to be provided | 1.19.1 | Appropriate sizing to minimise voltage drop and losses | 1 | Technical Proposal of 100MW Solar Power Plant, page 114 | 1 |  |  |  | AC ohmic loss 0,1% | What is the appropriate size? | leeway to allow MPP tracking when module voltage drops. At least 10%. Ralf, ist Vital kriterium.
Zte | JBU | AC Cabling | AC Cabling | Design factors to be provided | 1.19.1 | Lifetime longer than 25 years | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | no datasheet |  |  | C | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria.
Zte | JBU | AC Cabling | AC Cabling | Design factors to be provided | 1.19.1 | Rated voltage | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | no datasheet |  |  | C | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria.
Zte | JBU | AC Cabling | AC Cabling | Design factors to be provided | 1.19.1 | Bending radius | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | no datasheet |  |  | C | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria.
Zte | JBU | AC Cabling | AC Cabling | Design factors to be provided | 1.19.1 | Cables shall be suitable for the environmental conditions at the project site, including UV protection (The Bidder shall provide certification from manufacturer) | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | no datasheet |  |  | C | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria.
Zte | JBU | AC Cabling | AC Cabling | Design factors to be provided | 1.19.1 | Installation to be verified by measurement-protocols | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | no datasheet |  |  | C | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria.
Zte | JBU | AC Cabling | AC Cabling | Design factors to be provided | 1.19.1 | Cable installation shall ensure grounding and short-circuit protection | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | no datasheet |  |  | C | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria.
Zte | JBU | AC Cabling | AC Cabling | Design factors to be provided | 1.19.1 | Sufficient and effective cable protection against attacks of rodents for any cabling underground or above is required | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | no datasheet |  |  | C | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria.
Zte | JBU | AC Cabling | AC Cabling | Standards | 1.19.2 | IEC 60502 | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | no datasheet | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  | C | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria.
Zte | JBU | AC Cabling | AC Cabling | Standards | 1.19.2 | IEC 60364 | 1 |  | 1 |  |  |  | no datasheet | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient?
Zte | JBU | AC Cabling | AC Cabling | Standards | 1.19.2 | DIN-VDE-0276 | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | no datasheet | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  | C | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria.
Zte | JBU | AC Cabling | AC Cabling | Standards | 1.19.2 | EN 60332-1-1 and EN 60332-2-1 | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | no datasheet | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  | C | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria.
Zte | JBU | AC Cabling | AC Cabling | Specific Requirements | 1.19.3 | The runs of both the main DC and AC cables, in the System layout, should be adjusted to keep power losses below <1% at STC (Design calculations through cable loss simulation to be provided for review & comment). | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  | Part of system design | Kategorie ? | C | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria.
Zte | JBU | AC Combiner Box | AC Combiner Box | Design factors to be provided | 1.20.1 | Rated voltage | 1 |  | 1 |  |  |  | not applicable
Zte | JBU | AC Combiner Box | AC Combiner Box | Design factors to be provided | 1.20.1 | Rated current | 1 |  | 1 |  |  |  | not applicable
Zte | JBU | AC Combiner Box | AC Combiner Box | Design factors to be provided | 1.20.1 | Class 2 AC surge arrestor | 1 |  | 1 |  |  |  | not applicable
Zte | JBU | AC Combiner Box | AC Combiner Box | Design factors to be provided | 1.20.1 | Load breaker switch of adequate size | 1 |  | 1 |  |  |  | not applicable
Zte | JBU | AC Combiner Box | AC Combiner Box | Design factors to be provided | 1.20.1 | Flame test | 1 |  | 1 |  |  |  | not applicable
Zte | JBU | AC Combiner Box | AC Combiner Box | Design factors to be provided | 1.20.1 | Waterproof test | 1 |  | 1 |  |  |  | not applicable
Zte | JBU | AC Combiner Box | AC Combiner Box | Design factors to be provided | 1.20.1 | Operating temperature range | 1 |  | 1 |  |  |  | not applicable
Zte | JBU | AC Combiner Box | AC Combiner Box | Design factors to be provided | 1.20.1 | Stripping length of the individual wire | 1 |  | 1 |  |  |  | not applicable
Zte | JBU | AC Combiner Box | AC Combiner Box | Standards | 1.20.2 | IP 67 | 1 |  | 1 |  |  |  | not applicable
Zte | JBU | AC Combiner Box | AC Combiner Box | Standards | 1.20.2 | EN 60529, DIN-VDE-0472 | 1 |  | 1 |  |  |  | not applicable | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient?
Zte | JBU | Step-up Transformers/MV Switchgear | Step-up Transformers/MV Switchgear | Guarantees | 1.21.1 | Compatibility with NTDC grid connection code must be ensured | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  |  |  | C | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria.
Zte | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Design factors to be provided | 1.21.2 | 3-phase, double wound, continuously rated, oil-cooled, enclosed transformers, use of low loss core steel and close coupled copper windings | 1 | Technical Proposal of 100MW Solar Power Plant, page 64 |  | 1 | 1 | Unclear: We do not understand your proposal, please detail your proposal. Especially confirm that you are compliant with our requested criteria. | dry type transformer will be used |  |  | U | Unclear: We do not understand your proposal, please detail your proposal. Especially confirm that you are compliant with our requested criteria.
Zte | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Design factors to be provided | 1.21.2 | Incoming terminals | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  |  |  | C | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria.
Zte | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Design factors to be provided | 1.21.2 | Outgoing terminals | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  |  |  | C | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria.
Zte | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Design factors to be provided | 1.21.2 | kVA rating | 1 |  | 1
Zte | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Design factors to be provided | 1.21.2 | Primary side voltage | 1 |  | 1
Zte | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Design factors to be provided | 1.21.2 | Secondary side voltage | 1 |  | 1
Zte | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Design factors to be provided | 1.21.2 | Insulation type | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | no datasheet |  |  | C | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria.
Zte | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Design factors to be provided | 1.21.2 | Short-circuit impedance | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | no datasheet |  |  | C | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria.
Zte | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Design factors to be provided | 1.21.2 | No-load losses | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | no datasheet |  |  | C | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria.
Zte | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Design factors to be provided | 1.21.2 | Efficiency | 1 | Technical Proposal of 100MW Solar Power Plant, page 115 |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | no datasheet, combined AC and transformer loss is 1% according to Pvsyst simulation |  |  | C | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria.
Zte | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Design factors to be provided | 1.21.2 | Operating temperature range | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | no datasheet |  |  | C | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria.
Zte | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Design factors to be provided | 1.21.2 | Maximum ambient temperature and altitude | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | no datasheet |  |  | C | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria.
Zte | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Design factors to be provided | 1.21.2 | Humidity tolerance | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | no datasheet |  |  | C | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria.
Zte | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Design factors to be provided | 1.21.2 | Cooling method | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | no datasheet |  |  | C | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria.
Zte | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Design factors to be provided | 1.21.2 | Protection system | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | no datasheet |  |  | C | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria.
Zte | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Design factors to be provided | 1.21.2 | Operational data shall be logged in central operating system (e.g. oil temperature, oil level, pressure, Temperature probes (one per phase): Alarm and trip of cell etc.) | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | no datasheet |  |  | C | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria.
Zte | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Standards | 1.21.3 | IEC 62446 | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | no datasheet | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  | C | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria.
Zte | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Standards | 1.21.3 | IEC 60076 | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | no datasheet | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  | C | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria.
Zte | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Standards | 1.21.3 | IEC 60085 | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | no datasheet | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  | C | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria.
Zte | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Standards | 1.21.3 | IEC 60214 | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | no datasheet | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  | C | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria.
Zte | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Standards | 1.21.3 | IEC 60137 | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | no datasheet | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  | C | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria.
Zte | JBU | Step-up Transformers/MV Switchgear | Due Diligence | Quality Assurance | 1.21.3 | Factory witness testing will be required for MV transformer and switchgear to be installed at this project. The cost of the due diligence to be carried by the Employer through an independent technical consultant will be taken over by the successful bidder up to an amount of 30,000 USD. | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  |  |  | C | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria.
Zte | JBU | Step-up Transformers/MV Switchgear | MV Switchgear | Specific Requirements | 1.21.4 | MV Switchgears shall be SF6 gas insulated or VCB (Vacuum circuit breaker). | 1 |  | 1
Zte | JBU | Step-up Transformers/MV Switchgear | MV Switchgear | Specific Requirements | 1.21.4 | The separating equipment shall be installed with visible disconnection (pivotable disconnectors). | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  | Cannot be evaluated at this stage |  | C | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria.
Zte | JBU | Step-up Transformers/MV Switchgear | MV Switchgear | Specific Requirements | 1.21.4 | Interlocks will also be mechanically interlocked between line MV switchgears. | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  |  |  | C | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria.
Zte | JBU | Step-up Transformers/MV Switchgear | MV Switchgear | Design factors to be provided | 1.21.4 | System nominal voltage | 1 |  | 1
Zte | JBU | Step-up Transformers/MV Switchgear | MV Switchgear | Design factors to be provided | 1.21.4 | System maximum voltage | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  |  |  | C | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria.
Zte | JBU | Step-up Transformers/MV Switchgear | MV Switchgear | Design factors to be provided | 1.21.4 | Rated lightning impulse voltage | 1 |  | 1
Zte | JBU | Step-up Transformers/MV Switchgear | MV Switchgear | Design factors to be provided | 1.21.4 | Rated power frequency withstand voltage | 1 |  | 1
Zte | JBU | Step-up Transformers/MV Switchgear | MV Switchgear | Design factors to be provided | 1.21.4 | Rated short circuit current | 1 |  | 1
Zte | JBU | Step-up Transformers/MV Switchgear | MV Switchgear | Standards | 1.21.5 | IEC 62446 | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  | C | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria.
Zte | JBU | Step-up Transformers/MV Switchgear | MV Switchgear | Standards | 1.21.5 | IEC 62271-200 | 1 |  | 1 |  |  |  |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient?
Zte | JBU | Step-up Transformers/MV Switchgear | MV Switchgear | Standards | 1.21.5 | IEC 60529 | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  | C | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria.
Zte | JBU | Inverter/Transformer Station | Inverter/Transformer Station | Specific Requirements | 1.22 | Bidder shall firmly specify the number of stations, manufacturer, capacity and type of equipment. | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | no datasheet |  |  | C | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria.
Zte | JBU | Inverter/Transformer Station | Inverter/Transformer Station | Specific Requirements | 1.22 | All stations shall be equipped with fire and smoke detectors and alarm, connected to security and surveillance system | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | no datasheet |  |  | C | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria.
Zte | JBU | Inverter/Transformer Station | Inverter/Transformer Station | Specific Requirements | 1.22 | Fine sand filters shall be installed | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | no datasheet |  |  | C | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria.
Zte | JBU | Inverter/Transformer Station | Inverter/Transformer Station | Specific Requirements | 1.22 | The station shall enable the grounding of hardware and neutral will be left ground isolated | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | no datasheet |  |  | C | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria.
Zte | JBU | Inverter/Transformer Station | Inverter/Transformer Station | Specific Requirements | 1.22 | Every ten (10) or lesser number of stations shall be equipped with an earthing and short-circuiting equipment | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | no datasheet |  |  | C | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria.
Juwi | JBU | AC Cabling | AC Cabling | Design factors to be provided | 1.19.1 | AC cable shall be of Copper. Rated voltage, nominal voltage between phase and neutral and nominal voltage between phases to be specified by the Bidder | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Juwi | JBU | AC Cabling | AC Cabling | Design factors to be provided | 1.19.1 | Appropriate sizing to minimise voltage drop and losses | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | What is the appropriate size? | leeway to allow MPP tracking when module voltage drops. At least 10%. Ralf, ist Vital kriterium. | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Juwi | JBU | AC Cabling | AC Cabling | Design factors to be provided | 1.19.1 | Lifetime longer than 25 years | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Juwi | JBU | AC Cabling | AC Cabling | Design factors to be provided | 1.19.1 | Rated voltage | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Juwi | JBU | AC Cabling | AC Cabling | Design factors to be provided | 1.19.1 | Bending radius | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Juwi | JBU | AC Cabling | AC Cabling | Design factors to be provided | 1.19.1 | Cables shall be suitable for the environmental conditions at the project site, including UV protection (The Bidder shall provide certification from manufacturer) | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Juwi | JBU | AC Cabling | AC Cabling | Design factors to be provided | 1.19.1 | Installation to be verified by measurement-protocols | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Juwi | JBU | AC Cabling | AC Cabling | Design factors to be provided | 1.19.1 | Cable installation shall ensure grounding and short-circuit protection | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Juwi | JBU | AC Cabling | AC Cabling | Design factors to be provided | 1.19.1 | Sufficient and effective cable protection against attacks of rodents for any cabling underground or above is required | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Juwi | JBU | AC Cabling | AC Cabling | Standards | 1.19.2 | IEC 60502 | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Juwi | JBU | AC Cabling | AC Cabling | Standards | 1.19.2 | IEC 60364 | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Juwi | JBU | AC Cabling | AC Cabling | Standards | 1.19.2 | DIN-VDE-0276 | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Juwi | JBU | AC Cabling | AC Cabling | Standards | 1.19.2 | EN 60332-1-1 and EN 60332-2-1 | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Juwi | JBU | AC Cabling | AC Cabling | Specific Requirements | 1.19.3 | The runs of both the main DC and AC cables, in the System layout, should be adjusted to keep power losses below <1% at STC (Design calculations through cable loss simulation to be provided for review & comment). | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Part of system design | Kategorie ? | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Juwi | JBU | AC Combiner Box | AC Combiner Box | Design factors to be provided | 1.20.1 | Rated voltage | 1 |  | 1 |  |  |  | not applicable
Juwi | JBU | AC Combiner Box | AC Combiner Box | Design factors to be provided | 1.20.1 | Rated current | 1 |  | 1 |  |  |  | not applicable
Juwi | JBU | AC Combiner Box | AC Combiner Box | Design factors to be provided | 1.20.1 | Class 2 AC surge arrestor | 1 |  | 1 |  |  |  | not applicable
Juwi | JBU | AC Combiner Box | AC Combiner Box | Design factors to be provided | 1.20.1 | Load breaker switch of adequate size | 1 |  | 1 |  |  |  | not applicable
Juwi | JBU | AC Combiner Box | AC Combiner Box | Design factors to be provided | 1.20.1 | Flame test | 1 |  | 1 |  |  |  | not applicable
Juwi | JBU | AC Combiner Box | AC Combiner Box | Design factors to be provided | 1.20.1 | Waterproof test | 1 |  | 1 |  |  |  | not applicable
Juwi | JBU | AC Combiner Box | AC Combiner Box | Design factors to be provided | 1.20.1 | Operating temperature range | 1 |  | 1 |  |  |  | not applicable
Juwi | JBU | AC Combiner Box | AC Combiner Box | Design factors to be provided | 1.20.1 | Stripping length of the individual wire | 1 |  | 1 |  |  |  | not applicable
Juwi | JBU | AC Combiner Box | AC Combiner Box | Standards | 1.20.2 | IP 67 | 1 |  | 1 |  |  |  | not applicable
Juwi | JBU | AC Combiner Box | AC Combiner Box | Standards | 1.20.2 | EN 60529, DIN-VDE-0472 | 1 |  | 1 |  |  |  | not applicable | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient?
Juwi | JBU | Step-up Transformers/MV Switchgear | Step-up Transformers/MV Switchgear | Guarantees | 1.21.1 | Compatibility with NTDC grid connection code must be ensured | 1 |  |  |  | 1 |  | L
Juwi | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Design factors to be provided | 1.21.2 | 3-phase, double wound, continuously rated, oil-cooled, enclosed transformers, use of low loss core steel and close coupled copper windings | 1 |  | 1
Juwi | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Design factors to be provided | 1.21.2 | Incoming terminals | 1 |  | 1
Juwi | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Design factors to be provided | 1.21.2 | Outgoing terminals | 1 |  | 1
Juwi | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Design factors to be provided | 1.21.2 | kVA rating | 1 |  | 1
Juwi | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Design factors to be provided | 1.21.2 | Primary side voltage | 1 |  | 1
Juwi | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Design factors to be provided | 1.21.2 | Secondary side voltage | 1 |  | 1
Juwi | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Design factors to be provided | 1.21.2 | Insulation type | 1 |  | 1
Juwi | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Design factors to be provided | 1.21.2 | Short-circuit impedance | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Juwi | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Design factors to be provided | 1.21.2 | No-load losses | 1 |  | 1
Juwi | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Design factors to be provided | 1.21.2 | Efficiency | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | only total eff. Inv+transformer, page 287 |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Juwi | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Design factors to be provided | 1.21.2 | Operating temperature range | 1 |  | 1
Juwi | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Design factors to be provided | 1.21.2 | Maximum ambient temperature and altitude | 1 |  | 1
Juwi | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Design factors to be provided | 1.21.2 | Humidity tolerance | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Juwi | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Design factors to be provided | 1.21.2 | Cooling method | 1 |  | 1
Juwi | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Design factors to be provided | 1.21.2 | Protection system | 1 |  | 1
Juwi | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Design factors to be provided | 1.21.2 | Operational data shall be logged in central operating system (e.g. oil temperature, oil level, pressure, Temperature probes (one per phase): Alarm and trip of cell etc.) | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  |  |  | C | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria.
Juwi | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Standards | 1.21.3 | IEC 62446 | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Juwi | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Standards | 1.21.3 | IEC 60076 | 1 |  | 1 |  |  |  |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient?
Juwi | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Standards | 1.21.3 | IEC 60085 | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  | C | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria.
Juwi | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Standards | 1.21.3 | IEC 60214 | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  | C | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria.
Juwi | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Standards | 1.21.3 | IEC 60137 | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  | C | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria.
Juwi | JBU | Step-up Transformers/MV Switchgear | Due Diligence | Quality Assurance | 1.21.3 | Factory witness testing will be required for MV transformer and switchgear to be installed at this project. The cost of the due diligence to be carried by the Employer through an independent technical consultant will be taken over by the successful bidder up to an amount of 30,000 USD. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Juwi | JBU | Step-up Transformers/MV Switchgear | MV Switchgear | Specific Requirements | 1.21.4 | MV Switchgears shall be SF6 gas insulated or VCB (Vacuum circuit breaker). | 1 |  | 1
Juwi | JBU | Step-up Transformers/MV Switchgear | MV Switchgear | Specific Requirements | 1.21.4 | The separating equipment shall be installed with visible disconnection (pivotable disconnectors). | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  | Cannot be evaluated at this stage |  | C | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria.
Juwi | JBU | Step-up Transformers/MV Switchgear | MV Switchgear | Specific Requirements | 1.21.4 | Interlocks will also be mechanically interlocked between line MV switchgears. | 1 |  | 1
Juwi | JBU | Step-up Transformers/MV Switchgear | MV Switchgear | Design factors to be provided | 1.21.4 | System nominal voltage | 1 |  | 1
Juwi | JBU | Step-up Transformers/MV Switchgear | MV Switchgear | Design factors to be provided | 1.21.4 | System maximum voltage | 1 |  | 1
Juwi | JBU | Step-up Transformers/MV Switchgear | MV Switchgear | Design factors to be provided | 1.21.4 | Rated lightning impulse voltage | 1 |  | 1
Juwi | JBU | Step-up Transformers/MV Switchgear | MV Switchgear | Design factors to be provided | 1.21.4 | Rated power frequency withstand voltage | 1 |  | 1
Juwi | JBU | Step-up Transformers/MV Switchgear | MV Switchgear | Design factors to be provided | 1.21.4 | Rated short circuit current | 1 |  | 1
Juwi | JBU | Step-up Transformers/MV Switchgear | MV Switchgear | Standards | 1.21.5 | IEC 62446 | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Juwi | JBU | Step-up Transformers/MV Switchgear | MV Switchgear | Standards | 1.21.5 | IEC 62271-200 | 1 |  | 1 |  |  |  |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient?
Juwi | JBU | Step-up Transformers/MV Switchgear | MV Switchgear | Standards | 1.21.5 | IEC 60529 | 1 |  | 1 |  |  |  |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient?
Juwi | JBU | Inverter/Transformer Station | Inverter/Transformer Station | Specific Requirements | 1.22 | Bidder shall firmly specify the number of stations, manufacturer, capacity and type of equipment. | 1 |  | 1
Juwi | JBU | Inverter/Transformer Station | Inverter/Transformer Station | Specific Requirements | 1.22 | All stations shall be equipped with fire and smoke detectors and alarm, connected to security and surveillance system | 1 |  |  |  | 1 | Unclear: We do not understand your proposal, please detail your proposal. Especially confirm that you are compliant with our requested criteria. |  |  |  | U | Unclear: We do not understand your proposal, please detail your proposal. Especially confirm that you are compliant with our requested criteria.
Juwi | JBU | Inverter/Transformer Station | Inverter/Transformer Station | Specific Requirements | 1.22 | Fine sand filters shall be installed | 1 |  |  |  | 1 | Unclear: We do not understand your proposal, please detail your proposal. Especially confirm that you are compliant with our requested criteria. |  |  |  | U | Unclear: We do not understand your proposal, please detail your proposal. Especially confirm that you are compliant with our requested criteria.
Juwi | JBU | Inverter/Transformer Station | Inverter/Transformer Station | Specific Requirements | 1.22 | The station shall enable the grounding of hardware and neutral will be left ground isolated | 1 |  |  |  | 1 | Unclear: We do not understand your proposal, please detail your proposal. Especially confirm that you are compliant with our requested criteria. |  |  |  | U | Unclear: We do not understand your proposal, please detail your proposal. Especially confirm that you are compliant with our requested criteria.
Juwi | JBU | Inverter/Transformer Station | Inverter/Transformer Station | Specific Requirements | 1.22 | Every ten (10) or lesser number of stations shall be equipped with an earthing and short-circuiting equipment | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  |  |  | C | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria.
Chint | JBU | AC Cabling | AC Cabling | Design factors to be provided | 1.19.1 | AC cable shall be of Copper. Rated voltage, nominal voltage between phase and neutral and nominal voltage between phases to be specified by the Bidder | 1 |  | 1
Chint | JBU | AC Cabling | AC Cabling | Design factors to be provided | 1.19.1 | Appropriate sizing to minimise voltage drop and losses | 1 |  | 1 |  |  |  |  | What is the appropriate size? | leeway to allow MPP tracking when module voltage drops. At least 10%. Ralf, ist Vital kriterium.
Chint | JBU | AC Cabling | AC Cabling | Design factors to be provided | 1.19.1 | Lifetime longer than 25 years | 1 |  | 1
Chint | JBU | AC Cabling | AC Cabling | Design factors to be provided | 1.19.1 | Rated voltage | 1 |  | 1
Chint | JBU | AC Cabling | AC Cabling | Design factors to be provided | 1.19.1 | Bending radius | 1 |  | 1
Chint | JBU | AC Cabling | AC Cabling | Design factors to be provided | 1.19.1 | Cables shall be suitable for the environmental conditions at the project site, including UV protection (The Bidder shall provide certification from manufacturer) | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Chint | JBU | AC Cabling | AC Cabling | Design factors to be provided | 1.19.1 | Installation to be verified by measurement-protocols | 1 |  | 1
Chint | JBU | AC Cabling | AC Cabling | Design factors to be provided | 1.19.1 | Cable installation shall ensure grounding and short-circuit protection | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Chint | JBU | AC Cabling | AC Cabling | Design factors to be provided | 1.19.1 | Sufficient and effective cable protection against attacks of rodents for any cabling underground or above is required | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Chint | JBU | AC Cabling | AC Cabling | Standards | 1.19.2 | IEC 60502 | 1 |  | 1 |  |  |  |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient?
Chint | JBU | AC Cabling | AC Cabling | Standards | 1.19.2 | IEC 60364 | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Chint | JBU | AC Cabling | AC Cabling | Standards | 1.19.2 | DIN-VDE-0276 | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Chint | JBU | AC Cabling | AC Cabling | Standards | 1.19.2 | EN 60332-1-1 and EN 60332-2-1 | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Chint | JBU | AC Cabling | AC Cabling | Specific Requirements | 1.19.3 | The runs of both the main DC and AC cables, in the System layout, should be adjusted to keep power losses below <1% at STC (Design calculations through cable loss simulation to be provided for review & comment). | 1 |  | 1 |  |  |  |  | Part of system design | Kategorie ?
Chint | JBU | AC Combiner Box | AC Combiner Box | Design factors to be provided | 1.20.1 | Rated voltage | 1 |  | 1 |  |  |  | not applicable
Chint | JBU | AC Combiner Box | AC Combiner Box | Design factors to be provided | 1.20.1 | Rated current | 1 |  | 1 |  |  |  | not applicable
Chint | JBU | AC Combiner Box | AC Combiner Box | Design factors to be provided | 1.20.1 | Class 2 AC surge arrestor | 1 |  | 1 |  |  |  | not applicable
Chint | JBU | AC Combiner Box | AC Combiner Box | Design factors to be provided | 1.20.1 | Load breaker switch of adequate size | 1 |  | 1 |  |  |  | not applicable
Chint | JBU | AC Combiner Box | AC Combiner Box | Design factors to be provided | 1.20.1 | Flame test | 1 |  | 1 |  |  |  | not applicable
Chint | JBU | AC Combiner Box | AC Combiner Box | Design factors to be provided | 1.20.1 | Waterproof test | 1 |  | 1 |  |  |  | not applicable
Chint | JBU | AC Combiner Box | AC Combiner Box | Design factors to be provided | 1.20.1 | Operating temperature range | 1 |  | 1 |  |  |  | not applicable
Chint | JBU | AC Combiner Box | AC Combiner Box | Design factors to be provided | 1.20.1 | Stripping length of the individual wire | 1 |  | 1 |  |  |  | not applicable
Chint | JBU | AC Combiner Box | AC Combiner Box | Standards | 1.20.2 | IP 67 | 1 |  | 1 |  |  |  | not applicable
Chint | JBU | AC Combiner Box | AC Combiner Box | Standards | 1.20.2 | EN 60529, DIN-VDE-0472 | 1 |  | 1 |  |  |  | not applicable | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient?
Chint | JBU | Step-up Transformers/MV Switchgear | Step-up Transformers/MV Switchgear | Guarantees | 1.21.1 | Compatibility with NTDC grid connection code must be ensured | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Chint | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Design factors to be provided | 1.21.2 | 3-phase, double wound, continuously rated, oil-cooled, enclosed transformers, use of low loss core steel and close coupled copper windings | 1 |  | 1
Chint | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Design factors to be provided | 1.21.2 | Incoming terminals | 1 |  | 1
Chint | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Design factors to be provided | 1.21.2 | Outgoing terminals | 1 |  | 1
Chint | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Design factors to be provided | 1.21.2 | kVA rating | 1 |  | 1
Chint | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Design factors to be provided | 1.21.2 | Primary side voltage | 1 |  | 1
Chint | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Design factors to be provided | 1.21.2 | Secondary side voltage | 1 |  | 1
Chint | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Design factors to be provided | 1.21.2 | Insulation type | 1 |  | 1
Chint | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Design factors to be provided | 1.21.2 | Short-circuit impedance | 1 |  | 1
Chint | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Design factors to be provided | 1.21.2 | No-load losses | 1 |  | 1
Chint | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Design factors to be provided | 1.21.2 | Efficiency | 1 |  | 1
Chint | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Design factors to be provided | 1.21.2 | Operating temperature range | 1 |  | 1
Chint | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Design factors to be provided | 1.21.2 | Maximum ambient temperature and altitude | 1 |  | 1
Chint | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Design factors to be provided | 1.21.2 | Humidity tolerance | 1 |  | 1
Chint | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Design factors to be provided | 1.21.2 | Cooling method | 1 |  | 1
Chint | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Design factors to be provided | 1.21.2 | Protection system | 1 |  | 1
Chint | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Design factors to be provided | 1.21.2 | Operational data shall be logged in central operating system (e.g. oil temperature, oil level, pressure, Temperature probes (one per phase): Alarm and trip of cell etc.) | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  |  |  | C | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria.
Chint | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Standards | 1.21.3 | IEC 62446 | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  | C | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria.
Chint | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Standards | 1.21.3 | IEC 60076 | 1 |  | 1 |  |  |  |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient?
Chint | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Standards | 1.21.3 | IEC 60085 | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Chint | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Standards | 1.21.3 | IEC 60214 | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Chint | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Standards | 1.21.3 | IEC 60137 | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Chint | JBU | Step-up Transformers/MV Switchgear | Due Diligence | Quality Assurance | 1.21.3 | Factory witness testing will be required for MV transformer and switchgear to be installed at this project. The cost of the due diligence to be carried by the Employer through an independent technical consultant will be taken over by the successful bidder up to an amount of 30,000 USD. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Chint | JBU | Step-up Transformers/MV Switchgear | MV Switchgear | Specific Requirements | 1.21.4 | MV Switchgears shall be SF6 gas insulated or VCB (Vacuum circuit breaker). | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Chint | JBU | Step-up Transformers/MV Switchgear | MV Switchgear | Specific Requirements | 1.21.4 | The separating equipment shall be installed with visible disconnection (pivotable disconnectors). | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Cannot be evaluated at this stage |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Chint | JBU | Step-up Transformers/MV Switchgear | MV Switchgear | Specific Requirements | 1.21.4 | Interlocks will also be mechanically interlocked between line MV switchgears. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Chint | JBU | Step-up Transformers/MV Switchgear | MV Switchgear | Design factors to be provided | 1.21.4 | System nominal voltage | 1 |  | 1
Chint | JBU | Step-up Transformers/MV Switchgear | MV Switchgear | Design factors to be provided | 1.21.4 | System maximum voltage | 1 |  | 1
Chint | JBU | Step-up Transformers/MV Switchgear | MV Switchgear | Design factors to be provided | 1.21.4 | Rated lightning impulse voltage | 1 |  | 1
Chint | JBU | Step-up Transformers/MV Switchgear | MV Switchgear | Design factors to be provided | 1.21.4 | Rated power frequency withstand voltage | 1 |  | 1
Chint | JBU | Step-up Transformers/MV Switchgear | MV Switchgear | Design factors to be provided | 1.21.4 | Rated short circuit current | 1 |  | 1
Chint | JBU | Step-up Transformers/MV Switchgear | MV Switchgear | Standards | 1.21.5 | IEC 62446 | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Chint | JBU | Step-up Transformers/MV Switchgear | MV Switchgear | Standards | 1.21.5 | IEC 62271-200 | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Chint | JBU | Step-up Transformers/MV Switchgear | MV Switchgear | Standards | 1.21.5 | IEC 60529 | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Chint | JBU | Inverter/Transformer Station | Inverter/Transformer Station | Specific Requirements | 1.22 | Bidder shall firmly specify the number of stations, manufacturer, capacity and type of equipment. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Chint | JBU | Inverter/Transformer Station | Inverter/Transformer Station | Specific Requirements | 1.22 | All stations shall be equipped with fire and smoke detectors and alarm, connected to security and surveillance system | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Chint | JBU | Inverter/Transformer Station | Inverter/Transformer Station | Specific Requirements | 1.22 | Fine sand filters shall be installed | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Chint | JBU | Inverter/Transformer Station | Inverter/Transformer Station | Specific Requirements | 1.22 | The station shall enable the grounding of hardware and neutral will be left ground isolated | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Chint | JBU | Inverter/Transformer Station | Inverter/Transformer Station | Specific Requirements | 1.22 | Every ten (10) or lesser number of stations shall be equipped with an earthing and short-circuiting equipment | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Sumec | JBU | AC Cabling | AC Cabling | Design factors to be provided | 1.19.1 | AC cable shall be of Copper. Rated voltage, nominal voltage between phase and neutral and nominal voltage between phases to be specified by the Bidder | 1 |  | 1
Sumec | JBU | AC Cabling | AC Cabling | Design factors to be provided | 1.19.1 | Appropriate sizing to minimise voltage drop and losses | 1 |  | 1 |  |  |  |  | What is the appropriate size? | leeway to allow MPP tracking when module voltage drops. At least 10%. Ralf, ist Vital kriterium.
Sumec | JBU | AC Cabling | AC Cabling | Design factors to be provided | 1.19.1 | Lifetime longer than 25 years | 1 |  |  |  | 1 |  | L
Sumec | JBU | AC Cabling | AC Cabling | Design factors to be provided | 1.19.1 | Rated voltage | 1 |  |  |  | 1 |  | L
Sumec | JBU | AC Cabling | AC Cabling | Design factors to be provided | 1.19.1 | Bending radius | 1 |  |  |  | 1 |  | L
Sumec | JBU | AC Cabling | AC Cabling | Design factors to be provided | 1.19.1 | Cables shall be suitable for the environmental conditions at the project site, including UV protection (The Bidder shall provide certification from manufacturer) | 1 |  |  |  | 1 |  | L
Sumec | JBU | AC Cabling | AC Cabling | Design factors to be provided | 1.19.1 | Installation to be verified by measurement-protocols | 1 |  |  |  | 1 |  | L
Sumec | JBU | AC Cabling | AC Cabling | Design factors to be provided | 1.19.1 | Cable installation shall ensure grounding and short-circuit protection | 1 |  |  |  | 1 |  | L
Sumec | JBU | AC Cabling | AC Cabling | Design factors to be provided | 1.19.1 | Sufficient and effective cable protection against attacks of rodents for any cabling underground or above is required | 1 |  |  |  | 1 |  | L
Sumec | JBU | AC Cabling | AC Cabling | Standards | 1.19.2 | IEC 60502 | 1 |  |  |  | 1 |  | L | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient?
Sumec | JBU | AC Cabling | AC Cabling | Standards | 1.19.2 | IEC 60364 | 1 |  |  |  | 1 |  | L | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient?
Sumec | JBU | AC Cabling | AC Cabling | Standards | 1.19.2 | DIN-VDE-0276 | 1 |  |  |  | 1 |  | L | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient?
Sumec | JBU | AC Cabling | AC Cabling | Standards | 1.19.2 | EN 60332-1-1 and EN 60332-2-1 | 1 |  |  |  | 1 |  | L | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient?
Sumec | JBU | AC Cabling | AC Cabling | Specific Requirements | 1.19.3 | The runs of both the main DC and AC cables, in the System layout, should be adjusted to keep power losses below <1% at STC (Design calculations through cable loss simulation to be provided for review & comment). | 1 |  |  |  | 1 |  | L | Part of system design | Kategorie ?
Sumec | JBU | AC Combiner Box | AC Combiner Box | Design factors to be provided | 1.20.1 | Rated voltage | 1 |  | 1 |  |  |  | not applicable
Sumec | JBU | AC Combiner Box | AC Combiner Box | Design factors to be provided | 1.20.1 | Rated current | 1 |  | 1 |  |  |  | not applicable
Sumec | JBU | AC Combiner Box | AC Combiner Box | Design factors to be provided | 1.20.1 | Class 2 AC surge arrestor | 1 |  | 1 |  |  |  | not applicable
Sumec | JBU | AC Combiner Box | AC Combiner Box | Design factors to be provided | 1.20.1 | Load breaker switch of adequate size | 1 |  | 1 |  |  |  | not applicable
Sumec | JBU | AC Combiner Box | AC Combiner Box | Design factors to be provided | 1.20.1 | Flame test | 1 |  | 1 |  |  |  | not applicable
Sumec | JBU | AC Combiner Box | AC Combiner Box | Design factors to be provided | 1.20.1 | Waterproof test | 1 |  | 1 |  |  |  | not applicable
Sumec | JBU | AC Combiner Box | AC Combiner Box | Design factors to be provided | 1.20.1 | Operating temperature range | 1 |  | 1 |  |  |  | not applicable
Sumec | JBU | AC Combiner Box | AC Combiner Box | Design factors to be provided | 1.20.1 | Stripping length of the individual wire | 1 |  | 1 |  |  |  | not applicable
Sumec | JBU | AC Combiner Box | AC Combiner Box | Standards | 1.20.2 | IP 67 | 1 |  | 1 |  |  |  | not applicable
Sumec | JBU | AC Combiner Box | AC Combiner Box | Standards | 1.20.2 | EN 60529, DIN-VDE-0472 | 1 |  | 1 |  |  |  | not applicable | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient?
Sumec | JBU | Step-up Transformers/MV Switchgear | Step-up Transformers/MV Switchgear | Guarantees | 1.21.1 | Compatibility with NTDC grid connection code must be ensured | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Sumec | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Design factors to be provided | 1.21.2 | 3-phase, double wound, continuously rated, oil-cooled, enclosed transformers, use of low loss core steel and close coupled copper windings | 1 |  | 1
Sumec | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Design factors to be provided | 1.21.2 | Incoming terminals | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Sumec | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Design factors to be provided | 1.21.2 | Outgoing terminals | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Sumec | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Design factors to be provided | 1.21.2 | kVA rating | 1 |  | 1
Sumec | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Design factors to be provided | 1.21.2 | Primary side voltage | 1 |  | 1
Sumec | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Design factors to be provided | 1.21.2 | Secondary side voltage | 1 |  | 1
Sumec | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Design factors to be provided | 1.21.2 | Insulation type | 1 |  | 1
Sumec | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Design factors to be provided | 1.21.2 | Short-circuit impedance | 1 |  | 1
Sumec | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Design factors to be provided | 1.21.2 | No-load losses | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Sumec | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Design factors to be provided | 1.21.2 | Efficiency | 1 | TECHNICAL OFFER-VOLUME I, page 295 | 1 |  |  |  | 2% of losses
Sumec | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Design factors to be provided | 1.21.2 | Operating temperature range | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Sumec | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Design factors to be provided | 1.21.2 | Maximum ambient temperature and altitude | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Sumec | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Design factors to be provided | 1.21.2 | Humidity tolerance | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Sumec | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Design factors to be provided | 1.21.2 | Cooling method | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Sumec | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Design factors to be provided | 1.21.2 | Protection system | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Sumec | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Design factors to be provided | 1.21.2 | Operational data shall be logged in central operating system (e.g. oil temperature, oil level, pressure, Temperature probes (one per phase): Alarm and trip of cell etc.) | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Sumec | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Standards | 1.21.3 | IEC 62446 | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Sumec | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Standards | 1.21.3 | IEC 60076 | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Sumec | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Standards | 1.21.3 | IEC 60085 | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Sumec | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Standards | 1.21.3 | IEC 60214 | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Sumec | JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Standards | 1.21.3 | IEC 60137 | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Sumec | JBU | Step-up Transformers/MV Switchgear | Due Diligence | Quality Assurance | 1.21.3 | Factory witness testing will be required for MV transformer and switchgear to be installed at this project. The cost of the due diligence to be carried by the Employer through an independent technical consultant will be taken over by the successful bidder up to an amount of 30,000 USD. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Sumec | JBU | Step-up Transformers/MV Switchgear | MV Switchgear | Specific Requirements | 1.21.4 | MV Switchgears shall be SF6 gas insulated or VCB (Vacuum circuit breaker). | 1 |  | 1
Sumec | JBU | Step-up Transformers/MV Switchgear | MV Switchgear | Specific Requirements | 1.21.4 | The separating equipment shall be installed with visible disconnection (pivotable disconnectors). | 1 |  | 1 |  |  |  |  | Cannot be evaluated at this stage
Sumec | JBU | Step-up Transformers/MV Switchgear | MV Switchgear | Specific Requirements | 1.21.4 | Interlocks will also be mechanically interlocked between line MV switchgears. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Sumec | JBU | Step-up Transformers/MV Switchgear | MV Switchgear | Design factors to be provided | 1.21.4 | System nominal voltage | 1 |  | 1
Sumec | JBU | Step-up Transformers/MV Switchgear | MV Switchgear | Design factors to be provided | 1.21.4 | System maximum voltage | 1 |  | 1
Sumec | JBU | Step-up Transformers/MV Switchgear | MV Switchgear | Design factors to be provided | 1.21.4 | Rated lightning impulse voltage | 1 |  | 1
Sumec | JBU | Step-up Transformers/MV Switchgear | MV Switchgear | Design factors to be provided | 1.21.4 | Rated power frequency withstand voltage | 1 |  | 1
Sumec | JBU | Step-up Transformers/MV Switchgear | MV Switchgear | Design factors to be provided | 1.21.4 | Rated short circuit current | 1 |  | 1
Sumec | JBU | Step-up Transformers/MV Switchgear | MV Switchgear | Standards | 1.21.5 | IEC 62446 | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Sumec | JBU | Step-up Transformers/MV Switchgear | MV Switchgear | Standards | 1.21.5 | IEC 62271-200 | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Sumec | JBU | Step-up Transformers/MV Switchgear | MV Switchgear | Standards | 1.21.5 | IEC 60529 | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Sumec | JBU | Inverter/Transformer Station | Inverter/Transformer Station | Specific Requirements | 1.22 | Bidder shall firmly specify the number of stations, manufacturer, capacity and type of equipment. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Sumec | JBU | Inverter/Transformer Station | Inverter/Transformer Station | Specific Requirements | 1.22 | All stations shall be equipped with fire and smoke detectors and alarm, connected to security and surveillance system | 1 |  | 1
Sumec | JBU | Inverter/Transformer Station | Inverter/Transformer Station | Specific Requirements | 1.22 | Fine sand filters shall be installed | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Sumec | JBU | Inverter/Transformer Station | Inverter/Transformer Station | Specific Requirements | 1.22 | The station shall enable the grounding of hardware and neutral will be left ground isolated | 1 |  | 1
Sumec | JBU | Inverter/Transformer Station | Inverter/Transformer Station | Specific Requirements | 1.22 | Every ten (10) or lesser number of stations shall be equipped with an earthing and short-circuiting equipment | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Chint | JBU | Supervisory Control and Data Acquisition (SCADA) | SCADA | Specific Requirements | 1.9.1 | Safe and redundant archive for operational data. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | General understanding: expressions like "shall", "has to be", "must be" have the meaning of "will be delivered"? Please confirm. |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Chint | JBU | Supervisory Control and Data Acquisition (SCADA) | SCADA | Specific Requirements | 1.9.1 | Remote access to all operational data for independent monitoring purposes shall be possible (NTDC requirements) | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Chint | JBU | Supervisory Control and Data Acquisition (SCADA) | SCADA | Specific Requirements | 1.9.1 | The system has to provide different access-levels with different access rights allocated. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Chint | JBU | Supervisory Control and Data Acquisition (SCADA) | SCADA | Specific Requirements | 1.9.2 | Control room to remotely monitor and manage the whole system, on a 24 x 7 basis, with the capability of Web-based information sharing | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  |  |  | C | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria.
Chint | JBU | Supervisory Control and Data Acquisition (SCADA) | SCADA | Specific Requirements | 1.9.2 | Alarms/alerts and timely notification of key performance indicators | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Chint | JBU | Supervisory Control and Data Acquisition (SCADA) | SCADA | Specific Requirements | 1.9.2 | Data must be readily available for the fulfilment of all warranties and performance guarantees | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Cannot be evaluated at this stage. | statement | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Chint | JBU | Supervisory Control and Data Acquisition (SCADA) | SCADA | Specific Requirements | 1.9.2 | Data logging at intervals of not less than one minute, processing, transmission, and back-up | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  |  | not more (!) | C | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria.
Chint | JBU | Supervisory Control and Data Acquisition (SCADA) | SCADA | Specific Requirements | 1.9.2 | Separate inverter, zone, and string level (current and voltage) monitoring | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Chint | JBU | Supervisory Control and Data Acquisition (SCADA) | SCADA | Specific Requirements | 1.9.2 | Back-up power for a minimum of twelve hours | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  |  |  | C | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria.
Chint | JBU | Supervisory Control and Data Acquisition (SCADA) | SCADA | Specific Requirements | 1.9.2 | Data shall be provided via FTP (Push/Pull) to the Employer | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Chint | JBU | Supervisory Control and Data Acquisition (SCADA) | SCADA | Specific Requirements | 1.9.2 | All communication/data cables outside of buildings must be fiber-optic cables | 1 |  |  |  | 1 | Unclear: We do not understand your proposal, please detail your proposal. Especially confirm that you are compliant with our requested criteria. |  |  |  | U | Unclear: We do not understand your proposal, please detail your proposal. Especially confirm that you are compliant with our requested criteria.
Chint | JBU | Meteorological Sensors | Auxiliary Systems | Specific Requirements | 1.10.1 | Irradiation and temperature measurements are to be recorded at intervals of 15 min or less. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Chint | JBU | Meteorological Sensors | Auxiliary Systems | Specific Requirements | 1.10.1 | The equipment should have the capability of recording and storing data for 24 hours using auxiliary DC power. | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  | Should be priority 1 question |  | C | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria.
Chint | JBU | Meteorological Sensors | Auxiliary Systems | Specific Requirements | 1.10.2 | The irradiation measurement equipment should be calibrated by an independent certified third party at least every two years. The calibration must be traceable to international standards. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Should be checked in list of deviations |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Chint | JBU | Meteorological Sensors | Auxiliary Systems | Specific Requirements | 1.10.2 | Seven pyranometers shall be placed : three for measuring the horizontal plane irradiation and the others for the in-plane irradiation. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | As in 1.10.2, it is seven pyranometer per system, please clarify the word "per system" | 1.1.1: "100 MWp (DC capacity at Standard Testing Conditions, abbreviated STC … hereinafter called 'the System') " | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Chint | JBU | Meteorological Sensors | Auxiliary Systems | Specific Requirements | 1.10.2 | The pyranometers should conform to the standards of ISO 9060 (SR5: secondary standard) or the WMO classification, and IEC 60904. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Do we need to know some parameter values according to standards mentioned or just a statement of comlience with the standard would be sufficient? | compliance will be necessary, no data due diligence right now. | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Chint | JBU | Meteorological Sensors | Auxiliary Systems | Specific Requirements | 1.10.3 | Ambient air and the module temperature shall be measured at every 5 installed MWp in conformity with IEC 60751 AA | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Chint | JBU | Site Preparation and site access | Site Preparation and site access | Specific Requirements | 1.11.1 | The Bidder shall provide foundations and structures in accordance with the actual soil conditions. | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  |  | refer to Soil study | C | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria.
Chint | JBU | Earthworks | Site Preparation and site access | Specific Requirements | 1.12 | Within the plant boundary limits, access roads to all stations shall be suitable for heavy load trucks (axle load: min. 12 tonn). | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  |  |  | C | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria.
Chint | JBU | Earthworks | Site Preparation and site access | Specific Requirements | 1.12 | Position and specification of underground cable connections must be documented during installation | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  | Cannot be avaluated at this stage. |  | C | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria.
Chint | JBU | Earthworks | Site Preparation and site access | Specific Requirements | 1.12, 1.13.4, 1.7.7 | Cross-sections of foundations for stations shall be provided, including explanation of the foundations laying down, height, penetration, and method of installing foundation posts, mounting fixtures | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | no layouts of station foundations |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Chint | JBU | Earthworks | Site Preparation and site access | Design factors to be provided | 1.12 | All earth works required have to be specified and included in the offer | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  |  |  | C | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria.
Chint | JBU | Earthworks | Site Preparation and site access | Specific Requirements | 1.12 | After completion of construction and all earthworks ground shall be levelled and stabilized. | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  |  | (maintanance, dust) | C | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria.
Chint | JBU | Mounting | Mounting | Specific Requirements | 1.13.1 | The system is fixed-tilted. Tilt angle is specified. | 1 |  | 1
Chint | JBU | Mounting | Mounting | Specific Requirements | 1.13.3 | Mounting structure is made of durable material, resistant to sandstorms and compatible with the module frame material so as to avoid any adverse electrolytic/galvanic effects. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Information about materials to be known before evaluation. | right | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Chint | JBU | Mounting | Mounting | Specific Requirements | 1.13.3 | Mounting system resists high wind speeds (up to 40 m/s) | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Chint | JBU | Mounting | Mounting | Specific Requirements | 1.13.3 | Mounting system resists corrosion (passing the salt spray test IEC 61701, among other verification), | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Information about materials to be known before evaluation. | right | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Chint | JBU | Mounting | Mounting | Specific Requirements | 1.13.3 | Mounting system resists UV induced degradation | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Chint | JBU | Mounting | Mounting | Specific Requirements | 1.13.5 | All fastening structures must be verified for durability and resistance to environmental degradation for 25 years | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | What sort of mechanism is required for verification? | Sub structure description / materials double to line 172 - 175 | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Chint | JBU | Mounting | Mounting | Specific Requirements | 1.13.8 | The mounting structures must be earthed | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Chint | JBU | Mounting | Mounting | Specific Requirements | 1.13.9 | Specific site conditions have been considered. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Needs to be discussed. | … specific requirements of the soil conditions Static | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Chint | JBU | Mounting | Mounting | Standards | 1.13.9 | IEC 61730 (as above) | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? | no, just a statement of compliance | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Chint | JBU | Mounting | Mounting | Standards | 1.13.9 | STS 531 | 1 |  | - |  |  |  | not applicable | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? | no, just a statement of compliance
Chint | JBU | Mounting | Mounting | Standards | 1.13.9 | IEC 61730 | 1 |  | - |  |  |  | not applicable | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? | no, just a statement of compliance
Chint | JBU | Other infrastructure | Auxiliary systems | Design factors to be provided | 1.25.1 | One administration and office building with car port for 10 vehicles shall be provided, with sufficient space for operating personal, control room, security office, regular office rooms for permanent and visiting staff, meeting room, kitchen sanitary systems (toilet, showers separate for male and female), first aid, control room, electrical rooms, etc. The building shall have windows for office rooms and air conditioning system (split units) for all office rooms. | 1 |  | 1 |  |  |  |  | Priority to be discussed
Chint | JBU | Other infrastructure | Auxiliary systems | Design factors to be provided | 1.25.1 | Warehouse for spare parts and workshop for minor mechanical/electrical works. | 1 |  | 1
Chint | JBU | Other infrastructure | Auxiliary systems | Design factors to be provided | 1.25.1 | Water storage facility for drinking water, sanitary water (sufficient for 1 week) | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Chint | JBU | Other infrastructure | Auxiliary systems | Design factors to be provided | 1.25.1 | Service water system sufficiently sized for cleaning cycle of modules | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Chint | JBU | Other infrastructure | Auxiliary systems | Design factors to be provided | 1.25.1 | Sewage system including sewage disposal for Construction and O&M phase | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Chint | JBU | Other infrastructure | Auxiliary systems | Guarantees | 1.25.4 | All buildings should be designed in accordance with the requirements of the Pakistan Building Code (available at www.pec.org.pk/buildingcode.aspx) and latest Seismic Provisions 2007. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Link to code |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Chint | JBU | Other infrastructure | Auxiliary systems | Security Surveillance System | 1.25.5 | The system shall comply with insurance requirements | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Chint | JBU | Other infrastructure | Auxiliary systems | Security Surveillance System | 1.25.5 | The Bidder shall provide security personnel for 24 h / 7 days a week for the whole year | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Chint | JBU | Other infrastructure | Auxiliary systems | DC Backup System / uninterrupted power supply (UPS) | 1.25.6 | IEC-60051 and IEC-60439 standards apply | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Tbea | GD | Scope of the Bid | General items | Specific Requirements | 1.1.2 | The Offer shall include a list of all vendors and/or sub-contractors for major equipment. | 1 |  |  |  | 1 |  |  |  |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  | 1 |  | Open
Tbea | GD | Scope of the Bid | General items | Quality Assurance | 1.1.3 | Defect components consequences: If one tested sample fails in one criterion, all items of the same category will be regarded as failed and rejected. | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  | Only to be checked in list of deviations. | yes, we need to be sure that they comply as for most of the critera | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | 1 | 1 | Open
Tbea | GD | Scope of the Bid | General items | Guarantees | 1.1.5 | Energy Purchase Agreement (EPA) practices are followed | 1 |  |  |  | 1 | Important reasons: due to current uncertainty of the criteria we accept an open status. Please clarify that yo acknowledge the criteria and comply unless a reason of high importance will not allow you you to comply. In such a situation the parties will seek to agree a compromise. |  | This cannot be evaluated at this stage. | we need a sentence that it should and can only be disregarded for important reasons | Unclear: We do not understand your proposal, please detail your proposal. Especially confirm that you are compliant with our requested criteria. |  | 1 |  | Open
Tbea | GD | Scope of the Bid | Layout | Guarantees | 1.1.6 | The bidder confirms that the system complies with all applicable requirements of the NEPRA Grid Code of Pakistan and its Draft Amendment no. 2 for Solar Power Projects. | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  | Only to be checked in list of deviations. |  | Important reasons: due to current uncertainty of the criteria we accept an open status. Please clarify that yo acknowledge the criteria and comply unless a reason of high importance will not allow you you to comply. In such a situation the parties will seek to agree a compromise. |  | 1 |  | Open
Tbea | GD | Scope of the Bid | Credentials | EPC | 1.1.9 | The bid includes professional experience of the Bidders in ground mounted utility-scale PV and financial information about their long-term stability | 3 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | GD | Scope of the Bid | General items | Specific Requirements | 1.1.9 | The bid covers the planning of the System design, the required functionality of the System in terms of its sub-systems and components, detailed feature-wise descriptions of the components to be used in the System, the planning of the System installation, its integration, testing, monitoring, commissioning and O&M of the System | 1 |  |  |  | 1 | We can not find all of the requested criteria in your documents. Please confirm that your bid is compliant with all expectations and requirements of Section 6 of the RFP and provide a list with ALL exeptions or alterations. This applies to both, the EOPC And the O&M part. |  | This question should be removed as detailed design of every component/sub-system will be checked and evaluated thoroughly in technical evaluation | no, its an overall critera an need to be met |  |  | 1 | 1 | Open
Tbea | GD | Scope of the Bid | Credentials | EPC | 1.1.10 | The Bidder, or the Lead company in case of JV is a EPC contractor | 1 |  | 1 |  |  |  |  | This is a non-technical question. We suggest such question should be separated from technical questions and placed in checklist for "General/Substantive Responsiveness of Bid" | a question of reliability and experience of solid understanding of the task/System Technology. See also 1.1.10 |  |  | 1 |  | Pass
Tbea | GD | Conditions for Disqualification and Additional Information Required | Credentials | EPC | 1.2.6 | Detailed list of all the sites with the affirmation that the bidder played the leading EPC role in the turnkey installation of these systems. | 3 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | GD | Conditions for Disqualification and Additional Information Required | Credentials | EPC | 1.2.6 | Cumulative MWp of ground mounted PV turnkey installations >5 MWp with stating of actual MWp per project, project location, date of commissioning, module type and Inverter type. | 1 |  | 1 | [5 empty] | experience of Bidder / EPC |  |  | 1 | 1 | Pass
Tbea | GD | Conditions for Disqualification and Additional Information Required | Credentials | EPC | 1.2.6 | References and contact data (mail and phone) from owners of all installations > 5 MW with quotes of the corresponding system Performance Ratios, as well as system performance vs. initial yield assessment per year since the installation. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  | for selection of referenz objects |  |  | 1 | 1 | Open
Tbea | GD | Conditions for Disqualification and Additional Information Required | Credentials | EPC | 1.2.6 | Approval from bidder to owners or owner representatives to answer questions freely regarding the past performance of the bidder and performance of the system against contractual obligations. | 2 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | [5 empty] | 1 |  | Open
Tbea | GD | Conditions for Disqualification and Additional Information Required | Credentials | O&M | 1.2.6 | Cumulative MWp of ground mounted PV installations for which O&M services have been delivered by the bidder or his O&M subcontractor. | 2 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | [5 empty] | 1 |  | Open
Tbea | GD | Conditions for Disqualification and Additional Information Required | Credentials | O&M | 1.2.6 | References, contact data and approval from owners or owner representatives of all installations > 5 MW from bidder or his O&M subcontractor to answer questions freely regarding the past performance of the bidder and performance of the system against contractual obligations. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | [5 empty] | 1 | 1 | Open
Tbea | GD | Technical Bid Evaluation Criteria | Credentials | Guarantees | 1.3.1 | To have met the contractual requirements of the EPC and O&M deliverables including certificate to the effect that the entire equipment is brand new as required vide notification number NEPRA/UTS-01/777-779 dated Jan 21 ,2014, | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Only to be checked in list of deviations. |  |  |  | 1 | 1 | Open
Tbea | GD | Technical Bid Evaluation Criteria | Credentials | EPC | 1.3.1 | the systems have been completed on time and within budget, | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | [5 empty] | 1 | 1 | Open
Tbea | GD | Technical Bid Evaluation Criteria | Credentials | O&M | 1.3.1 | that they have started supplying electricity to the grid and are still operating satisfactorily in 9 out of 10 MW for all the cases | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | [5 empty] | 1 | 1 | Open
Tbea | GD | Technical Bid Evaluation Criteria | Credentials | O&M | 1.3.1 | In case of a non-performance, comprehensible evidence has to be given why this case will not affect this project. | 3 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | [5 empty] | 1 |  | Open
Tbea | GD | Technical Bid Evaluation Criteria | Credentials | O&M | 1.3.2 | Prove at least 100 MW of EPC experience and 50 MW of full O&M experience for a period longer than 24 months. | 1 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | GD | Technical Bid Evaluation Criteria | Due Diligence | Quality Assurance | 1.3.5 | The cost of the due diligence to be carried out by the Employer through an independent technical consultant before contract signature will be taken over by the successful bidder up to an amount of 50,000 USD independent of the result. The due diligence will cover a module factory visit, an inverter factory inspection and a due diligence on the provided financial, EPC and O&M credentials including up to three site visits. | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  | Only to be checked in list of deviations. |  |  |  | 1 |  | Open
Tbea | GD | PR and System Performance Guarantee | System PR | Guarantees | 1.4.1 | A 25 years commitment, in the form of a whole System performance guarantee, is required. The performance guarantee is based on measuring the PR with the actual kWh-AC delivery per year adjusted for the actual POA irradiation for the same period | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  | Only to be checked in list of deviations. |  |  |  | 1 | 1 | Open
Tbea | GD | PR and System Performance Guarantee | System PR | System PR | 1.4.1 | The billing system/metering system will be installed at interconnection point of 132 kV bus bar of HV substation to be installed by the EPC Contractor and the 132 kV Transmission line of NTDC existing at site. | 2 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  | Only to be checked in list of deviations. |  |  |  | 1 |  | Open
Tbea | GD | PR and System Performance Guarantee | System PR | System PR | 1.4.2 | Guaranteed PR values in the form of the Table in 1.4.1 for the acceptance phase and annual output of the PV system shall be specified. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Link to table in Documents sheet |  |  |  | 1 | 1 | Open
Tbea | GD | PR and System Performance Guarantee | System PR | System PR | 1.4.4 | The initial PR will be first measured after the time of commissioning of the completed PV System during the acceptance phase of 30 days. | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  | Cannot be evaluated at this stage. Only to be checked in list of deviations. |  |  |  | 1 | 1 | Open
Tbea | GD | PR and System Performance Guarantee | Compensations | System PR | 1.4.4 | The successful Bidder shall conduct the initial PR test for the daylight hours of at least 30 consecutive days, recording data at a frequency of fifteen minute intervals or less, to validate the guaranteed PR value for acceptance. Any excused downtime (e.g., from Grid Operator ordered shutdowns, grid failure, theft, force majeure) will be excluded from that calculation by an independent consultant (Auditing Body). That day will be taken out and another day added, if the initial PR falls short of the guaranteed PR value, the successful Bidder shall be obliged to identify and rectify the causes for the performance shortfall at their own cost. | 2 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  | Cannot be evaluated at this stage. Only to be checked in list of deviations. |  |  |  | 1 |  | Open
Tbea | GD | PR and System Performance Guarantee | Compensations | System PR | 1.4.4 | If the measured PR within further 30 days does not reach the guaranteed PR, the Employer can demand that the price of the system will be reduced by the percentage of shortfall times 1.2 for liquidated damages or the contractor will have to install more power at its own cost or combination of both. | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  | Cannot be evaluated at this stage. Only to be checked in list of deviations. |  |  |  | 1 | 1 | Open
Tbea | GD | PR and System Performance Guarantee | Compensations | O&M | 1.4.5 | If the annual measured PR falls below the guaranteed PR value according to Table 1.4.1, the liquidated damages will be levied on the successful Bidder at the rate of USD 0.20-per-kWh or the kWh Value the Employer receives for each kWh of shortfall – whichever is higher. Adjustments shall be made for any events outside the control of the O&M operator as grid outages, from grid operator ordered shutdowns, or force majeure events during the year. | 2 |  |  |  | 1 |  |  | Cannot be evaluated at this stage. Only to be checked in list of deviations. | Only to be checked in list of deviations. |  |  | 1 |  | Open
Tbea | GD | PR and System Performance Guarantee | Compensations | O&M | 1.4.5 | In case the PR is higher than the guaranteed PR value, the net value of this excess energy will be shared as follows: 50% towards the asset replacement fund, 25% towards the Employer, 25% towards the O&M contractor | 3 |  |  |  | 1 |  |  | Cannot be evaluated at this stage. Only to be checked in list of deviations. |  |  |  | 1 |  | Open
Tbea | GD | PR and System Performance Guarantee | Compensations | O&M | 1.4.5 | For timely compensation the PR Calculation will be carried out provisionally for each quarter whereby the contractor and employer might jointly agree on different PR values for each quarter. In the last quarter of each calendar year the annual PR compensation of the full year will be carried out and any provisions will be offset by the annual compensation. | 3 |  |  |  | 1 |  |  | Cannot be evaluated at this stage. Only to be checked in list of deviations. |  |  |  | 1 |  | Open
Tbea | GD | PR and System Performance Guarantee | Compensations | O&M | 1.4.6 | If the successful Bidder defaults in being able to provide the O&M services required for the Systems performance guarantee, then it will be liable to cover all costs – but at least in the amount of Liquidated Damages imposed to the Employer by its PPA agreements - incurred by the Employer, including the loss of the guaranteed electricity export to the grid (but at a minimum rate of USD 0.20-per-kWh) for the disrupted period, in finding and hiring a replacement for the purpose. | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  | Cannot be evaluated at this stage. Only to be checked in list of deviations. |  |  |  | 1 | 1 | Open

## JBS (hidden)
Bidder | Expert | Chapter in RfP | Topic | Subtopic | Clause | Criteria | 1 Vital 2 Valuable 3 Not Important | Link to Bidders Documents | Pass =1 | Fail =1 | Open =1 | Question to bidder for clarification | Comments | Comments QA on Criteria | Comment on "Comments" | Typical Questions to be send to bidders if Open status |  | Sub-category
Juwi | JBS | System PR Specification | System PR | O&M | 1.5.2 | The target PR specification at the time of commissioning the System is equal to or greater than 0.75 (75%). | 1 | Page 392-395 |  | 1 | 1 |  | 74.8%
Juwi | JBS | System PR Specification | System PR | Losses included in PR calculation | 1.5.4 | Module Array (temperature dependence, soiling, low light inefficiency, shading, mismatches in array) | 1 | Page 392-395 | 1 |  |  |  |  | We don’t understand the question. Kindly clarify. | we want to see these losses specified. Thos need to be aligned with O+M Startegy and System composition
Juwi | JBS | System PR Specification | System PR | Losses included in PR calculation | 1.5.4 | Inverter (operating efficiency, operating voltage variations, power/voltage levels) | 1 | Page 392-395 | 1 |  |  |  |  | We don’t understand the question. Kindly clarify. | see relevant chapter 1.5.4 List of technical losses that make the PR
Juwi | JBS | System PR Specification | System PR | Losses included in PR calculation | 1.5.4 | Transformer losses | 1 | Page 392-395 | 1 |  |  |  |  | We don’t understand the question. Kindly clarify. | see relevant chapter 1.5.4 List of technical losses that make the PR
Juwi | JBS | System PR Specification | System PR | Losses included in PR calculation | 1.5.4 | Ohmic losses in cables | 1 | Page 392-395 | 1 |  |  |  |  | We don’t understand the question. Kindly clarify. | see relevant chapter 1.5.4 List of technical losses that make the PR
Juwi | JBS | System PR Specification | System PR | Losses included in PR calculation | 1.5.4 | Auxiliary loads | 1 | Page 392-395 |  | 1 | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | Nicht berücksichtigt | We don’t understand the question. Kindly clarify. | see relevant chapter 1.5.4 List of "losses" = auxilary loads from PV Energy that make the PR | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Juwi | JBS | Basic Scope of Supply | General items | Specific Requirements | 1.6 | The maximum DC voltage shall not exceed 1500 V | 1 | Page 392-395 | 1
Juwi | JBS | Basic Scope of Supply | General items | Specific Requirements | 1.6 | The required AC voltage / frequency at grid connection shall 132 kV/50 Hz | 1 |  | 1
Juwi | JBS | Basic Scope of Supply | Warranty | Quality Assurance | 1.6 | The Product Warranties shall be given for a duration of at least 5 years | 1 |  |  |  | 1 |  | Nicht für alle gefunden | Cannot be evaluated at this stage. Only to be checked in list of deviations. |  | C
Juwi | JBS | Physical layout | System PR | Specific Requirements | 1.7.1, 1.1.8 | Layout calculations of predicted kWh over the system lifetime and PR using the tool PVSyst V5.62 or higher | 1 | Page 392-395 | 1
Juwi | JBS | Physical layout | System PR | Specific Requirements | 1.7.1 | Provide a report using Solar GIS data provided by the Employer | 1 | Page 41 | 1 |  |  |  |  | Replace 'Report' with ' PV-Syst report'. | 'Report' is original wording in ER in 1.7.1
Juwi | JBS | Physical layout | Layout | Specific Requirements | 1.7.2 | Provide a schematic electrical Single Line Diagram (SLD) of the entire System layout from the modules to the grid-connection, identifying and listing all of the following DC and AC components. | 1 | Page 307 - 310 | 1
Juwi | JBS | Physical layout | Layout | Specific Requirements | 1.7.2 | The system design shall be such as to ensure ease of maintenance and a multiple ring main unit (RMU) philosophy (on MV level) must be followed for circuit breaker configuration. | 1 | Page 310 |  | 1 | 1 |  | Stichleitung mit 5 Stationen max. |  |  | U
Juwi | JBS | Physical layout | Physical layout plan | Specific Requirements | 1.7.7 | Floor plans and elevations for all buildings, housing units, containers on site: e.g. , substations, the SCADA operational room, inverters, O&M, storage facilities | 1 | Page 37 | 1
Juwi | JBS | Physical layout | Physical layout plan | Specific Requirements | 1.7.7 | Detailed view of the distribution of inverters and connections to the PV string/array | 1 | Page 307 - 310 | 1
Juwi | JBS | Physical layout | Physical layout plan | Specific Requirements | 1.7.7 | Detailed top view of the PV mounting structure, including module sizes and spacing between the module rows | 1 | Page 274 | 1
Juwi | JBS | Physical layout | Physical layout plan | Specific Requirements | 1.7.7 | Detailed side and front view of the PV mounting structure | 1 | Page 274 | 1
Juwi | JBS | Physical layout | Physical layout plan | Specific Requirements | 1.7.7 | Detailed top view of electrical cabling interconnections | 1 | Page 307 - 310 | 1
Juwi | JBS | Physical layout | Physical layout plan | Specific Requirements | 1.7.7 | Location of the system metering and grid connection point | 1 | Page 307 - 310 | 1
Juwi | JBS | Physical layout | Auxiliary equipment | Specific Requirements | 1.7.8 | Provide complete indicating, regulating, controlling, protecting and interlocking equipment necessary for safe and efficient operation of the plant and substation, including complete protection scheme. | 1 | Page 307 - 310 | 1
Juwi | JBS | Physical layout | Auxiliary equipment | Specific Requirements | 1.7.8 | The outline of protection schemes shall be shown on the single line diagram (SLD) | 1 | Page 309 | 1
Juwi | JBS | Physical layout | Auxiliary equipment | Specific Requirements | 1.7.8 | All parts of the installation are covered by two high speed protection schemes, which shall be independent to avoid common mode failures | 1 | Page 309 | 1
Juwi | JBS | Physical layout | Auxiliary equipment | Specific Requirements | 1.7.8 | The Bidder shall include a fire prevention and response plan | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Juwi | JBS | Physical layout | Auxiliary equipment | Specific Requirements | 1.7.8 | The fire prevention and response plan shall include a fire alarm und detection system with a main panel in the control room | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Juwi | JBS | Physical layout | Auxiliary equipment | Specific Requirements | 1.7.9 | The documentation includes clearly labelled objects and figures annotated in English language. | 1 |  |  |  | 1 |  |  |  |  | C
Juwi | JBS | Physical layout | Auxiliary equipment | Specific Requirements | 1.7.9 | The scope of the documentation shall cover at least the requirements of IEC 62446. | 1 |  |  |  | 1 | Unclear: We do not understand your proposal, please detail your proposal. Especially confirm that you are compliant with our requested criteria. |  |  |  | C | Unclear: We do not understand your proposal, please detail your proposal. Especially confirm that you are compliant with our requested criteria.
Juwi | JBS | Workflow, Project Management Plan and Timelines | Project schedule / Project management | Project schedule | 1.8.1 | Provide installation schedule in compliance with sub-clause 8.2 of Particular Conditions (Time for Completion is 225 days after Commencement Date). | 1 | Page 487 |  | 1 | 1 |  | 341 Tage | Find sub-clause 8.2 of Particular Conditions
Juwi | JBS | Workflow, Project Management Plan and Timelines | Project schedule / Project management | Project schedule | 1.8.1 | Provide work breakdown structures, activity decomposition and sequencing and dependability with the baseline schedule clearly showing the critical path | 1 | Page 487 | 1
Juwi | JBS | Workflow, Project Management Plan and Timelines | Project schedule / Project management | Project schedule | 1.8.1 | Schedule of tasks | 1 |  | 1
Juwi | JBS | Workflow, Project Management Plan and Timelines | Project schedule / Project management | Project schedule | 1.8.1 | Interdependencies between the tasks | 1 |  | 1
Juwi | JBS | Workflow, Project Management Plan and Timelines | Project schedule / Project management | Project schedule | 1.8.1 | Interdependencies of tasks with equipment order and delivery times | 1 |  | 1
Juwi | JBS | Workflow, Project Management Plan and Timelines | Project schedule / Project management | Project schedule | 1.8.1 | Key milestones to indicate that the progress in on schedule | 1 |  | 1 |  |  | Unclear: We do not understand your proposal, please detail your proposal. Especially confirm that you are compliant with our requested criteria. |  |  |  |  | Unclear: We do not understand your proposal, please detail your proposal. Especially confirm that you are compliant with our requested criteria.
Juwi | JBS | Workflow, Project Management Plan and Timelines | Project schedule / Project management | Project schedule | 1.8.1 | Teams, the number and skills of personnel to be deployed for each task | 1 |  | 1
Juwi | JBS | Workflow, Project Management Plan and Timelines | Project schedule / Project management | Quality Assurance | 1.8.3 | Quality control of delivered modules | 1 |  |  | 1 | 1 |  |  |  |  | C
Juwi | JBS | Workflow, Project Management Plan and Timelines | Project schedule / Project management | Quality Assurance | 1.8.3 | Inspection of equipment delivery | 1 |  |  | 1 | 1 |  |  |  |  | C
Juwi | JBS | Workflow, Project Management Plan and Timelines | Project schedule / Project management | Quality Assurance | 1.8.3 | Milestones for the completion of civil, mechanical, and electrical works | 1 |  |  | 1 | 1 | Unclear: We do not understand your proposal, please detail your proposal. Especially confirm that you are compliant with our requested criteria. |  |  | dobble to 105 and 111 | C | Unclear: We do not understand your proposal, please detail your proposal. Especially confirm that you are compliant with our requested criteria.
Juwi | JBS | Workflow, Project Management Plan and Timelines | Project schedule / Project management | Quality Assurance | 1.8.3 | Risk analysis and mitigation plan | 1 |  |  | 1 | 1 |  |  |  |  | C
Juwi | JBS | Workflow, Project Management Plan and Timelines | Project schedule / Project management | Quality Assurance | 1.8.3 | System acceptance QA procedure by the Employer | 1 |  |  | 1 | 1 |  |  |  |  | C
Juwi | JBS | Labelling | General items | Labelling | 1.26 | the ID numbering / coding system shall allow unique identification of all components and be understandable | 1 |  |  |  | 1 | Unclear: We do not understand your proposal, please detail your proposal. Especially confirm that you are compliant with our requested criteria. |  | Cannot be evaluated at this stage |  | C | Unclear: We do not understand your proposal, please detail your proposal. Especially confirm that you are compliant with our requested criteria.
Juwi | JBS | Labelling | General items | Labelling | 1.26 | Tags shall be weather and UV resistant. | 1 |  |  |  | 1 |  |  | Cannot be evaluated at this stage |  | C
Juwi | JBS | Labelling | General items | Labelling | 1.26 | The ID’s shall correspond to all drawings, plant documentation and control system. | 1 |  |  |  | 1 |  |  | Cannot be evaluated at this stage |  | C
Juwi | JBS | Power plant documentation | Power plant documentation | Quality Assurance | 1.27.1 | The Bidder shall confirm that the complete as-built documentation of the plant will be provided in compliance with IEC 62446. Additionally all module serial numbers shall be listed with their individual location. | 1 |  |  |  | 1 |  |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  | C
Juwi | JBS | Power plant documentation | Power plant documentation | Quality Assurance | 1.27.1 | Flash report list of all modules shall be provided in digital form. | 1 |  |  |  | 1 |  |  |  |  | C
Juwi | JBS | Power plant documentation | Spare parts | Warranty | 1.27.2 | The successful bidder shall provide all warranty spares for a warranty period of 5 years. | 1 |  |  |  | 1 |  |  |  |  | C
Juwi | JBS | Equipment guarantees | Warranty | Guarantees | 1.28 | The overall Guarantee and Power Plant Acceptance Procedures required for the Project are described in Sections 1.3, 1.4, 1.14, 1.18 and Schedule D and shall be met. | 1 |  |  |  | 1 |  |  | Link |  | C
Juwi | JBS | Equipment guarantees | Modules | Guarantees | 1.28.1 | The Successful bidder shall provide a Module warranty of at least 10 years. The performance warranty of the module shall be linear with a fixed factor over 25 years. | 1 | Page 17 | 1 |  |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  | To be discussed |  |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria.
Juwi | JBS | Equipment guarantees | Inverter | Guarantees | 1.28.2 | The Successful Bidder shall provide an Inverter warranty of at least 5 years. A spare parts warranty shall be included for the 25 years operational period. | 1 |  |  |  | 1 |  | kein Hinweis, dass die Verlängerung auf 25 im Angebot enthalten |  |  | C
Juwi | JBS | Equipment guarantees | Mounting | Guarantees | 1.28.3 | The Successful Bidder shall provide a product warranty for the structure of at least 10 years. | 1 | Page 18 | 1
Juwi | JBS | Equipment guarantees | Warranty | Guarantees | 1.28.4, 1.6 | A detailed list of all guarantee conditions for the main equipments (beside modules and inverters) shall be provided by the Successful Bidder with the technical offer. The product warranty shall be at least 5 years. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Juwi | JBS | Miscellaneous | Auxiliary systems | Power supply | 1.29.1 | An off-grid power station may need to be provided by the Bidder for commencing the work. Diesel generators shall be arranged by the bidder on its own. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Juwi | JBS | Miscellaneous | Project schedule / Project management | Specific Requirements | 1.29.9 | The Bidder shall submit an organizational chart illustrating management and functional relationships among all project team members including consultants, sub-contractors and vendors at each significant stage of the work, such as permitting, design, construction, testing and commissioning and O&M. | 1 | Page 406 | 1
Chint | JBS | System PR Specification | System PR | O&M | 1.5.2 | The target PR specification at the time of commissioning the System is equal to or greater than 0.75 (75%). | 1 |  | 1 |  |  |  | mit 75% gerade an der Grenze
Chint | JBS | System PR Specification | System PR | Losses included in PR calculation | 1.5.4 | Module Array (temperature dependence, soiling, low light inefficiency, shading, mismatches in array) | 1 |  | 1 |  |  |  |  | We don’t understand the question. Kindly clarify. | we want to see these losses specified. Thos need to be aligned with O+M Startegy and System composition
Chint | JBS | System PR Specification | System PR | Losses included in PR calculation | 1.5.4 | Inverter (operating efficiency, operating voltage variations, power/voltage levels) | 1 |  | 1 |  |  |  | Temperaturverlsute 16,9 | We don’t understand the question. Kindly clarify. | see relevant chapter 1.5.4 List of technical losses that make the PR
Chint | JBS | System PR Specification | System PR | Losses included in PR calculation | 1.5.4 | Transformer losses | 1 | Page 443-447 |  | 1 | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | Trafoverluste nicht berücksichtigt | We don’t understand the question. Kindly clarify. | see relevant chapter 1.5.4 List of technical losses that make the PR | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Chint | JBS | System PR Specification | System PR | Losses included in PR calculation | 1.5.4 | Ohmic losses in cables | 1 | Page 443-447 | 1 |  |  |  |  | We don’t understand the question. Kindly clarify. | see relevant chapter 1.5.4 List of technical losses that make the PR
Chint | JBS | System PR Specification | System PR | Losses included in PR calculation | 1.5.4 | Auxiliary loads | 1 | Page 443-447 |  | 1 | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | Nicht berücksichtigt | We don’t understand the question. Kindly clarify. | see relevant chapter 1.5.4 List of "losses" = auxilary loads from PV Energy that make the PR | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Chint | JBS | Basic Scope of Supply | General items | Specific Requirements | 1.6 | The maximum DC voltage shall not exceed 1500 V | 1 | Page 443-447 | 1 |  |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  |  |  |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria.
Chint | JBS | Basic Scope of Supply | General items | Specific Requirements | 1.6 | The required AC voltage / frequency at grid connection shall 132 kV/50 Hz | 1 | Page 443-447 | 1
Chint | JBS | Basic Scope of Supply | Warranty | Quality Assurance | 1.6 | The Product Warranties shall be given for a duration of at least 5 years | 1 |  |  |  | 1 |  |  | Cannot be evaluated at this stage. Only to be checked in list of deviations. |  | C
Chint | JBS | Physical layout | System PR | Specific Requirements | 1.7.1, 1.1.8 | Layout calculations of predicted kWh over the system lifetime and PR using the tool PVSyst V5.62 or higher | 1 | Page 443-447 | 1
Chint | JBS | Physical layout | System PR | Specific Requirements | 1.7.1 | Provide a report using Solar GIS data provided by the Employer | 1 | Page 443-447 | 1 |  |  |  |  | Replace 'Report' with ' PV-Syst report'. | 'Report' is original wording in ER in 1.7.1
Chint | JBS | Physical layout | Layout | Specific Requirements | 1.7.2 | Provide a schematic electrical Single Line Diagram (SLD) of the entire System layout from the modules to the grid-connection, identifying and listing all of the following DC and AC components. | 1 | Page 449- 453 | 1
Chint | JBS | Physical layout | Layout | Specific Requirements | 1.7.2 | The system design shall be such as to ensure ease of maintenance and a multiple ring main unit (RMU) philosophy (on MV level) must be followed for circuit breaker configuration. | 1 | Page 450 | 1 |  |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  |  |  |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria.
Chint | JBS | Physical layout | Physical layout plan | Specific Requirements | 1.7.7 | Floor plans and elevations for all buildings, housing units, containers on site: e.g. , substations, the SCADA operational room, inverters, O&M, storage facilities | 1 | Page 453 | 1
Chint | JBS | Physical layout | Physical layout plan | Specific Requirements | 1.7.7 | Detailed view of the distribution of inverters and connections to the PV string/array | 1 | Page 449 | 1 |  |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  |  |  |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria.
Chint | JBS | Physical layout | Physical layout plan | Specific Requirements | 1.7.7 | Detailed top view of the PV mounting structure, including module sizes and spacing between the module rows | 1 | Page 455 | 1 |  |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  |  |  |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria.
Chint | JBS | Physical layout | Physical layout plan | Specific Requirements | 1.7.7 | Detailed side and front view of the PV mounting structure | 1 | Page 455 | 1 |  |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  |  |  |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria.
Chint | JBS | Physical layout | Physical layout plan | Specific Requirements | 1.7.7 | Detailed top view of electrical cabling interconnections | 1 | Page 455 | 1 |  |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  |  |  |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria.
Chint | JBS | Physical layout | Physical layout plan | Specific Requirements | 1.7.7 | Location of the system metering and grid connection point | 1 | Page 452 | 1 |  |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  |  |  |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria.
Chint | JBS | Physical layout | Auxiliary equipment | Specific Requirements | 1.7.8 | Provide complete indicating, regulating, controlling, protecting and interlocking equipment necessary for safe and efficient operation of the plant and substation, including complete protection scheme. | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  |  |  |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria.
Chint | JBS | Physical layout | Auxiliary equipment | Specific Requirements | 1.7.8 | The outline of protection schemes shall be shown on the single line diagram (SLD) | 1 | Page 449- 453 | 1 |  |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  |  |  |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria.
Chint | JBS | Physical layout | Auxiliary equipment | Specific Requirements | 1.7.8 | All parts of the installation are covered by two high speed protection schemes, which shall be independent to avoid common mode failures | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  |  |  |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria.
Chint | JBS | Physical layout | Auxiliary equipment | Specific Requirements | 1.7.8 | The Bidder shall include a fire prevention and response plan | 1 | Chapter 2 | 1
Chint | JBS | Physical layout | Auxiliary equipment | Specific Requirements | 1.7.8 | The fire prevention and response plan shall include a fire alarm und detection system with a main panel in the control room | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  |  |  |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria.
Chint | JBS | Physical layout | Auxiliary equipment | Specific Requirements | 1.7.9 | The documentation includes clearly labelled objects and figures annotated in English language. | 1 |  | 1 |  |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  |  |  |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria.
Chint | JBS | Physical layout | Auxiliary equipment | Specific Requirements | 1.7.9 | The scope of the documentation shall cover at least the requirements of IEC 62446. | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  |  |  | C | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria.
Chint | JBS | Workflow, Project Management Plan and Timelines | Project schedule / Project management | Project schedule | 1.8.1 | Provide installation schedule in compliance with sub-clause 8.2 of Particular Conditions (Time for Completion is 225 days after Commencement Date). | 1 | Page 106 | 1 |  |  |  |  | Find sub-clause 8.2 of Particular Conditions
Chint | JBS | Workflow, Project Management Plan and Timelines | Project schedule / Project management | Project schedule | 1.8.1 | Provide work breakdown structures, activity decomposition and sequencing and dependability with the baseline schedule clearly showing the critical path | 1 |  | 1
Chint | JBS | Workflow, Project Management Plan and Timelines | Project schedule / Project management | Project schedule | 1.8.1 | Schedule of tasks | 1 |  | 1
Chint | JBS | Workflow, Project Management Plan and Timelines | Project schedule / Project management | Project schedule | 1.8.1 | Interdependencies between the tasks | 1 |  | 1
Chint | JBS | Workflow, Project Management Plan and Timelines | Project schedule / Project management | Project schedule | 1.8.1 | Interdependencies of tasks with equipment order and delivery times | 1 |  | 1
Chint | JBS | Workflow, Project Management Plan and Timelines | Project schedule / Project management | Project schedule | 1.8.1 | Key milestones to indicate that the progress in on schedule | 1 |  |  |  | 1
Chint | JBS | Workflow, Project Management Plan and Timelines | Project schedule / Project management | Project schedule | 1.8.1 | Teams, the number and skills of personnel to be deployed for each task | 1 |  | 1
Chint | JBS | Workflow, Project Management Plan and Timelines | Project schedule / Project management | Quality Assurance | 1.8.3 | Quality control of delivered modules | 1 |  |  | 1 | 1 |  |  |  |  | C
Chint | JBS | Workflow, Project Management Plan and Timelines | Project schedule / Project management | Quality Assurance | 1.8.3 | Inspection of equipment delivery | 1 |  |  | 1 | 1 |  |  |  |  | C
Chint | JBS | Workflow, Project Management Plan and Timelines | Project schedule / Project management | Quality Assurance | 1.8.3 | Milestones for the completion of civil, mechanical, and electrical works | 1 |  |  |  | 1 |  |  |  | dobble to 105 and 111 | C
Chint | JBS | Workflow, Project Management Plan and Timelines | Project schedule / Project management | Quality Assurance | 1.8.3 | Risk analysis and mitigation plan | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  |  |  | C | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria.
Chint | JBS | Workflow, Project Management Plan and Timelines | Project schedule / Project management | Quality Assurance | 1.8.3 | System acceptance QA procedure by the Employer | 1 |  |  |  | 1 | Unclear: We do not understand your proposal, please detail your proposal. Especially confirm that you are compliant with our requested criteria. |  |  |  | C | Unclear: We do not understand your proposal, please detail your proposal. Especially confirm that you are compliant with our requested criteria.
Chint | JBS | Labelling | General items | Labelling | 1.26 | the ID numbering / coding system shall allow unique identification of all components and be understandable | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  | Cannot be evaluated at this stage |  | C | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria.
Chint | JBS | Labelling | General items | Labelling | 1.26 | Tags shall be weather and UV resistant. | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  | Cannot be evaluated at this stage |  | C | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria.
Chint | JBS | Labelling | General items | Labelling | 1.26 | The ID’s shall correspond to all drawings, plant documentation and control system. | 1 |  |  |  | 1 |  |  | Cannot be evaluated at this stage |  | C
Chint | JBS | Power plant documentation | Power plant documentation | Quality Assurance | 1.27.1 | The Bidder shall confirm that the complete as-built documentation of the plant will be provided in compliance with IEC 62446. Additionally all module serial numbers shall be listed with their individual location. | 1 |  |  |  | 1 |  |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  | C
Chint | JBS | Power plant documentation | Power plant documentation | Quality Assurance | 1.27.1 | Flash report list of all modules shall be provided in digital form. | 1 |  |  |  | 1 |  |  |  |  | C
Chint | JBS | Power plant documentation | Spare parts | Warranty | 1.27.2 | The successful bidder shall provide all warranty spares for a warranty period of 5 years. | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  |  |  | C | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria.
Chint | JBS | Equipment guarantees | Warranty | Guarantees | 1.28 | The overall Guarantee and Power Plant Acceptance Procedures required for the Project are described in Sections 1.3, 1.4, 1.14, 1.18 and Schedule D and shall be met. | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  | Link |  | C | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria.
Chint | JBS | Equipment guarantees | Modules | Guarantees | 1.28.1 | The Successful bidder shall provide a Module warranty of at least 10 years. The performance warranty of the module shall be linear with a fixed factor over 25 years. | 1 | Page 21 | 1 |  |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  | To be discussed |  |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria.
Chint | JBS | Equipment guarantees | Inverter | Guarantees | 1.28.2 | The Successful Bidder shall provide an Inverter warranty of at least 5 years. A spare parts warranty shall be included for the 25 years operational period. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Chint | JBS | Equipment guarantees | Mounting | Guarantees | 1.28.3 | The Successful Bidder shall provide a product warranty for the structure of at least 10 years. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Chint | JBS | Equipment guarantees | Warranty | Guarantees | 1.28.4, 1.6 | A detailed list of all guarantee conditions for the main equipments (beside modules and inverters) shall be provided by the Successful Bidder with the technical offer. The product warranty shall be at least 5 years. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Chint | JBS | Miscellaneous | Auxiliary systems | Power supply | 1.29.1 | An off-grid power station may need to be provided by the Bidder for commencing the work. Diesel generators shall be arranged by the bidder on its own. | 1 | Page 116 | 1 |  |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  |  |  |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria.
Chint | JBS | Miscellaneous | Project schedule / Project management | Specific Requirements | 1.29.9 | The Bidder shall submit an organizational chart illustrating management and functional relationships among all project team members including consultants, sub-contractors and vendors at each significant stage of the work, such as permitting, design, construction, testing and commissioning and O&M. | 1 | Page 38/39 | 1 |  |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  |  |  |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria.
Tbea | JBS | System PR Specification | System PR | O&M | 1.5.2 | The target PR specification at the time of commissioning the System is equal to or greater than 0.75 (75%). | 1 | page 77 -78 |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  |  |  |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria.
Tbea | JBS | System PR Specification | System PR | Losses included in PR calculation | 1.5.4 | Module Array (temperature dependence, soiling, low light inefficiency, shading, mismatches in array) | 1 | page 77 -78 |  | 1 | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | Shading and IAM losses missing | We don’t understand the question. Kindly clarify. | we want to see these losses specified. Thos need to be aligned with O+M Startegy and System composition | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Tbea | JBS | System PR Specification | System PR | Losses included in PR calculation | 1.5.4 | Inverter (operating efficiency, operating voltage variations, power/voltage levels) | 1 | page 77 -78 | 1 |  |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  | We don’t understand the question. Kindly clarify. | see relevant chapter 1.5.4 List of technical losses that make the PR |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria.
Tbea | JBS | System PR Specification | System PR | Losses included in PR calculation | 1.5.4 | Transformer losses | 1 | page 77 -78 | 1 |  |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  | We don’t understand the question. Kindly clarify. | see relevant chapter 1.5.4 List of technical losses that make the PR |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria.
Tbea | JBS | System PR Specification | System PR | Losses included in PR calculation | 1.5.4 | Ohmic losses in cables | 1 | page 77 -78 | 1 |  |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  | We don’t understand the question. Kindly clarify. | see relevant chapter 1.5.4 List of technical losses that make the PR |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria.
Tbea | JBS | System PR Specification | System PR | Losses included in PR calculation | 1.5.4 | Auxiliary loads | 1 | page 77 -78 |  | 1 | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | Nicht berücksichtigt | We don’t understand the question. Kindly clarify. | see relevant chapter 1.5.4 List of "losses" = auxilary loads from PV Energy that make the PR | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Tbea | JBS | Basic Scope of Supply | General items | Specific Requirements | 1.6 | The maximum DC voltage shall not exceed 1500 V | 1 |  | 1 |  |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  |  |  |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria.
Tbea | JBS | Basic Scope of Supply | General items | Specific Requirements | 1.6 | The required AC voltage / frequency at grid connection shall 132 kV/50 Hz | 1 |  | 1 |  |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  |  |  |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria.
Tbea | JBS | Basic Scope of Supply | Warranty | Quality Assurance | 1.6 | The Product Warranties shall be given for a duration of at least 5 years | 1 | page 83 | 1 | G |  |  |  | Cannot be evaluated at this stage. Only to be checked in list of deviations.
Tbea | JBS | Physical layout | System PR | Specific Requirements | 1.7.1, 1.1.8 | Layout calculations of predicted kWh over the system lifetime and PR using the tool PVSyst V5.62 or higher | 1 | page 76 | 1 |  |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  |  |  |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria.
Tbea | JBS | Physical layout | System PR | Specific Requirements | 1.7.1 | Provide a report using Solar GIS data provided by the Employer | 1 | page 75 | 1 |  |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  | Replace 'Report' with ' PV-Syst report'. | 'Report' is original wording in ER in 1.7.1 |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria.
Tbea | JBS | Physical layout | Layout | Specific Requirements | 1.7.2 | Provide a schematic electrical Single Line Diagram (SLD) of the entire System layout from the modules to the grid-connection, identifying and listing all of the following DC and AC components. | 1 | page 85 | 1
Tbea | JBS | Physical layout | Layout | Specific Requirements | 1.7.2 | The system design shall be such as to ensure ease of maintenance and a multiple ring main unit (RMU) philosophy (on MV level) must be followed for circuit breaker configuration. | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  |  |  | U | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria.
Tbea | JBS | Physical layout | Physical layout plan | Specific Requirements | 1.7.7 | Floor plans and elevations for all buildings, housing units, containers on site: e.g. , substations, the SCADA operational room, inverters, O&M, storage facilities | 1 | page 1124 | 1
Tbea | JBS | Physical layout | Physical layout plan | Specific Requirements | 1.7.7 | Detailed view of the distribution of inverters and connections to the PV string/array | 1 | page 84 | 1
Tbea | JBS | Physical layout | Physical layout plan | Specific Requirements | 1.7.7 | Detailed top view of the PV mounting structure, including module sizes and spacing between the module rows | 1 | page 145/146 | 1
Tbea | JBS | Physical layout | Physical layout plan | Specific Requirements | 1.7.7 | Detailed side and front view of the PV mounting structure | 1 | page 145/146 | 1 |  |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  |  |  |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria.
Tbea | JBS | Physical layout | Physical layout plan | Specific Requirements | 1.7.7 | Detailed top view of electrical cabling interconnections | 1 | page 134 | 1
Tbea | JBS | Physical layout | Physical layout plan | Specific Requirements | 1.7.7 | Location of the system metering and grid connection point | 1 | page 85 | 1 |  |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  |  |  |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria.
Tbea | JBS | Physical layout | Auxiliary equipment | Specific Requirements | 1.7.8 | Provide complete indicating, regulating, controlling, protecting and interlocking equipment necessary for safe and efficient operation of the plant and substation, including complete protection scheme. | 1 | page 85 | 1 |  |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  |  |  |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria.
Tbea | JBS | Physical layout | Auxiliary equipment | Specific Requirements | 1.7.8 | The outline of protection schemes shall be shown on the single line diagram (SLD) | 1 | page 85 | 1 |  |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  |  |  |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria.
Tbea | JBS | Physical layout | Auxiliary equipment | Specific Requirements | 1.7.8 | All parts of the installation are covered by two high speed protection schemes, which shall be independent to avoid common mode failures | 1 | page 85 | 1 |  |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  |  |  |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria.
Tbea | JBS | Physical layout | Auxiliary equipment | Specific Requirements | 1.7.8 | The Bidder shall include a fire prevention and response plan | 1 | page 86 |  |  | 1 | General understanding: expressions like "shall", "shall be supplied with", "has to be", "must be" have the meaning of "will be delivered"? Please confirm. |  |  |  | G | General understanding: expressions like "shall", "shall be supplied with", "has to be", "must be" have the meaning of "will be delivered"? Please confirm.
Tbea | JBS | Physical layout | Auxiliary equipment | Specific Requirements | 1.7.8 | The fire prevention and response plan shall include a fire alarm und detection system with a main panel in the control room | 1 | page 87 |  |  | 1 | General understanding: expressions like "shall", "shall be supplied with", "has to be", "must be" have the meaning of "will be delivered"? Please confirm. |  |  |  | G | General understanding: expressions like "shall", "shall be supplied with", "has to be", "must be" have the meaning of "will be delivered"? Please confirm.
Tbea | JBS | Physical layout | Auxiliary equipment | Specific Requirements | 1.7.9 | The documentation includes clearly labelled objects and figures annotated in English language. | 1
Tbea | JBS | Physical layout | Auxiliary equipment | Specific Requirements | 1.7.9 | The scope of the documentation shall cover at least the requirements of IEC 62446. | 1 | page 87 |  |  | 1 | General understanding: expressions like "shall", "shall be supplied with", "has to be", "must be" have the meaning of "will be delivered"? Please confirm. |  |  |  | G | General understanding: expressions like "shall", "shall be supplied with", "has to be", "must be" have the meaning of "will be delivered"? Please confirm.
Tbea | JBS | Workflow, Project Management Plan and Timelines | Project schedule / Project management | Project schedule | 1.8.1 | Provide installation schedule in compliance with sub-clause 8.2 of Particular Conditions (Time for Completion is 225 days after Commencement Date). | 1 | page 44-45 | 1 |  |  |  |  | Find sub-clause 8.2 of Particular Conditions
Tbea | JBS | Workflow, Project Management Plan and Timelines | Project schedule / Project management | Project schedule | 1.8.1 | Provide work breakdown structures, activity decomposition and sequencing and dependability with the baseline schedule clearly showing the critical path | 1 | page 44-45 | 1
Tbea | JBS | Workflow, Project Management Plan and Timelines | Project schedule / Project management | Project schedule | 1.8.1 | Schedule of tasks | 1 | page 44-45 | 1
Tbea | JBS | Workflow, Project Management Plan and Timelines | Project schedule / Project management | Project schedule | 1.8.1 | Interdependencies between the tasks | 1 | page 44-45 | 1
Tbea | JBS | Workflow, Project Management Plan and Timelines | Project schedule / Project management | Project schedule | 1.8.1 | Interdependencies of tasks with equipment order and delivery times | 1 | page 44-45 | 1
Tbea | JBS | Workflow, Project Management Plan and Timelines | Project schedule / Project management | Project schedule | 1.8.1 | Key milestones to indicate that the progress in on schedule | 1 | page 44-45 | 1
Tbea | JBS | Workflow, Project Management Plan and Timelines | Project schedule / Project management | Project schedule | 1.8.1 | Teams, the number and skills of personnel to be deployed for each task | 1 | Page 13-41 | 1
Tbea | JBS | Workflow, Project Management Plan and Timelines | Project schedule / Project management | Quality Assurance | 1.8.3 | Quality control of delivered modules | 1 | Page 93, 1018 | 1
Tbea | JBS | Workflow, Project Management Plan and Timelines | Project schedule / Project management | Quality Assurance | 1.8.3 | Inspection of equipment delivery | 1 | Page 1018 | 1
Tbea | JBS | Workflow, Project Management Plan and Timelines | Project schedule / Project management | Quality Assurance | 1.8.3 | Milestones for the completion of civil, mechanical, and electrical works | 1 | page 1025 | 1 | [5 empty] | dobble to 105 and 111
Tbea | JBS | Workflow, Project Management Plan and Timelines | Project schedule / Project management | Quality Assurance | 1.8.3 | Risk analysis and mitigation plan | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Tbea | JBS | Workflow, Project Management Plan and Timelines | Project schedule / Project management | Quality Assurance | 1.8.3 | System acceptance QA procedure by the Employer | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Tbea | JBS | Labelling | General items | Labelling | 1.26 | the ID numbering / coding system shall allow unique identification of all components and be understandable | 1 |  |  |  | 1 | General understanding: expressions like "shall", "shall be supplied with", "has to be", "must be" have the meaning of "will be delivered"? Please confirm. |  | Cannot be evaluated at this stage |  | G | General understanding: expressions like "shall", "shall be supplied with", "has to be", "must be" have the meaning of "will be delivered"? Please confirm.
Tbea | JBS | Labelling | General items | Labelling | 1.26 | Tags shall be weather and UV resistant. | 1 |  |  |  | 1 | General understanding: expressions like "shall", "shall be supplied with", "has to be", "must be" have the meaning of "will be delivered"? Please confirm. |  | Cannot be evaluated at this stage |  | G | General understanding: expressions like "shall", "shall be supplied with", "has to be", "must be" have the meaning of "will be delivered"? Please confirm.
Tbea | JBS | Labelling | General items | Labelling | 1.26 | The ID’s shall correspond to all drawings, plant documentation and control system. | 1 |  |  |  | 1 | General understanding: expressions like "shall", "shall be supplied with", "has to be", "must be" have the meaning of "will be delivered"? Please confirm. |  | Cannot be evaluated at this stage |  | G | General understanding: expressions like "shall", "shall be supplied with", "has to be", "must be" have the meaning of "will be delivered"? Please confirm.
Tbea | JBS | Power plant documentation | Power plant documentation | Quality Assurance | 1.27.1 | The Bidder shall confirm that the complete as-built documentation of the plant will be provided in compliance with IEC 62446. Additionally all module serial numbers shall be listed with their individual location. | 1 |  |  |  | 1 | General understanding: expressions like "shall", "shall be supplied with", "has to be", "must be" have the meaning of "will be delivered"? Please confirm. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  | G | General understanding: expressions like "shall", "shall be supplied with", "has to be", "must be" have the meaning of "will be delivered"? Please confirm.
Tbea | JBS | Power plant documentation | Power plant documentation | Quality Assurance | 1.27.1 | Flash report list of all modules shall be provided in digital form. | 1 |  |  |  | 1 | General understanding: expressions like "shall", "shall be supplied with", "has to be", "must be" have the meaning of "will be delivered"? Please confirm. |  |  |  | G | General understanding: expressions like "shall", "shall be supplied with", "has to be", "must be" have the meaning of "will be delivered"? Please confirm.
Tbea | JBS | Power plant documentation | Spare parts | Warranty | 1.27.2 | The successful bidder shall provide all warranty spares for a warranty period of 5 years. | 1 |  |  |  | 1 | General understanding: expressions like "shall", "shall be supplied with", "has to be", "must be" have the meaning of "will be delivered"? Please confirm. |  |  |  | G | General understanding: expressions like "shall", "shall be supplied with", "has to be", "must be" have the meaning of "will be delivered"? Please confirm.
Tbea | JBS | Equipment guarantees | Warranty | Guarantees | 1.28 | The overall Guarantee and Power Plant Acceptance Procedures required for the Project are described in Sections 1.3, 1.4, 1.14, 1.18 and Schedule D and shall be met. | 1 |  |  |  | 1 | General understanding: expressions like "shall", "shall be supplied with", "has to be", "must be" have the meaning of "will be delivered"? Please confirm. |  | Link |  | G | General understanding: expressions like "shall", "shall be supplied with", "has to be", "must be" have the meaning of "will be delivered"? Please confirm.
Tbea | JBS | Equipment guarantees | Modules | Guarantees | 1.28.1 | The Successful bidder shall provide a Module warranty of at least 10 years. The performance warranty of the module shall be linear with a fixed factor over 25 years. | 1 |  |  |  | 1 | General understanding: expressions like "shall", "shall be supplied with", "has to be", "must be" have the meaning of "will be delivered"? Please confirm. |  | To be discussed |  | G | General understanding: expressions like "shall", "shall be supplied with", "has to be", "must be" have the meaning of "will be delivered"? Please confirm.
Tbea | JBS | Equipment guarantees | Inverter | Guarantees | 1.28.2 | The Successful Bidder shall provide an Inverter warranty of at least 5 years. A spare parts warranty shall be included for the 25 years operational period. | 1 |  |  |  | 1 | General understanding: expressions like "shall", "shall be supplied with", "has to be", "must be" have the meaning of "will be delivered"? Please confirm. |  |  |  | G | General understanding: expressions like "shall", "shall be supplied with", "has to be", "must be" have the meaning of "will be delivered"? Please confirm.
Tbea | JBS | Equipment guarantees | Mounting | Guarantees | 1.28.3 | The Successful Bidder shall provide a product warranty for the structure of at least 10 years. | 1 |  |  |  | 1 | General understanding: expressions like "shall", "shall be supplied with", "has to be", "must be" have the meaning of "will be delivered"? Please confirm. |  |  |  | G | General understanding: expressions like "shall", "shall be supplied with", "has to be", "must be" have the meaning of "will be delivered"? Please confirm.
Tbea | JBS | Equipment guarantees | Warranty | Guarantees | 1.28.4, 1.6 | A detailed list of all guarantee conditions for the main equipments (beside modules and inverters) shall be provided by the Successful Bidder with the technical offer. The product warranty shall be at least 5 years. | 1 |  |  |  | 1 | General understanding: expressions like "shall", "shall be supplied with", "has to be", "must be" have the meaning of "will be delivered"? Please confirm. |  |  |  | G | General understanding: expressions like "shall", "shall be supplied with", "has to be", "must be" have the meaning of "will be delivered"? Please confirm.
Tbea | JBS | Miscellaneous | Auxiliary systems | Power supply | 1.29.1 | An off-grid power station may need to be provided by the Bidder for commencing the work. Diesel generators shall be arranged by the bidder on its own. | 1 | page 51 | 1
Tbea | JBS | Miscellaneous | Project schedule / Project management | Specific Requirements | 1.29.9 | The Bidder shall submit an organizational chart illustrating management and functional relationships among all project team members including consultants, sub-contractors and vendors at each significant stage of the work, such as permitting, design, construction, testing and commissioning and O&M. | 1 | page 14 | 1
Zte | JBS | System PR Specification | System PR | O&M | 1.5.2 | The target PR specification at the time of commissioning the System is equal to or greater than 0.75 (75%). | 1 | 1. SoC to Bidding Document 30-01-14.pdf Page 107 |  |  | 1
Zte | JBS | System PR Specification | System PR | Losses included in PR calculation | 1.5.4 | Module Array (temperature dependence, soiling, low light inefficiency, shading, mismatches in array) | 1 | 1. SoC to Bidding Document 30-01-14.pdf Page 114 |  |  | 1 |  | keine Verschattung gerechnet, Soiling zu gering, Qualitätsaufschlag eindeutig zu hoch. | We don’t understand the question. Kindly clarify. | we want to see these losses specified. Thos need to be aligned with O+M Startegy and System composition
Zte | JBS | System PR Specification | System PR | Losses included in PR calculation | 1.5.4 | Inverter (operating efficiency, operating voltage variations, power/voltage levels) | 1 | 1. SoC to Bidding Document 30-01-14.pdf Page 114 | 1 |  |  |  |  | We don’t understand the question. Kindly clarify. | see relevant chapter 1.5.4 List of technical losses that make the PR
Zte | JBS | System PR Specification | System PR | Losses included in PR calculation | 1.5.4 | Transformer losses | 1 | 1. SoC to Bidding Document 30-01-14.pdf Page 114 | 1 |  |  |  | Trocken-Transfomer Datenblatt nicht vorhanden. | We don’t understand the question. Kindly clarify. | see relevant chapter 1.5.4 List of technical losses that make the PR
Zte | JBS | System PR Specification | System PR | Losses included in PR calculation | 1.5.4 | Ohmic losses in cables | 1 | 1. SoC to Bidding Document 30-01-14.pdf Page 114 |  |  | 1 |  |  | We don’t understand the question. Kindly clarify. | see relevant chapter 1.5.4 List of technical losses that make the PR
Zte | JBS | System PR Specification | System PR | Losses included in PR calculation | 1.5.4 | Auxiliary loads | 1 |  |  | 1 | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | nicht berücksichtigt | We don’t understand the question. Kindly clarify. | see relevant chapter 1.5.4 List of "losses" = auxilary loads from PV Energy that make the PR | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Zte | JBS | Basic Scope of Supply | General items | Specific Requirements | 1.6 | The maximum DC voltage shall not exceed 1500 V | 1 |  | 1
Zte | JBS | Basic Scope of Supply | General items | Specific Requirements | 1.6 | The required AC voltage / frequency at grid connection shall 132 kV/50 Hz | 1 |  | 1
Zte | JBS | Basic Scope of Supply | Warranty | Quality Assurance | 1.6 | The Product Warranties shall be given for a duration of at least 5 years | 1 | 1. SoC to Bidding Document 30-01-14.pdf Page 101 | 1 |  |  |  |  | Cannot be evaluated at this stage. Only to be checked in list of deviations.
Zte | JBS | Physical layout | System PR | Specific Requirements | 1.7.1, 1.1.8 | Layout calculations of predicted kWh over the system lifetime and PR using the tool PVSyst V5.62 or higher | 1 | 1. SoC to Bidding Document 30-01-14.pdf Page 106 | 1
Zte | JBS | Physical layout | System PR | Specific Requirements | 1.7.1 | Provide a report using Solar GIS data provided by the Employer | 1 | 1. SoC to Bidding Document 30-01-14.pdf Page 101 | 1 |  |  |  |  | Replace 'Report' with ' PV-Syst report'. | 'Report' is original wording in ER in 1.7.1
Zte | JBS | Physical layout | Layout | Specific Requirements | 1.7.2 | Provide a schematic electrical Single Line Diagram (SLD) of the entire System layout from the modules to the grid-connection, identifying and listing all of the following DC and AC components. | 1 | P004 Single line diagram.pdf | 1
Zte | JBS | Physical layout | Layout | Specific Requirements | 1.7.2 | The system design shall be such as to ensure ease of maintenance and a multiple ring main unit (RMU) philosophy (on MV level) must be followed for circuit breaker configuration. | 1 | P004 Single line diagram.pdf | 1
Zte | JBS | Physical layout | Physical layout plan | Specific Requirements | 1.7.7 | Floor plans and elevations for all buildings, housing units, containers on site: e.g. , substations, the SCADA operational room, inverters, O&M, storage facilities | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  |  |  | U | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria.
Zte | JBS | Physical layout | Physical layout plan | Specific Requirements | 1.7.7 | Detailed view of the distribution of inverters and connections to the PV string/array | 1 | P001 100MW PV Power plant layout.pdf, P006 1 MWp PV generation subsystem.pdf | 1
Zte | JBS | Physical layout | Physical layout plan | Specific Requirements | 1.7.7 | Detailed top view of the PV mounting structure, including module sizes and spacing between the module rows | 1 | P002 PV module support structure.pdf, P003 PV array layout.pdf | 1
Zte | JBS | Physical layout | Physical layout plan | Specific Requirements | 1.7.7 | Detailed side and front view of the PV mounting structure | 1 | P002 PV module support structure.pdf | 1 |  |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  |  |  |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria.
Zte | JBS | Physical layout | Physical layout plan | Specific Requirements | 1.7.7 | Detailed top view of electrical cabling interconnections | 1 |  | 1 |  |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  |  |  |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria.
Zte | JBS | Physical layout | Physical layout plan | Specific Requirements | 1.7.7 | Location of the system metering and grid connection point | 1 | P004 Single line diagram.pdf | 1 |  |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  |  |  |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria.
Zte | JBS | Physical layout | Auxiliary equipment | Specific Requirements | 1.7.8 | Provide complete indicating, regulating, controlling, protecting and interlocking equipment necessary for safe and efficient operation of the plant and substation, including complete protection scheme. | 1 | P004 Single line diagram.pdf | 1
Zte | JBS | Physical layout | Auxiliary equipment | Specific Requirements | 1.7.8 | The outline of protection schemes shall be shown on the single line diagram (SLD) | 1 |  | 1
Zte | JBS | Physical layout | Auxiliary equipment | Specific Requirements | 1.7.8 | All parts of the installation are covered by two high speed protection schemes, which shall be independent to avoid common mode failures | 1 | Technical Proposal of 100MW Solar Power Plant.pdfPate 17 | 1 |  |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  |  |  |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria.
Zte | JBS | Physical layout | Auxiliary equipment | Specific Requirements | 1.7.8 | The Bidder shall include a fire prevention and response plan | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Zte | JBS | Physical layout | Auxiliary equipment | Specific Requirements | 1.7.8 | The fire prevention and response plan shall include a fire alarm und detection system with a main panel in the control room | 1 | 1. SoC to Bidding Document 30-01-14.pdf Page 97 | 1
Zte | JBS | Physical layout | Auxiliary equipment | Specific Requirements | 1.7.9 | The documentation includes clearly labelled objects and figures annotated in English language. | 1 | 1. SoC to Bidding Document 30-01-14.pdf | 1
Zte | JBS | Physical layout | Auxiliary equipment | Specific Requirements | 1.7.9 | The scope of the documentation shall cover at least the requirements of IEC 62446. | 1 | 1. SoC to Bidding Document 30-01-14.pdf | 1
Zte | JBS | Workflow, Project Management Plan and Timelines | Project schedule / Project management | Project schedule | 1.8.1 | Provide installation schedule in compliance with sub-clause 8.2 of Particular Conditions (Time for Completion is 225 days after Commencement Date). | 1 | 1. Time Schedule for QA Soar Park.pdf | 1 |  |  |  |  | Find sub-clause 8.2 of Particular Conditions
Zte | JBS | Workflow, Project Management Plan and Timelines | Project schedule / Project management | Project schedule | 1.8.1 | Provide work breakdown structures, activity decomposition and sequencing and dependability with the baseline schedule clearly showing the critical path | 1 | 1. Time Schedule for QA Soar Park.pdf | 1
Zte | JBS | Workflow, Project Management Plan and Timelines | Project schedule / Project management | Project schedule | 1.8.1 | Schedule of tasks | 1 | 1. Time Schedule for QA Soar Park.pdf | 1
Zte | JBS | Workflow, Project Management Plan and Timelines | Project schedule / Project management | Project schedule | 1.8.1 | Interdependencies between the tasks | 1 | 1. Time Schedule for QA Soar Park.pdf | 1
Zte | JBS | Workflow, Project Management Plan and Timelines | Project schedule / Project management | Project schedule | 1.8.1 | Interdependencies of tasks with equipment order and delivery times | 1 | 1. Time Schedule for QA Soar Park.pdf | 1
Zte | JBS | Workflow, Project Management Plan and Timelines | Project schedule / Project management | Project schedule | 1.8.1 | Key milestones to indicate that the progress in on schedule | 1 | 1. Time Schedule for QA Soar Park.pdf | 1
Zte | JBS | Workflow, Project Management Plan and Timelines | Project schedule / Project management | Project schedule | 1.8.1 | Teams, the number and skills of personnel to be deployed for each task | 1 | Implementation proposal-0218.pdf |  |  | 1 | Unclear: We do not understand your proposal, please detail your proposal. Especially confirm that you are compliant with our requested criteria. |  |  |  |  | Unclear: We do not understand your proposal, please detail your proposal. Especially confirm that you are compliant with our requested criteria.
Zte | JBS | Workflow, Project Management Plan and Timelines | Project schedule / Project management | Quality Assurance | 1.8.3 | Quality control of delivered modules | 1 |  |  | 1 | 1 | Unclear: We do not understand your proposal, please detail your proposal. Especially confirm that you are compliant with our requested criteria. |  |  |  | C | Unclear: We do not understand your proposal, please detail your proposal. Especially confirm that you are compliant with our requested criteria.
Zte | JBS | Workflow, Project Management Plan and Timelines | Project schedule / Project management | Quality Assurance | 1.8.3 | Inspection of equipment delivery | 1 |  |  | 1 | 1 | Unclear: We do not understand your proposal, please detail your proposal. Especially confirm that you are compliant with our requested criteria. |  |  |  | C | Unclear: We do not understand your proposal, please detail your proposal. Especially confirm that you are compliant with our requested criteria.
Zte | JBS | Workflow, Project Management Plan and Timelines | Project schedule / Project management | Quality Assurance | 1.8.3 | Milestones for the completion of civil, mechanical, and electrical works | 1 |  |  | 1 | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  |  | dobble to 105 and 111 | C | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria.
Zte | JBS | Workflow, Project Management Plan and Timelines | Project schedule / Project management | Quality Assurance | 1.8.3 | Risk analysis and mitigation plan | 1 |  |  | 1 | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  |  |  | C
Zte | JBS | Workflow, Project Management Plan and Timelines | Project schedule / Project management | Quality Assurance | 1.8.3 | System acceptance QA procedure by the Employer | 1 |  |  | 1 | 1 |  |  |  |  | C
Zte | JBS | Labelling | General items | Labelling | 1.26 | the ID numbering / coding system shall allow unique identification of all components and be understandable | 1 | 1. SoC to Bidding Document 30-01-14.pdf | 1 |  |  |  |  | Cannot be evaluated at this stage
Zte | JBS | Labelling | General items | Labelling | 1.26 | Tags shall be weather and UV resistant. | 1 | 1. SoC to Bidding Document 30-01-14.pdf | 1 |  |  |  |  | Cannot be evaluated at this stage
Zte | JBS | Labelling | General items | Labelling | 1.26 | The ID’s shall correspond to all drawings, plant documentation and control system. | 1 | 1. SoC to Bidding Document 30-01-14.pdf | 1 |  |  |  |  | Cannot be evaluated at this stage
Zte | JBS | Power plant documentation | Power plant documentation | Quality Assurance | 1.27.1 | The Bidder shall confirm that the complete as-built documentation of the plant will be provided in compliance with IEC 62446. Additionally all module serial numbers shall be listed with their individual location. | 1 | 1. SoC to Bidding Document 30-01-14.pdf | 1 |  |  |  |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient?
Zte | JBS | Power plant documentation | Power plant documentation | Quality Assurance | 1.27.1 | Flash report list of all modules shall be provided in digital form. | 1 | 1. SoC to Bidding Document 30-01-14.pdf | 1
Zte | JBS | Power plant documentation | Spare parts | Warranty | 1.27.2 | The successful bidder shall provide all warranty spares for a warranty period of 5 years. | 1 | 1. SoC to Bidding Document 30-01-14.pdf | 1
Zte | JBS | Equipment guarantees | Warranty | Guarantees | 1.28 | The overall Guarantee and Power Plant Acceptance Procedures required for the Project are described in Sections 1.3, 1.4, 1.14, 1.18 and Schedule D and shall be met. | 1 | 1. SoC to Bidding Document 30-01-14.pdf | 1 |  |  |  |  | Link
Zte | JBS | Equipment guarantees | Modules | Guarantees | 1.28.1 | The Successful bidder shall provide a Module warranty of at least 10 years. The performance warranty of the module shall be linear with a fixed factor over 25 years. | 1 | 1. SoC to Bidding Document 30-01-14.pdf | 1 |  |  |  |  | To be discussed
Zte | JBS | Equipment guarantees | Inverter | Guarantees | 1.28.2 | The Successful Bidder shall provide an Inverter warranty of at least 5 years. A spare parts warranty shall be included for the 25 years operational period. | 1 | 1. SoC to Bidding Document 30-01-14.pdf | 1
Zte | JBS | Equipment guarantees | Mounting | Guarantees | 1.28.3 | The Successful Bidder shall provide a product warranty for the structure of at least 10 years. | 1 | 1. SoC to Bidding Document 30-01-14.pdf | 1
Zte | JBS | Equipment guarantees | Warranty | Guarantees | 1.28.4, 1.6 | A detailed list of all guarantee conditions for the main equipments (beside modules and inverters) shall be provided by the Successful Bidder with the technical offer. The product warranty shall be at least 5 years. | 1 | 1. SoC to Bidding Document 30-01-14.pdf | 1
Zte | JBS | Miscellaneous | Auxiliary systems | Power supply | 1.29.1 | An off-grid power station may need to be provided by the Bidder for commencing the work. Diesel generators shall be arranged by the bidder on its own. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Zte | JBS | Miscellaneous | Project schedule / Project management | Specific Requirements | 1.29.9 | The Bidder shall submit an organizational chart illustrating management and functional relationships among all project team members including consultants, sub-contractors and vendors at each significant stage of the work, such as permitting, design, construction, testing and commissioning and O&M. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Sumec | JBS | System PR Specification | System PR | O&M | 1.5.2 | The target PR specification at the time of commissioning the System is equal to or greater than 0.75 (75%). | 1 |  |  |  | 1 | The PR of 80.5% does not consider several parameter, see following items. Please calculate new.
Sumec | JBS | System PR Specification | System PR | Losses included in PR calculation | 1.5.4 | Module Array (temperature dependence, soiling, low light inefficiency, shading, mismatches in array) | 1 | Vol 1 page 294 ff |  |  | 1 | Please calculate new considering shading losses and low light inefficiency losses |  | We don’t understand the question. Kindly clarify. | we want to see these losses specified. Thos need to be aligned with O+M Startegy and System composition
Sumec | JBS | System PR Specification | System PR | Losses included in PR calculation | 1.5.4 | Inverter (operating efficiency, operating voltage variations, power/voltage levels) | 1 | Vol 1 page 296 ff | 1 |  |  |  |  | We don’t understand the question. Kindly clarify. | see relevant chapter 1.5.4 List of technical losses that make the PR
Sumec | JBS | System PR Specification | System PR | Losses included in PR calculation | 1.5.4 | Transformer losses | 1 | Vol 1 page 294 ff | 1 |  |  |  |  | We don’t understand the question. Kindly clarify. | see relevant chapter 1.5.4 List of technical losses that make the PR
Sumec | JBS | System PR Specification | System PR | Losses included in PR calculation | 1.5.4 | Ohmic losses in cables | 1 | Vol 1 page 294 ff | 1 |  |  |  |  | We don’t understand the question. Kindly clarify. | see relevant chapter 1.5.4 List of technical losses that make the PR
Sumec | JBS | System PR Specification | System PR | Losses included in PR calculation | 1.5.4 | Auxiliary loads | 1 | Vol 1 page 296 ff | 1 |  |  |  |  | We don’t understand the question. Kindly clarify. | see relevant chapter 1.5.4 List of "losses" = auxilary loads from PV Energy that make the PR
Sumec | JBS | Basic Scope of Supply | General items | Specific Requirements | 1.6 | The maximum DC voltage shall not exceed 1500 V | 1 | Volume 1 page 8 | 1
Sumec | JBS | Basic Scope of Supply | General items | Specific Requirements | 1.6 | The required AC voltage / frequency at grid connection shall 132 kV/50 Hz | 1 | Vol 1page 311 ff | 1
Sumec | JBS | Basic Scope of Supply | Warranty | Quality Assurance | 1.6 | The Product Warranties shall be given for a duration of at least 5 years | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Cannot be evaluated at this stage. Only to be checked in list of deviations.
Sumec | JBS | Physical layout | System PR | Specific Requirements | 1.7.1, 1.1.8 | Layout calculations of predicted kWh over the system lifetime and PR using the tool PVSyst V5.62 or higher | 1 |  | 1
Sumec | JBS | Physical layout | System PR | Specific Requirements | 1.7.1 | Provide a report using Solar GIS data provided by the Employer | 1 | Vol 1page 249 | 1 |  |  |  |  | Replace 'Report' with ' PV-Syst report'. | 'Report' is original wording in ER in 1.7.1
Sumec | JBS | Physical layout | Layout | Specific Requirements | 1.7.2 | Provide a schematic electrical Single Line Diagram (SLD) of the entire System layout from the modules to the grid-connection, identifying and listing all of the following DC and AC components. | 1 | Vol 3page 4 | 1
Sumec | JBS | Physical layout | Layout | Specific Requirements | 1.7.2 | The system design shall be such as to ensure ease of maintenance and a multiple ring main unit (RMU) philosophy (on MV level) must be followed for circuit breaker configuration. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Sumec | JBS | Physical layout | Physical layout plan | Specific Requirements | 1.7.7 | Floor plans and elevations for all buildings, housing units, containers on site: e.g. , substations, the SCADA operational room, inverters, O&M, storage facilities | 1 | Vol 3page 15 | 1
Sumec | JBS | Physical layout | Physical layout plan | Specific Requirements | 1.7.7 | Detailed view of the distribution of inverters and connections to the PV string/array | 1 | Vol 3page 4 | 1
Sumec | JBS | Physical layout | Physical layout plan | Specific Requirements | 1.7.7 | Detailed top view of the PV mounting structure, including module sizes and spacing between the module rows | 1 | Vol 3page 21 |  |  | 1 | Is the row distance calculated with the lowest sun elevation angle of the year?
Sumec | JBS | Physical layout | Physical layout plan | Specific Requirements | 1.7.7 | Detailed side and front view of the PV mounting structure | 1 | Vol 3page 21 | 1
Sumec | JBS | Physical layout | Physical layout plan | Specific Requirements | 1.7.7 | Detailed top view of electrical cabling interconnections | 1 |  | 1
Sumec | JBS | Physical layout | Physical layout plan | Specific Requirements | 1.7.7 | Location of the system metering and grid connection point | 1 |  | 1
Sumec | JBS | Physical layout | Auxiliary equipment | Specific Requirements | 1.7.8 | Provide complete indicating, regulating, controlling, protecting and interlocking equipment necessary for safe and efficient operation of the plant and substation, including complete protection scheme. | 1 | Vol 3page 9 | 1
Sumec | JBS | Physical layout | Auxiliary equipment | Specific Requirements | 1.7.8 | The outline of protection schemes shall be shown on the single line diagram (SLD) | 1 |  | 1
Sumec | JBS | Physical layout | Auxiliary equipment | Specific Requirements | 1.7.8 | All parts of the installation are covered by two high speed protection schemes, which shall be independent to avoid common mode failures | 1 | Vol 3page 9 | 1
Sumec | JBS | Physical layout | Auxiliary equipment | Specific Requirements | 1.7.8 | The Bidder shall include a fire prevention and response plan | 1 | Vol 1 page 161 ff; Vol 2 page 320 ff | 1
Sumec | JBS | Physical layout | Auxiliary equipment | Specific Requirements | 1.7.8 | The fire prevention and response plan shall include a fire alarm und detection system with a main panel in the control room | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Sumec | JBS | Physical layout | Auxiliary equipment | Specific Requirements | 1.7.9 | The documentation includes clearly labelled objects and figures annotated in English language. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Sumec | JBS | Physical layout | Auxiliary equipment | Specific Requirements | 1.7.9 | The scope of the documentation shall cover at least the requirements of IEC 62446. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Sumec | JBS | Workflow, Project Management Plan and Timelines | Project schedule / Project management | Project schedule | 1.8.1 | Provide installation schedule in compliance with sub-clause 8.2 of Particular Conditions (Time for Completion is 225 days after Commencement Date). | 1 | Vol 1 page 170 | 1 |  |  |  | 215 Tage | Find sub-clause 8.2 of Particular Conditions |  |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria.
Sumec | JBS | Workflow, Project Management Plan and Timelines | Project schedule / Project management | Project schedule | 1.8.1 | Provide work breakdown structures, activity decomposition and sequencing and dependability with the baseline schedule clearly showing the critical path | 1 | Vol 1 page 170 | 1
Sumec | JBS | Workflow, Project Management Plan and Timelines | Project schedule / Project management | Project schedule | 1.8.1 | Schedule of tasks | 1 | Vol 1 page 171 ff | 1
Sumec | JBS | Workflow, Project Management Plan and Timelines | Project schedule / Project management | Project schedule | 1.8.1 | Interdependencies between the tasks | 1 | Vol 1 page 170 | 1
Sumec | JBS | Workflow, Project Management Plan and Timelines | Project schedule / Project management | Project schedule | 1.8.1 | Interdependencies of tasks with equipment order and delivery times | 1 |  |  |  | 1 | Please provide a plan with equipment ordering.
Sumec | JBS | Workflow, Project Management Plan and Timelines | Project schedule / Project management | Project schedule | 1.8.1 | Key milestones to indicate that the progress in on schedule | 1 | Vol 1 page 170 | 1
Sumec | JBS | Workflow, Project Management Plan and Timelines | Project schedule / Project management | Project schedule | 1.8.1 | Teams, the number and skills of personnel to be deployed for each task | 1 | Vol 1 page 48 ff | 1
Sumec | JBS | Workflow, Project Management Plan and Timelines | Project schedule / Project management | Quality Assurance | 1.8.3 | Quality control of delivered modules | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Sumec | JBS | Workflow, Project Management Plan and Timelines | Project schedule / Project management | Quality Assurance | 1.8.3 | Inspection of equipment delivery | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Sumec | JBS | Workflow, Project Management Plan and Timelines | Project schedule / Project management | Quality Assurance | 1.8.3 | Milestones for the completion of civil, mechanical, and electrical works | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  | dobble to 105 and 111 | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Sumec | JBS | Workflow, Project Management Plan and Timelines | Project schedule / Project management | Quality Assurance | 1.8.3 | Risk analysis and mitigation plan | 1 | Vol 1 page 133 | 1
Sumec | JBS | Workflow, Project Management Plan and Timelines | Project schedule / Project management | Quality Assurance | 1.8.3 | System acceptance QA procedure by the Employer | 1 | Vol 1 page 142 |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Sumec | JBS | Labelling | General items | Labelling | 1.26 | the ID numbering / coding system shall allow unique identification of all components and be understandable | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Cannot be evaluated at this stage |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Sumec | JBS | Labelling | General items | Labelling | 1.26 | Tags shall be weather and UV resistant. | 1 | Vol 1 page 99 | 1 |  |  |  |  | Cannot be evaluated at this stage
Sumec | JBS | Labelling | General items | Labelling | 1.26 | The ID’s shall correspond to all drawings, plant documentation and control system. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Cannot be evaluated at this stage |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Sumec | JBS | Power plant documentation | Power plant documentation | Quality Assurance | 1.27.1 | The Bidder shall confirm that the complete as-built documentation of the plant will be provided in compliance with IEC 62446. Additionally all module serial numbers shall be listed with their individual location. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Sumec | JBS | Power plant documentation | Power plant documentation | Quality Assurance | 1.27.1 | Flash report list of all modules shall be provided in digital form. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Sumec | JBS | Power plant documentation | Spare parts | Warranty | 1.27.2 | The successful bidder shall provide all warranty spares for a warranty period of 5 years. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Sumec | JBS | Equipment guarantees | Warranty | Guarantees | 1.28 | The overall Guarantee and Power Plant Acceptance Procedures required for the Project are described in Sections 1.3, 1.4, 1.14, 1.18 and Schedule D and shall be met. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Link |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Sumec | JBS | Equipment guarantees | Modules | Guarantees | 1.28.1 | The Successful bidder shall provide a Module warranty of at least 10 years. The performance warranty of the module shall be linear with a fixed factor over 25 years. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | To be discussed |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Sumec | JBS | Equipment guarantees | Inverter | Guarantees | 1.28.2 | The Successful Bidder shall provide an Inverter warranty of at least 5 years. A spare parts warranty shall be included for the 25 years operational period. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Sumec | JBS | Equipment guarantees | Mounting | Guarantees | 1.28.3 | The Successful Bidder shall provide a product warranty for the structure of at least 10 years. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Sumec | JBS | Equipment guarantees | Warranty | Guarantees | 1.28.4, 1.6 | A detailed list of all guarantee conditions for the main equipments (beside modules and inverters) shall be provided by the Successful Bidder with the technical offer. The product warranty shall be at least 5 years. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Sumec | JBS | Miscellaneous | Auxiliary systems | Power supply | 1.29.1 | An off-grid power station may need to be provided by the Bidder for commencing the work. Diesel generators shall be arranged by the bidder on its own. | 1 | Vol 1 Page 37 | 1
Sumec | JBS | Miscellaneous | Project schedule / Project management | Specific Requirements | 1.29.9 | The Bidder shall submit an organizational chart illustrating management and functional relationships among all project team members including consultants, sub-contractors and vendors at each significant stage of the work, such as permitting, design, construction, testing and commissioning and O&M. | 1 | Vol 1 Page 35, 45 ff | 1
Chint | GD | Scope of the Bid | General items | Specific Requirements | 1.1.2 | The Offer shall include a list of all vendors and/or sub-contractors for major equipment. | 1 |  | 1 | [6 empty] | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  | 1 |  | Pass
Chint | GD | Scope of the Bid | General items | Quality Assurance | 1.1.3 | Defect components consequences: If one tested sample fails in one criterion, all items of the same category will be regarded as failed and rejected. | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  | Only to be checked in list of deviations. | yes, we need to be sure that they comply as for most of the critera | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | 1 | 1 | Open
Chint | GD | Scope of the Bid | General items | Guarantees | 1.1.5 | Energy Purchase Agreement (EPA) practices are followed | 1 |  |  |  | 1 | Important reasons: due to current uncertainty of the criteria we accept an open status. Please clarify that yo acknowledge the criteria and comply unless a reason of high importance will not allow you you to comply. In such a situation the parties will seek to agree a compromise. |  | This cannot be evaluated at this stage. | we need a sentence that it should and can only be disregarded for important reasons | Unclear: We do not understand your proposal, please detail your proposal. Especially confirm that you are compliant with our requested criteria. |  | 1 |  | Open
Chint | GD | Scope of the Bid | Layout | Guarantees | 1.1.6 | The bidder confirms that the system complies with all applicable requirements of the NEPRA Grid Code of Pakistan and its Draft Amendment no. 2 for Solar Power Projects. | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  | Only to be checked in list of deviations. |  | Important reasons: due to current uncertainty of the criteria we accept an open status. Please clarify that yo acknowledge the criteria and comply unless a reason of high importance will not allow you you to comply. In such a situation the parties will seek to agree a compromise. |  | 1 |  | Open
Chint | GD | Scope of the Bid | Credentials | EPC | 1.1.9 | The bid includes professional experience of the Bidders in ground mounted utility-scale PV and financial information about their long-term stability | 3 |  | 1 | [8 empty] | 1 |  | Pass
Chint | GD | Scope of the Bid | General items | Specific Requirements | 1.1.9 | The bid covers the planning of the System design, the required functionality of the System in terms of its sub-systems and components, detailed feature-wise descriptions of the components to be used in the System, the planning of the System installation, its integration, testing, monitoring, commissioning and O&M of the System | 3 |  |  |  | 1 | We can not find all of the requested criteria in your documents. Please confirm that your bid is compliant with all expectations and requirements of Section 6 of the RFP and provide a list with ALL exeptions or alterations. This applies to both, the EOPC And the O&M part. |  | This question should be removed as detailed design of every component/sub-system will be checked and evaluated thoroughly in technical evaluation | no, its an overall critera an need to be met |  |  | 1 | 1 | Open
Chint | GD | Scope of the Bid | Credentials | EPC | 1.1.10 | The Bidder, or the Lead company in case of JV is a EPC contractor | 1 |  | 1 |  |  |  |  | This is a non-technical question. We suggest such question should be separated from technical questions and placed in checklist for "General/Substantive Responsiveness of Bid" | a question of reliability and experience of solid understanding of the task/System Technology. See also 1.1.10 |  |  | 1 |  | Pass
Chint | GD | Conditions for Disqualification and Additional Information Required | Credentials | EPC | 1.2.6 | Detailed list of all the sites with the affirmation that the bidder played the leading EPC role in the turnkey installation of these systems. | 3 |  | 1 | [8 empty] | 1 |  | Pass
Chint | GD | Conditions for Disqualification and Additional Information Required | Credentials | EPC | 1.2.6 | Cumulative MWp of ground mounted PV turnkey installations >5 MWp with stating of actual MWp per project, project location, date of commissioning, module type and Inverter type. | 1 |  | 1 | [5 empty] | experience of Bidder / EPC |  |  | 1 | 1 | Pass
Chint | GD | Conditions for Disqualification and Additional Information Required | Credentials | EPC | 1.2.6 | References and contact data (mail and phone) from owners of all installations > 5 MW with quotes of the corresponding system Performance Ratios, as well as system performance vs. initial yield assessment per year since the installation. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  | for selection of referenz objects |  |  | 1 | 1 | Open
Chint | GD | Conditions for Disqualification and Additional Information Required | Credentials | EPC | 1.2.6 | Approval from bidder to owners or owner representatives to answer questions freely regarding the past performance of the bidder and performance of the system against contractual obligations. | 2 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | [5 empty] | 1 |  | Open
Chint | GD | Conditions for Disqualification and Additional Information Required | Credentials | O&M | 1.2.6 | Cumulative MWp of ground mounted PV installations for which O&M services have been delivered by the bidder or his O&M subcontractor. | 2 |  | 1 | [8 empty] | 1 |  | Pass
Chint | GD | Conditions for Disqualification and Additional Information Required | Credentials | O&M | 1.2.6 | References, contact data and approval from owners or owner representatives of all installations > 5 MW from bidder or his O&M subcontractor to answer questions freely regarding the past performance of the bidder and performance of the system against contractual obligations. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | [5 empty] | 1 | 1 | Open
Chint | GD | Technical Bid Evaluation Criteria | Credentials | Guarantees | 1.3.1 | To have met the contractual requirements of the EPC and O&M deliverables including certificate to the effect that the entire equipment is brand new as required vide notification number NEPRA/UTS-01/777-779 dated Jan 21 ,2014, | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Only to be checked in list of deviations. |  |  |  | 1 | 1 | Open
Chint | GD | Technical Bid Evaluation Criteria | Credentials | EPC | 1.3.1 | the systems have been completed on time and within budget, | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | [5 empty] | 1 | 1 | Open
Chint | GD | Technical Bid Evaluation Criteria | Credentials | O&M | 1.3.1 | that they have started supplying electricity to the grid and are still operating satisfactorily in 9 out of 10 MW for all the cases | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | [5 empty] | 1 | 1 | Open
Chint | GD | Technical Bid Evaluation Criteria | Credentials | O&M | 1.3.1 | In case of a non-performance, comprehensible evidence has to be given why this case will not affect this project. | 3 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | [5 empty] | 1 |  | Open
Chint | GD | Technical Bid Evaluation Criteria | Credentials | O&M | 1.3.2 | Prove at least 100 MW of EPC experience and 50 MW of full O&M experience for a period longer than 24 months. | 1 |  | 1 | [8 empty] | 1 |  | Pass
Chint | GD | Technical Bid Evaluation Criteria | Due Diligence | Quality Assurance | 1.3.5 | The cost of the due diligence to be carried out by the Employer through an independent technical consultant before contract signature will be taken over by the successful bidder up to an amount of 50,000 USD independent of the result. The due diligence will cover a module factory visit, an inverter factory inspection and a due diligence on the provided financial, EPC and O&M credentials including up to three site visits. | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  | Only to be checked in list of deviations. |  |  |  | 1 |  | Open
Chint | GD | PR and System Performance Guarantee | System PR | Guarantees | 1.4.1 | A 25 years commitment, in the form of a whole System performance guarantee, is required. The performance guarantee is based on measuring the PR with the actual kWh-AC delivery per year adjusted for the actual POA irradiation for the same period | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  | Only to be checked in list of deviations. |  |  |  | 1 | 1 | Open
Chint | GD | PR and System Performance Guarantee | System PR | System PR | 1.4.1 | The billing system/metering system will be installed at interconnection point of 132 kV bus bar of HV substation to be installed by the EPC Contractor and the 132 kV Transmission line of NTDC existing at site. | 2 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  | Only to be checked in list of deviations. |  |  |  | 1 |  | Open
Chint | GD | PR and System Performance Guarantee | System PR | System PR | 1.4.2 | Guaranteed PR values in the form of the Table in 1.4.1 for the acceptance phase and annual output of the PV system shall be specified. | 1 |  | 1 |  |  |  |  | Link to table in Documents sheet |  |  |  | 1 | 1 | Pass
Chint | GD | PR and System Performance Guarantee | System PR | System PR | 1.4.4 | The initial PR will be first measured after the time of commissioning of the completed PV System during the acceptance phase of 30 days. | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  | Cannot be evaluated at this stage. Only to be checked in list of deviations. |  |  |  | 1 | 1 | Open
Chint | GD | PR and System Performance Guarantee | Compensations | System PR | 1.4.4 | The successful Bidder shall conduct the initial PR test for the daylight hours of at least 30 consecutive days, recording data at a frequency of fifteen minute intervals or less, to validate the guaranteed PR value for acceptance. Any excused downtime (e.g., from Grid Operator ordered shutdowns, grid failure, theft, force majeure) will be excluded from that calculation by an independent consultant (Auditing Body). That day will be taken out and another day added, if the initial PR falls short of the guaranteed PR value, the successful Bidder shall be obliged to identify and rectify the causes for the performance shortfall at their own cost. | 2 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  | Cannot be evaluated at this stage. Only to be checked in list of deviations. |  |  |  | 1 |  | Open
Chint | GD | PR and System Performance Guarantee | Compensations | System PR | 1.4.4 | If the measured PR within further 30 days does not reach the guaranteed PR, the Employer can demand that the price of the system will be reduced by the percentage of shortfall times 1.2 for liquidated damages or the contractor will have to install more power at its own cost or combination of both. | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  | Cannot be evaluated at this stage. Only to be checked in list of deviations. |  |  |  | 1 | 1 | Open
Chint | GD | PR and System Performance Guarantee | Compensations | O&M | 1.4.5 | If the annual measured PR falls below the guaranteed PR value according to Table 1.4.1, the liquidated damages will be levied on the successful Bidder at the rate of USD 0.20-per-kWh or the kWh Value the Employer receives for each kWh of shortfall – whichever is higher. Adjustments shall be made for any events outside the control of the O&M operator as grid outages, from grid operator ordered shutdowns, or force majeure events during the year. | 2 |  |  |  | 1 |  |  | Cannot be evaluated at this stage. Only to be checked in list of deviations. | Only to be checked in list of deviations. |  |  | 1 |  | Open
Chint | GD | PR and System Performance Guarantee | Compensations | O&M | 1.4.5 | In case the PR is higher than the guaranteed PR value, the net value of this excess energy will be shared as follows: 50% towards the asset replacement fund, 25% towards the Employer, 25% towards the O&M contractor | 3 |  |  |  | 1 |  |  | Cannot be evaluated at this stage. Only to be checked in list of deviations. |  |  |  | 1 |  | Open
Chint | GD | PR and System Performance Guarantee | Compensations | O&M | 1.4.5 | For timely compensation the PR Calculation will be carried out provisionally for each quarter whereby the contractor and employer might jointly agree on different PR values for each quarter. In the last quarter of each calendar year the annual PR compensation of the full year will be carried out and any provisions will be offset by the annual compensation. | 3 |  |  |  | 1 |  |  | Cannot be evaluated at this stage. Only to be checked in list of deviations. |  |  |  | 1 |  | Open
Chint | GD | PR and System Performance Guarantee | Compensations | O&M | 1.4.6 | If the successful Bidder defaults in being able to provide the O&M services required for the Systems performance guarantee, then it will be liable to cover all costs – but at least in the amount of Liquidated Damages imposed to the Employer by its PPA agreements - incurred by the Employer, including the loss of the guaranteed electricity export to the grid (but at a minimum rate of USD 0.20-per-kWh) for the disrupted period, in finding and hiring a replacement for the purpose. | 1 |  |  |  | 1 | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. |  | Cannot be evaluated at this stage. Only to be checked in list of deviations. |  |  |  | 1 | 1 | Open

## RM (hidden)
Bidder | Expert | Chapter in RfP | Topic | Subtopic | Clause | Criteria | 1 Vital 2 Valuable 3 Not Important | Link to Bidders Documents | Pass =1 | Fail =1 | Open =1 | Question to bidder for clarification | Comments | Comments QA on Criteria | Comment on "Comments" | Typical Questions to be send to bidders if Open status |  | Sub-category
Juwi | RM | Supervisory Control and Data Acquisition (SCADA) | SCADA | Specific Requirements | 1.9.1 | Safe and redundant archive for operational data. | 1 | Annex 11 | ? |  |  |  | 1.14 page 25 ff >> Annex 11 on site data logging Analyse, compare, grafics, reports, fault management, overview, web interface, plant map,
Juwi | RM | Supervisory Control and Data Acquisition (SCADA) | SCADA | Specific Requirements | 1.9.1 | Remote access to all operational data for independent monitoring purposes shall be possible (NTDC requirements) | 1 |  | 1 |  |  |  | RS485 and CAN Bus fibre optics Web interface
Juwi | RM | Supervisory Control and Data Acquisition (SCADA) | SCADA | Specific Requirements | 1.9.1 | The system has to provide different access-levels with different access rights allocated. | 1 |  |  |  | 1 | please confirm and describe "read only", "write"
Juwi | RM | Supervisory Control and Data Acquisition (SCADA) | SCADA | Specific Requirements | 1.9.2 | Control room to remotely monitor and manage the whole system, on a 24 x 7 basis, with the capability of Web-based information sharing | 1 |  |  |  | 1 | please describe
Juwi | RM | Supervisory Control and Data Acquisition (SCADA) | SCADA | Specific Requirements | 1.9.2 | Alarms/alerts and timely notification of key performance indicators | 1 |  | 1
Juwi | RM | Supervisory Control and Data Acquisition (SCADA) | SCADA | Specific Requirements | 1.9.2 | Data must be readily available for the fulfilment of all warranties and performance guarantees | 1 |  | 1 |  |  | Please confirm seperately | by description of data management this is most likely possible | Cannot be evaluated at this stage. | statement
Juwi | RM | Supervisory Control and Data Acquisition (SCADA) | SCADA | Specific Requirements | 1.9.2 | Data logging at intervals of not less than one minute, processing, transmission, and back-up | 1 |  | 1 |  |  | Correct meaning was: maximum interval length of 1 minute. Please confirm. |  |  | not more (!)
Juwi | RM | Supervisory Control and Data Acquisition (SCADA) | SCADA | Specific Requirements | 1.9.2 | Separate inverter, zone, and string level (current and voltage) monitoring | 1 | p384 | 1
Juwi | RM | Supervisory Control and Data Acquisition (SCADA) | SCADA | Specific Requirements | 1.9.2 | Back-up power for a minimum of twelve hours | 1 |  | 1 |  |  |  | 40h
Juwi | RM | Supervisory Control and Data Acquisition (SCADA) | SCADA | Specific Requirements | 1.9.2 | Data shall be provided via FTP (Push/Pull) to the Employer | 1 | p385 | 1 |  |  | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Juwi | RM | Supervisory Control and Data Acquisition (SCADA) | SCADA | Specific Requirements | 1.9.2 | All communication/data cables outside of buildings must be fiber-optic cables | 1 |  | 1 |  |  | general option. Please confirm delivery
Juwi | RM | Meteorological Sensors | Auxiliary Systems | Specific Requirements | 1.10.1 | Irradiation and temperature measurements are to be recorded at intervals of 15 min or less. | 1 |  | 1 |  |  |  | 1 min
Juwi | RM | Meteorological Sensors | Auxiliary Systems | Specific Requirements | 1.10.1 | The equipment should have the capability of recording and storing data for 24 hours using auxiliary DC power. | 1 |  | 1 |  |  |  | min. 2 weeks | Should be priority 1 question
Juwi | RM | Meteorological Sensors | Auxiliary Systems | Specific Requirements | 1.10.2 | The irradiation measurement equipment should be calibrated by an independent certified third party at least every two years. The calibration must be traceable to international standards. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Should be checked in list of deviations
Juwi | RM | Meteorological Sensors | Auxiliary Systems | Specific Requirements | 1.10.2 | Seven pyranometers shall be placed : three for measuring the horizontal plane irradiation and the others for the in-plane irradiation. | 1 | p383 5.0 Monitoring SLD |  |  | 1 | SLD is not sharp enough presented Hardware concept not readable |  | As in 1.10.2, it is seven pyranometer per system, please clarify the word "per system" | 1.1.1: "100 MWp (DC capacity at Standard Testing Conditions, abbreviated STC … hereinafter called 'the System') "
Juwi | RM | Meteorological Sensors | Auxiliary Systems | Specific Requirements | 1.10.2 | The pyranometers should conform to the standards of ISO 9060 (SR5: secondary standard) or the WMO classification, and IEC 60904. | 1 |  | 1 |  |  |  |  | Do we need to know some parameter values according to standards mentioned or just a statement of comlience with the standard would be sufficient? | compliance will be necessary, no data due diligence right now.
Juwi | RM | Meteorological Sensors | Auxiliary Systems | Specific Requirements | 1.10.3 | Ambient air and the module temperature shall be measured at every 5 installed MWp in conformity with IEC 60751 AA | 1 |  |  |  | 1 | SLD is not sharp enough presented Hardware concept not readable
Juwi | RM | Site Preparation and site access | Site Preparation and site access | Specific Requirements | 1.11.1 | The Bidder shall provide foundations and structures in accordance with the actual soil conditions. | 1 | p18 / 1.8 | 1 |  |  | tilt 10° - pleas explain with PVSyst analyse with 20° | additionial geo survey and pull-out test Screw piles tilt 10° (!!) |  | refer to Soil study
Juwi | RM | Earthworks | Site Preparation and site access | Specific Requirements | 1.12 | Within the plant boundary limits, access roads to all stations shall be suitable for heavy load trucks (axle load: min. 12 tonn). | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Juwi | RM | Earthworks | Site Preparation and site access | Specific Requirements | 1.12 | Position and specification of underground cable connections must be documented during installation | 1 |  | 1 |  |  |  |  | Cannot be avaluated at this stage.
Juwi | RM | Earthworks | Site Preparation and site access | Specific Requirements | 1.12, 1.13.4, 1.7.7 | Cross-sections of foundations for stations shall be provided, including explanation of the foundations laying down, height, penetration, and method of installing foundation posts, mounting fixtures | 1 |  | 1
Juwi | RM | Earthworks | Site Preparation and site access | Design factors to be provided | 1.12 | All earth works required have to be specified and included in the offer | 1 |  |  |  | 1 | Location: Only nice pictures. We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Juwi | RM | Earthworks | Site Preparation and site access | Specific Requirements | 1.12 | After completion of construction and all earthworks ground shall be levelled and stabilized. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  | (maintanance, dust)
Juwi | RM | Mounting | Mounting | Specific Requirements | 1.13.1 | The system is fixed-tilted. Tilt angle is specified. | 1 |  | 1 |  |  | tilt 10° - pleas explain with PVSyst analyse with 20°
Juwi | RM | Mounting | Mounting | Specific Requirements | 1.13.3 | Mounting structure is made of durable material, resistant to sandstorms and compatible with the module frame material so as to avoid any adverse electrolytic/galvanic effects. | 1 |  |  |  | 1 | Location: No information in Annexxure4. We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Information about materials to be known before evaluation. | right
Juwi | RM | Mounting | Mounting | Specific Requirements | 1.13.3 | Mounting system resists high wind speeds (up to 40 m/s) | 1 |  |  |  | 1 | Location: No information in Annexxure4. We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Juwi | RM | Mounting | Mounting | Specific Requirements | 1.13.3 | Mounting system resists corrosion (passing the salt spray test IEC 61701, among other verification), | 1 |  |  |  | 1 | Location: No information in Annexxure4. We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Information about materials to be known before evaluation. | right
Juwi | RM | Mounting | Mounting | Specific Requirements | 1.13.3 | Mounting system resists UV induced degradation | 1 |  |  |  | 1 | Location: No information in Annexxure4. We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Juwi | RM | Mounting | Mounting | Specific Requirements | 1.13.5 | All fastening structures must be verified for durability and resistance to environmental degradation for 25 years | 1 |  |  |  | 1 | Location: No information in Annexxure4. We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | What sort of mechanism is required for verification? | Sub structure description / materials double to line 172 - 175
Juwi | RM | Mounting | Mounting | Specific Requirements | 1.13.8 | The mounting structures must be earthed | 1 |  |  |  | 1
Juwi | RM | Mounting | Mounting | Specific Requirements | 1.13.9 | Specific site conditions have been considered. | 1 |  | 1 |  |  |  |  | Needs to be discussed. | … specific requirements of the soil conditions Static
Juwi | RM | Mounting | Mounting | Standards | 1.13.9 | IEC 61730 (as above) | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? | no, just a statement of compliance
Juwi | RM | Mounting | Mounting | Standards | 1.13.9 | STS 531 | 1 |  |  |  | - |  |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? | no, just a statement of compliance
Juwi | RM | Mounting | Mounting | Standards | 1.13.9 | IEC 61730 | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? | no, just a statement of compliance
Juwi | RM | Other infrastructure | Auxiliary systems | Design factors to be provided | 1.25.1 | One administration and office building with car port for 10 vehicles shall be provided, with sufficient space for operating personal, control room, security office, regular office rooms for permanent and visiting staff, meeting room, kitchen sanitary systems (toilet, showers separate for male and female), first aid, control room, electrical rooms, etc. The building shall have windows for office rooms and air conditioning system (split units) for all office rooms. | 1 |  | 1 |  |  |  |  | Priority to be discussed
Juwi | RM | Other infrastructure | Auxiliary systems | Design factors to be provided | 1.25.1 | Warehouse for spare parts and workshop for minor mechanical/electrical works. | 1 |  | 1
Juwi | RM | Other infrastructure | Auxiliary systems | Design factors to be provided | 1.25.1 | Water storage facility for drinking water, sanitary water (sufficient for 1 week) | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Juwi | RM | Other infrastructure | Auxiliary systems | Design factors to be provided | 1.25.1 | Service water system sufficiently sized for cleaning cycle of modules | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Juwi | RM | Other infrastructure | Auxiliary systems | Design factors to be provided | 1.25.1 | Sewage system including sewage disposal for Construction and O&M phase | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Juwi | RM | Other infrastructure | Auxiliary systems | Guarantees | 1.25.4 | All buildings should be designed in accordance with the requirements of the Pakistan Building Code (available at www.pec.org.pk/buildingcode.aspx) and latest Seismic Provisions 2007. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Link to code
Juwi | RM | Other infrastructure | Auxiliary systems | Security Surveillance System | 1.25.5 | The system shall comply with insurance requirements | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Juwi | RM | Other infrastructure | Auxiliary systems | Security Surveillance System | 1.25.5 | The Bidder shall provide security personnel for 24 h / 7 days a week for the whole year | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Juwi | RM | Other infrastructure | Auxiliary systems | DC Backup System / uninterrupted power supply (UPS) | 1.25.6 | IEC-60051 and IEC-60439 standards apply | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient?
Zte | RM | Supervisory Control and Data Acquisition (SCADA) | SCADA | Specific Requirements | 1.9.1 | Safe and redundant archive for operational data. | 1 | 1.TP, p17 1.TP, p87 annex P005 “ Comprehensive Monitoring” | 1 |  |  | please explain "data processing" on site. Explain redundant archive | Monitoring struckture overview
Zte | RM | Supervisory Control and Data Acquisition (SCADA) | SCADA | Specific Requirements | 1.9.1 | Remote access to all operational data for independent monitoring purposes shall be possible (NTDC requirements) | 1 | 1.TP, p87, p94 P005 | 1 |  |  |  | "5.2.4.4 Relaying Protection Information Management Sub-station " "NTDC relaying protection dispatching information net,…"
Zte | RM | Supervisory Control and Data Acquisition (SCADA) | SCADA | Specific Requirements | 1.9.1 | The system has to provide different access-levels with different access rights allocated. | 1 |  |  |  | 1 | please confirm different levels of "read only", "write", User authority
Zte | RM | Supervisory Control and Data Acquisition (SCADA) | SCADA | Specific Requirements | 1.9.2 | Control room to remotely monitor and manage the whole system, on a 24 x 7 basis, with the capability of Web-based information sharing | 1 | 1.TP, 5.3.2 1.TP, 7.1 | 1
Zte | RM | Supervisory Control and Data Acquisition (SCADA) | SCADA | Specific Requirements | 1.9.2 | Alarms/alerts and timely notification of key performance indicators | 1 |  | 1
Zte | RM | Supervisory Control and Data Acquisition (SCADA) | SCADA | Specific Requirements | 1.9.2 | Data must be readily available for the fulfilment of all warranties and performance guarantees | 1 |  |  |  | 1 | please describe and confirm |  | Cannot be evaluated at this stage. | statement
Zte | RM | Supervisory Control and Data Acquisition (SCADA) | SCADA | Specific Requirements | 1.9.2 | Data logging at intervals of not less than one minute, processing, transmission, and back-up | 1 |  |  |  | 1 | please confirm | hint: correct meaning is: no longer interval than 1 minute |  | not more (!)
Zte | RM | Supervisory Control and Data Acquisition (SCADA) | SCADA | Specific Requirements | 1.9.2 | Separate inverter, zone, and string level (current and voltage) monitoring | 1 |  | 1
Zte | RM | Supervisory Control and Data Acquisition (SCADA) | SCADA | Specific Requirements | 1.9.2 | Back-up power for a minimum of twelve hours | 1 |  |  |  | 1 | please confirm 12 h back-up
Zte | RM | Supervisory Control and Data Acquisition (SCADA) | SCADA | Specific Requirements | 1.9.2 | Data shall be provided via FTP (Push/Pull) to the Employer | 1 |  |  |  | 1 | please confirm
Zte | RM | Supervisory Control and Data Acquisition (SCADA) | SCADA | Specific Requirements | 1.9.2 | All communication/data cables outside of buildings must be fiber-optic cables | 1 |  | 1
Zte | RM | Meteorological Sensors | Auxiliary Systems | Specific Requirements | 1.10.1 | Irradiation and temperature measurements are to be recorded at intervals of 15 min or less. | 1 |  |  |  | 1 | "Technical Proposal of 100MW Solar Power Plant.pdf" 5.2.10: more details requiered
Zte | RM | Meteorological Sensors | Auxiliary Systems | Specific Requirements | 1.10.1 | The equipment should have the capability of recording and storing data for 24 hours using auxiliary DC power. | 1 |  |  |  | 1 | DC control power system back-up 100Ah: pease confirm back-up time |  | Should be priority 1 question
Zte | RM | Meteorological Sensors | Auxiliary Systems | Specific Requirements | 1.10.2 | The irradiation measurement equipment should be calibrated by an independent certified third party at least every two years. The calibration must be traceable to international standards. | 1 |  |  |  | 1 | please confirm |  | Should be checked in list of deviations
Zte | RM | Meteorological Sensors | Auxiliary Systems | Specific Requirements | 1.10.2 | Seven pyranometers shall be placed : three for measuring the horizontal plane irradiation and the others for the in-plane irradiation. | 1 |  |  |  | 1 | please confirm Secondary Standard and 7 Py's as required |  | As in 1.10.2, it is seven pyranometer per system, please clarify the word "per system" | 1.1.1: "100 MWp (DC capacity at Standard Testing Conditions, abbreviated STC … hereinafter called 'the System') "
Zte | RM | Meteorological Sensors | Auxiliary Systems | Specific Requirements | 1.10.2 | The pyranometers should conform to the standards of ISO 9060 (SR5: secondary standard) or the WMO classification, and IEC 60904. | 1 |  |  |  | 1 | please confirm |  | Do we need to know some parameter values according to standards mentioned or just a statement of comlience with the standard would be sufficient? | compliance will be necessary, no data due diligence right now.
Zte | RM | Meteorological Sensors | Auxiliary Systems | Specific Requirements | 1.10.3 | Ambient air and the module temperature shall be measured at every 5 installed MWp in conformity with IEC 60751 AA | 1 |  |  |  | 1 | please confirm
Zte | RM | Site Preparation and site access | Site Preparation and site access | Specific Requirements | 1.11.1 | The Bidder shall provide foundations and structures in accordance with the actual soil conditions. | 1 | 1.TP, p126 P002 | 1 |  |  |  | strip footing in Portland Cement P002: screw pile |  | refer to Soil study
Zte | RM | Earthworks | Site Preparation and site access | Specific Requirements | 1.12 | Within the plant boundary limits, access roads to all stations shall be suitable for heavy load trucks (axle load: min. 12 tonn). | 1 | 1.TP, p120 P014 | 1 |  |  | please confirm sutibility for heavy load | access road: 6m wide internal road: 4m wide
Zte | RM | Earthworks | Site Preparation and site access | Specific Requirements | 1.12 | Position and specification of underground cable connections must be documented during installation | 1 |  |  |  | 1 | please confirm delivery with documentation |  | Cannot be avaluated at this stage.
Zte | RM | Earthworks | Site Preparation and site access | Specific Requirements | 1.12, 1.13.4, 1.7.7 | Cross-sections of foundations for stations shall be provided, including explanation of the foundations laying down, height, penetration, and method of installing foundation posts, mounting fixtures | 1 | P002 | 1
Zte | RM | Earthworks | Site Preparation and site access | Design factors to be provided | 1.12 | All earth works required have to be specified and included in the offer | 1 |  |  |  | 1 | burried cable installaton (P015) please describe protection against rodents; please provide description for foundation for MV container
Zte | RM | Earthworks | Site Preparation and site access | Specific Requirements | 1.12 | After completion of construction and all earthworks ground shall be levelled and stabilized. | 1 |  |  |  | 1 | please confirm leveling because soil stabilizes in the left form after short time | afforesting is described |  | (maintanance, dust)
Zte | RM | Mounting | Mounting | Specific Requirements | 1.13.1 | The system is fixed-tilted. Tilt angle is specified. | 1 |  | 1 |  |  |  | 27°
Zte | RM | Mounting | Mounting | Specific Requirements | 1.13.3 | Mounting structure is made of durable material, resistant to sandstorms and compatible with the module frame material so as to avoid any adverse electrolytic/galvanic effects. | 1 | 1.TP | 1 |  |  |  |  | Information about materials to be known before evaluation. | right
Zte | RM | Mounting | Mounting | Specific Requirements | 1.13.3 | Mounting system resists high wind speeds (up to 40 m/s) | 1 |  | 1
Zte | RM | Mounting | Mounting | Specific Requirements | 1.13.3 | Mounting system resists corrosion (passing the salt spray test IEC 61701, among other verification), | 1 |  | 1 |  |  |  |  | Information about materials to be known before evaluation. | right
Zte | RM | Mounting | Mounting | Specific Requirements | 1.13.3 | Mounting system resists UV induced degradation | 1 |  | 1
Zte | RM | Mounting | Mounting | Specific Requirements | 1.13.5 | All fastening structures must be verified for durability and resistance to environmental degradation for 25 years | 1 |  |  |  | 1 | please confirm durability |  | What sort of mechanism is required for verification? | Sub structure description / materials double to line 172 - 175
Zte | RM | Mounting | Mounting | Specific Requirements | 1.13.8 | The mounting structures must be earthed | 1 | P012 | 1
Zte | RM | Mounting | Mounting | Specific Requirements | 1.13.9 | Specific site conditions have been considered. | 1 |  | 1 |  |  |  |  | Needs to be discussed. | … specific requirements of the soil conditions Static
Zte | RM | Mounting | Mounting | Standards | 1.13.9 | IEC 61730 (as above) | 1 |  | 1 |  |  |  |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? | no, just a statement of compliance
Zte | RM | Mounting | Mounting | Standards | 1.13.9 | STS 531 | 1 |  | - |  |  |  |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? | no, just a statement of compliance
Zte | RM | Mounting | Mounting | Standards | 1.13.9 | IEC 61730 | 1 |  | - |  |  |  |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? | no, just a statement of compliance
Zte | RM | Other infrastructure | Auxiliary systems | Design factors to be provided | 1.25.1 | One administration and office building with car port for 10 vehicles shall be provided, with sufficient space for operating personal, control room, security office, regular office rooms for permanent and visiting staff, meeting room, kitchen sanitary systems (toilet, showers separate for male and female), first aid, control room, electrical rooms, etc. The building shall have windows for office rooms and air conditioning system (split units) for all office rooms. | 1 |  | 1 |  |  |  |  | Priority to be discussed
Zte | RM | Other infrastructure | Auxiliary systems | Design factors to be provided | 1.25.1 | Warehouse for spare parts and workshop for minor mechanical/electrical works. | 1 |  | 1
Zte | RM | Other infrastructure | Auxiliary systems | Design factors to be provided | 1.25.1 | Water storage facility for drinking water, sanitary water (sufficient for 1 week) | 1 |  |  |  | 1 | description is exhaustive, but please confirm cormity with RFP
Zte | RM | Other infrastructure | Auxiliary systems | Design factors to be provided | 1.25.1 | Service water system sufficiently sized for cleaning cycle of modules | 1 |  | 1
Zte | RM | Other infrastructure | Auxiliary systems | Design factors to be provided | 1.25.1 | Sewage system including sewage disposal for Construction and O&M phase | 1 |  | 1
Zte | RM | Other infrastructure | Auxiliary systems | Guarantees | 1.25.4 | All buildings should be designed in accordance with the requirements of the Pakistan Building Code (available at www.pec.org.pk/buildingcode.aspx) and latest Seismic Provisions 2007. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Link to code
Zte | RM | Other infrastructure | Auxiliary systems | Security Surveillance System | 1.25.5 | The system shall comply with insurance requirements | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Zte | RM | Other infrastructure | Auxiliary systems | Security Surveillance System | 1.25.5 | The Bidder shall provide security personnel for 24 h / 7 days a week for the whole year | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Zte | RM | Other infrastructure | Auxiliary systems | DC Backup System / uninterrupted power supply (UPS) | 1.25.6 | IEC-60051 and IEC-60439 standards apply | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient?
Tbea | RM | Supervisory Control and Data Acquisition (SCADA) | SCADA | Specific Requirements | 1.9.1 | Safe and redundant archive for operational data. | 1 |  | 1 |  |  | General understanding: expressions like "shall", "has to be", "must be" have the meaning of "will be delivered"?
Tbea | RM | Supervisory Control and Data Acquisition (SCADA) | SCADA | Specific Requirements | 1.9.1 | Remote access to all operational data for independent monitoring purposes shall be possible (NTDC requirements) | 1 |  | 1
Tbea | RM | Supervisory Control and Data Acquisition (SCADA) | SCADA | Specific Requirements | 1.9.1 | The system has to provide different access-levels with different access rights allocated. | 1 |  | 1
Tbea | RM | Supervisory Control and Data Acquisition (SCADA) | SCADA | Specific Requirements | 1.9.2 | Control room to remotely monitor and manage the whole system, on a 24 x 7 basis, with the capability of Web-based information sharing | 1 |  | 1
Tbea | RM | Supervisory Control and Data Acquisition (SCADA) | SCADA | Specific Requirements | 1.9.2 | Alarms/alerts and timely notification of key performance indicators | 1 |  | 1
Tbea | RM | Supervisory Control and Data Acquisition (SCADA) | SCADA | Specific Requirements | 1.9.2 | Data must be readily available for the fulfilment of all warranties and performance guarantees | 1 |  | 1 |  |  |  |  | Cannot be evaluated at this stage. | statement
Tbea | RM | Supervisory Control and Data Acquisition (SCADA) | SCADA | Specific Requirements | 1.9.2 | Data logging at intervals of not less than one minute, processing, transmission, and back-up | 1 |  |  |  | 1 | Correct meaning was: maximum interval length of 1 minute. Please confirm. |  |  | not more (!)
Tbea | RM | Supervisory Control and Data Acquisition (SCADA) | SCADA | Specific Requirements | 1.9.2 | Separate inverter, zone, and string level (current and voltage) monitoring | 1 |  | 1
Tbea | RM | Supervisory Control and Data Acquisition (SCADA) | SCADA | Specific Requirements | 1.9.2 | Back-up power for a minimum of twelve hours | 1 |  | 1
Tbea | RM | Supervisory Control and Data Acquisition (SCADA) | SCADA | Specific Requirements | 1.9.2 | Data shall be provided via FTP (Push/Pull) to the Employer | 1 |  | 1
Tbea | RM | Supervisory Control and Data Acquisition (SCADA) | SCADA | Specific Requirements | 1.9.2 | All communication/data cables outside of buildings must be fiber-optic cables | 1 |  | 1
Tbea | RM | Meteorological Sensors | Auxiliary Systems | Specific Requirements | 1.10.1 | Irradiation and temperature measurements are to be recorded at intervals of 15 min or less. | 1 |  | 1
Tbea | RM | Meteorological Sensors | Auxiliary Systems | Specific Requirements | 1.10.1 | The equipment should have the capability of recording and storing data for 24 hours using auxiliary DC power. | 1 |  | 1 |  |  |  |  | Should be priority 1 question
Tbea | RM | Meteorological Sensors | Auxiliary Systems | Specific Requirements | 1.10.2 | The irradiation measurement equipment should be calibrated by an independent certified third party at least every two years. The calibration must be traceable to international standards. | 1 |  | 1 |  |  |  |  | Should be checked in list of deviations
Tbea | RM | Meteorological Sensors | Auxiliary Systems | Specific Requirements | 1.10.2 | Seven pyranometers shall be placed : three for measuring the horizontal plane irradiation and the others for the in-plane irradiation. | 1 |  | 1 |  |  |  |  | As in 1.10.2, it is seven pyranometer per system, please clarify the word "per system" | 1.1.1: "100 MWp (DC capacity at Standard Testing Conditions, abbreviated STC … hereinafter called 'the System') "
Tbea | RM | Meteorological Sensors | Auxiliary Systems | Specific Requirements | 1.10.2 | The pyranometers should conform to the standards of ISO 9060 (SR5: secondary standard) or the WMO classification, and IEC 60904. | 1 |  | 1 |  |  |  |  | Do we need to know some parameter values according to standards mentioned or just a statement of comlience with the standard would be sufficient? | compliance will be necessary, no data due diligence right now.
Tbea | RM | Meteorological Sensors | Auxiliary Systems | Specific Requirements | 1.10.3 | Ambient air and the module temperature shall be measured at every 5 installed MWp in conformity with IEC 60751 AA | 1 |  | 1
Tbea | RM | Site Preparation and site access | Site Preparation and site access | Specific Requirements | 1.11.1 | The Bidder shall provide foundations and structures in accordance with the actual soil conditions. | 1 |  |  |  | 1 | I please describe so far calculations / plannings / uncertainties. Soil study is for information even if professionally executed. |  |  | refer to Soil study
Tbea | RM | Earthworks | Site Preparation and site access | Specific Requirements | 1.12 | Within the plant boundary limits, access roads to all stations shall be suitable for heavy load trucks (axle load: min. 12 tonn). | 1 |  | 1
Tbea | RM | Earthworks | Site Preparation and site access | Specific Requirements | 1.12 | Position and specification of underground cable connections must be documented during installation | 1 |  | 1 |  |  |  |  | Cannot be avaluated at this stage.
Tbea | RM | Earthworks | Site Preparation and site access | Specific Requirements | 1.12, 1.13.4, 1.7.7 | Cross-sections of foundations for stations shall be provided, including explanation of the foundations laying down, height, penetration, and method of installing foundation posts, mounting fixtures | 1 |  | 1 |  |  | Stated | TBEA-12 Appedices Structure solution not finalized. Site testings will be executed in advance. Check in detail.
Tbea | RM | Earthworks | Site Preparation and site access | Design factors to be provided | 1.12 | All earth works required have to be specified and included in the offer | 1 |  |  |  | 1 | How about access accross those trenches into rows / where located? What is the idea of the paved station suare? Please describe cross section of internal access roads (line 163) | TBEA-12 Appendices Structure foundaton+earthing Inverter Station foundation MV box foundation Station square Cabel trench (solid box), top cover is 150mm above (!) ground
Tbea | RM | Earthworks | Site Preparation and site access | Specific Requirements | 1.12 | After completion of construction and all earthworks ground shall be levelled and stabilized. | 1 |  | 1 | [5 empty] | (maintanance, dust)
Tbea | RM | Mounting | Mounting | Specific Requirements | 1.13.1 | The system is fixed-tilted. Tilt angle is specified. | 1 |  | 1 |  |  |  | S.89 29° - 30° south
Tbea | RM | Mounting | Mounting | Specific Requirements | 1.13.3 | Mounting structure is made of durable material, resistant to sandstorms and compatible with the module frame material so as to avoid any adverse electrolytic/galvanic effects. | 1 |  | 1 |  |  |  |  | Information about materials to be known before evaluation. | right
Tbea | RM | Mounting | Mounting | Specific Requirements | 1.13.3 | Mounting system resists high wind speeds (up to 40 m/s) | 1 |  | 1
Tbea | RM | Mounting | Mounting | Specific Requirements | 1.13.3 | Mounting system resists corrosion (passing the salt spray test IEC 61701, among other verification), | 1 |  | 1 |  |  |  |  | Information about materials to be known before evaluation. | right
Tbea | RM | Mounting | Mounting | Specific Requirements | 1.13.3 | Mounting system resists UV induced degradation | 1 |  | 1
Tbea | RM | Mounting | Mounting | Specific Requirements | 1.13.5 | All fastening structures must be verified for durability and resistance to environmental degradation for 25 years | 1 |  | 1 |  |  | "Applicable construction codes" not mentioned in TBEA-12 / 8… Please add. |  | What sort of mechanism is required for verification? | Sub structure description / materials double to line 172 - 175
Tbea | RM | Mounting | Mounting | Specific Requirements | 1.13.8 | The mounting structures must be earthed | 1 |  |  |  | 1 | We cant find the information in the Bid. Please provide Location TBEA-12/11 is only catodic protection
Tbea | RM | Mounting | Mounting | Specific Requirements | 1.13.9 | Specific site conditions have been considered. | 1 |  |  |  | 1 | Please confirm that at minimum IEC stadards are fullfilled |  | Needs to be discussed. | … specific requirements of the soil conditions Static
Tbea | RM | Mounting | Mounting | Standards | 1.13.9 | IEC 61730 (as above) | 1 |  |  |  | 1 | Please confirm that at minimum IEC stadards are fullfilled |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? | no, just a statement of compliance
Tbea | RM | Mounting | Mounting | Standards | 1.13.9 | STS 531 | 1 |  |  |  | 1 | Please confirm that at minimum IEC stadards are fullfilled |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? | no, just a statement of compliance
Tbea | RM | Mounting | Mounting | Standards | 1.13.9 | IEC 61730 | 1 |  |  |  | 1 | Please confirm that at minimum IEC stadards are fullfilled |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? | no, just a statement of compliance
Tbea | RM | Other infrastructure | Auxiliary systems | Design factors to be provided | 1.25.1 | One administration and office building with car port for 10 vehicles shall be provided, with sufficient space for operating personal, control room, security office, regular office rooms for permanent and visiting staff, meeting room, kitchen sanitary systems (toilet, showers separate for male and female), first aid, control room, electrical rooms, etc. The building shall have windows for office rooms and air conditioning system (split units) for all office rooms. | 1 |  |  |  | 1 |  |  | Priority to be discussed
Tbea | RM | Other infrastructure | Auxiliary systems | Design factors to be provided | 1.25.1 | Warehouse for spare parts and workshop for minor mechanical/electrical works. | 1 |  |  |  | 1
Tbea | RM | Other infrastructure | Auxiliary systems | Design factors to be provided | 1.25.1 | Water storage facility for drinking water, sanitary water (sufficient for 1 week) | 1 |  |  |  | 1
Tbea | RM | Other infrastructure | Auxiliary systems | Design factors to be provided | 1.25.1 | Service water system sufficiently sized for cleaning cycle of modules | 1 |  |  |  | 1
Tbea | RM | Other infrastructure | Auxiliary systems | Design factors to be provided | 1.25.1 | Sewage system including sewage disposal for Construction and O&M phase | 1 |  |  |  | 1
Tbea | RM | Other infrastructure | Auxiliary systems | Guarantees | 1.25.4 | All buildings should be designed in accordance with the requirements of the Pakistan Building Code (available at www.pec.org.pk/buildingcode.aspx) and latest Seismic Provisions 2007. | 1 |  |  |  | 1 |  |  | Link to code
Tbea | RM | Other infrastructure | Auxiliary systems | Security Surveillance System | 1.25.5 | The system shall comply with insurance requirements | 1 |  |  |  | 1
Tbea | RM | Other infrastructure | Auxiliary systems | Security Surveillance System | 1.25.5 | The Bidder shall provide security personnel for 24 h / 7 days a week for the whole year | 1 |  |  |  | 1
Tbea | RM | Other infrastructure | Auxiliary systems | DC Backup System / uninterrupted power supply (UPS) | 1.25.6 | IEC-60051 and IEC-60439 standards apply | 1 |  |  |  | 1 |  | Wording in Bid is still "IEC-51and IEC-439" insted of 60051 / 60439 | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient?
Sumec | RM | Supervisory Control and Data Acquisition (SCADA) | SCADA | Specific Requirements | 1.9.1 | Safe and redundant archive for operational data. | 1 | Vol-III, F7 Vol-I, p321-328 | 1 |  |  | General understanding: expressions like "shall", "has to be", "must be" have the meaning of "will be delivered"? | 10 Ethernet rings /97 Inv. DataCollectorCabinet |  |  | General understanding: expressions like "shall", "has to be", "must be" have the meaning of "will be delivered"?
Sumec | RM | Supervisory Control and Data Acquisition (SCADA) | SCADA | Specific Requirements | 1.9.1 | Remote access to all operational data for independent monitoring purposes shall be possible (NTDC requirements) | 1 |  | 1
Sumec | RM | Supervisory Control and Data Acquisition (SCADA) | SCADA | Specific Requirements | 1.9.1 | The system has to provide different access-levels with different access rights allocated. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Sumec | RM | Supervisory Control and Data Acquisition (SCADA) | SCADA | Specific Requirements | 1.9.2 | Control room to remotely monitor and manage the whole system, on a 24 x 7 basis, with the capability of Web-based information sharing | 1 |  | 1
Sumec | RM | Supervisory Control and Data Acquisition (SCADA) | SCADA | Specific Requirements | 1.9.2 | Alarms/alerts and timely notification of key performance indicators | 1 |  | 1
Sumec | RM | Supervisory Control and Data Acquisition (SCADA) | SCADA | Specific Requirements | 1.9.2 | Data must be readily available for the fulfilment of all warranties and performance guarantees | 1 |  | 1 |  |  |  |  | Cannot be evaluated at this stage. | statement
Sumec | RM | Supervisory Control and Data Acquisition (SCADA) | SCADA | Specific Requirements | 1.9.2 | Data logging at intervals of not less than one minute, processing, transmission, and back-up | 1 |  |  |  | 1 |  |  |  | not more (!)
Sumec | RM | Supervisory Control and Data Acquisition (SCADA) | SCADA | Specific Requirements | 1.9.2 | Separate inverter, zone, and string level (current and voltage) monitoring | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Sumec | RM | Supervisory Control and Data Acquisition (SCADA) | SCADA | Specific Requirements | 1.9.2 | Back-up power for a minimum of twelve hours | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | 200Ah means what? |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Sumec | RM | Supervisory Control and Data Acquisition (SCADA) | SCADA | Specific Requirements | 1.9.2 | Data shall be provided via FTP (Push/Pull) to the Employer | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Sumec | RM | Supervisory Control and Data Acquisition (SCADA) | SCADA | Specific Requirements | 1.9.2 | All communication/data cables outside of buildings must be fiber-optic cables | 1 | Vol-I, p23 |  | 1 |  |  | 45km of DJYVRP2-22-2*1.0 = copper for outside
Sumec | RM | Meteorological Sensors | Auxiliary Systems | Specific Requirements | 1.10.1 | Irradiation and temperature measurements are to be recorded at intervals of 15 min or less. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Sumec | RM | Meteorological Sensors | Auxiliary Systems | Specific Requirements | 1.10.1 | The equipment should have the capability of recording and storing data for 24 hours using auxiliary DC power. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Should be priority 1 question |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Sumec | RM | Meteorological Sensors | Auxiliary Systems | Specific Requirements | 1.10.2 | The irradiation measurement equipment should be calibrated by an independent certified third party at least every two years. The calibration must be traceable to international standards. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Should be checked in list of deviations |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Sumec | RM | Meteorological Sensors | Auxiliary Systems | Specific Requirements | 1.10.2 | Seven pyranometers shall be placed : three for measuring the horizontal plane irradiation and the others for the in-plane irradiation. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | As in 1.10.2, it is seven pyranometer per system, please clarify the word "per system" | 1.1.1: "100 MWp (DC capacity at Standard Testing Conditions, abbreviated STC … hereinafter called 'the System') " | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Sumec | RM | Meteorological Sensors | Auxiliary Systems | Specific Requirements | 1.10.2 | The pyranometers should conform to the standards of ISO 9060 (SR5: secondary standard) or the WMO classification, and IEC 60904. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Do we need to know some parameter values according to standards mentioned or just a statement of comlience with the standard would be sufficient? | compliance will be necessary, no data due diligence right now. | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Sumec | RM | Meteorological Sensors | Auxiliary Systems | Specific Requirements | 1.10.3 | Ambient air and the module temperature shall be measured at every 5 installed MWp in conformity with IEC 60751 AA | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Sumec | RM | Site Preparation and site access | Site Preparation and site access | Specific Requirements | 1.11.1 | The Bidder shall provide foundations and structures in accordance with the actual soil conditions. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. | only example for bracket pile not final |  | refer to Soil study | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Sumec | RM | Earthworks | Site Preparation and site access | Specific Requirements | 1.12 | Within the plant boundary limits, access roads to all stations shall be suitable for heavy load trucks (axle load: min. 12 tonn). | 1 | Vol-I, p37 p68 |  |  | 1 |  | Vol-II, p398 exvacation: 42000m³ backfilling: 1500m³ foundation (Stations?): 780m³
Sumec | RM | Earthworks | Site Preparation and site access | Specific Requirements | 1.12 | Position and specification of underground cable connections must be documented during installation | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Cannot be avaluated at this stage. |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Sumec | RM | Earthworks | Site Preparation and site access | Specific Requirements | 1.12, 1.13.4, 1.7.7 | Cross-sections of foundations for stations shall be provided, including explanation of the foundations laying down, height, penetration, and method of installing foundation posts, mounting fixtures | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Sumec | RM | Earthworks | Site Preparation and site access | Design factors to be provided | 1.12 | All earth works required have to be specified and included in the offer | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Sumec | RM | Earthworks | Site Preparation and site access | Specific Requirements | 1.12 | After completion of construction and all earthworks ground shall be levelled and stabilized. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  | (maintanance, dust) | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Sumec | RM | Mounting | Mounting | Specific Requirements | 1.13.1 | The system is fixed-tilted. Tilt angle is specified. | 1 | Vol-II,p396 Vol-I, p80 | 1 |  |  |  | 27°
Sumec | RM | Mounting | Mounting | Specific Requirements | 1.13.3 | Mounting structure is made of durable material, resistant to sandstorms and compatible with the module frame material so as to avoid any adverse electrolytic/galvanic effects. | 1 | Vol-III, F19 |  |  | 1 |  | hot dip galv. Stee | Information about materials to be known before evaluation. | right
Sumec | RM | Mounting | Mounting | Specific Requirements | 1.13.3 | Mounting system resists high wind speeds (up to 40 m/s) | 1 | Vol-III, F19 |  |  | 1
Sumec | RM | Mounting | Mounting | Specific Requirements | 1.13.3 | Mounting system resists corrosion (passing the salt spray test IEC 61701, among other verification), | 1 | Vol-III, F19 |  |  | 1 |  | hot dip galv. Stee | Information about materials to be known before evaluation. | right
Sumec | RM | Mounting | Mounting | Specific Requirements | 1.13.3 | Mounting system resists UV induced degradation | 1 | Vol-III, F19 |  |  | 1 |  | hot dip galv. Stee
Sumec | RM | Mounting | Mounting | Specific Requirements | 1.13.5 | All fastening structures must be verified for durability and resistance to environmental degradation for 25 years | 1 | Vol-III, F19 |  |  | 1 |  | hot dip galv. Steel: Thickness? | What sort of mechanism is required for verification? | Sub structure description / materials double to line 172 - 175
Sumec | RM | Mounting | Mounting | Specific Requirements | 1.13.8 | The mounting structures must be earthed | 1 | Vol-III, F19 |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Sumec | RM | Mounting | Mounting | Specific Requirements | 1.13.9 | Specific site conditions have been considered. | 1 | Vol-III, F19 |  |  | 1 |  | "Final geo survey" shall be executed by bidder. Breacket Pile foundation offered | Needs to be discussed. | … specific requirements of the soil conditions Static
Sumec | RM | Mounting | Mounting | Standards | 1.13.9 | IEC 61730 (as above) | 1 |  | - |  |  |  |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? | no, just a statement of compliance
Sumec | RM | Other infrastructure | Auxiliary systems | Design factors to be provided | 1.25.1 | One administration and office building with car port for 10 vehicles shall be provided, with sufficient space for operating personal, control room, security office, regular office rooms for permanent and visiting staff, meeting room, kitchen sanitary systems (toilet, showers separate for male and female), first aid, control room, electrical rooms, etc. The building shall have windows for office rooms and air conditioning system (split units) for all office rooms. | 1 | Vol-III, F2 F12, F13 | 1 |  |  |  |  | Priority to be discussed
Sumec | RM | Other infrastructure | Auxiliary systems | Design factors to be provided | 1.25.1 | Warehouse for spare parts and workshop for minor mechanical/electrical works. | 1 | Vol-III, F12-13 | 1 |  |  |  | Standard rooms in office buildings
Sumec | RM | Other infrastructure | Auxiliary systems | Design factors to be provided | 1.25.1 | Water storage facility for drinking water, sanitary water (sufficient for 1 week) | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Sumec | RM | Other infrastructure | Auxiliary systems | Design factors to be provided | 1.25.1 | Service water system sufficiently sized for cleaning cycle of modules | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Sumec | RM | Other infrastructure | Auxiliary systems | Design factors to be provided | 1.25.1 | Sewage system including sewage disposal for Construction and O&M phase | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Sumec | RM | Other infrastructure | Auxiliary systems | Guarantees | 1.25.4 | All buildings should be designed in accordance with the requirements of the Pakistan Building Code (available at www.pec.org.pk/buildingcode.aspx) and latest Seismic Provisions 2007. | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  | Link to code |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Sumec | RM | Other infrastructure | Auxiliary systems | Security Surveillance System | 1.25.5 | The system shall comply with insurance requirements | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Sumec | RM | Other infrastructure | Auxiliary systems | Security Surveillance System | 1.25.5 | The Bidder shall provide security personnel for 24 h / 7 days a week for the whole year | 1 |  |  |  | 1 | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents. |  |  |  | L | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Sumec | RM | Other infrastructure | Auxiliary systems | DC Backup System / uninterrupted power supply (UPS) | 1.25.6 | IEC-60051 and IEC-60439 standards apply | 1 | Vol-I, p40 |  | 1 |  | Please confirm requiered international standards | All listed standards arer China | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria.

## EPC (hidden)
Bidder | Expert | Chapter in RfP | Topic | Subtopic | Clause | Criteria | 1 Vital 2 Valuable 3 Not Important | Link to Bidders Documents | Pass =1 | Fail =1 | Open =1 | Question to bidder for clarification | Comments | Comments QA on Criteria | Comment on "Comments" | Typical Questions to be send to bidders if Open status | Sub-category
| GD | Scope of the Bid | General items | Specific Requirements | 1.1.2 | The Offer shall include a list of all vendors and/or sub-contractors for major equipment. | 1 | [8 empty] | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria.
| GD | Scope of the Bid | General items | Quality Assurance | 1.1.3 | Defect components consequences: If one tested sample fails in one criterion, all items of the same category will be regarded as failed and rejected. | 1 | [6 empty] | Only to be checked in list of deviations. | yes, we need to be sure that they comply as for most of the critera | Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
| GD | Scope of the Bid | General items | Guarantees | 1.1.5 | Energy Purchase Agreement (EPA) practices are followed | 1 | [6 empty] | This cannot be evaluated at this stage. | we need a sentence that it should and can only be disregarded for important reasons | Unclear: We do not understand your proposal, please detail your proposal. Especially confirm that you are compliant with our requested criteria.
| GD | Scope of the Bid | Layout | Guarantees | 1.1.6 | The bidder confirms that the system complies with all applicable requirements of the NEPRA Grid Code of Pakistan and its Draft Amendment no. 2 for Solar Power Projects. | 1 | [6 empty] | Only to be checked in list of deviations. |  | Important reasons: due to current uncertainty of the criteria we accept an open status. Please clarify that yo acknowledge the criteria and comply unless a reason of high importance will not allow you you to comply. In such a situation the parties will seek to agree a compromise.
| GD | Scope of the Bid | Credentials | EPC | 1.1.9 | The bid includes professional experience of the Bidders in ground mounted utility-scale PV and financial information about their long-term stability | 3
| GD | Scope of the Bid | General items | Specific Requirements | 1.1.9 | The bid covers the planning of the System design, the required functionality of the System in terms of its sub-systems and components, detailed feature-wise descriptions of the components to be used in the System, the planning of the System installation, its integration, testing, monitoring, commissioning and O&M of the System | 3 | [6 empty] | This question should be removed as detailed design of every component/sub-system will be checked and evaluated thoroughly in technical evaluation | no, its an overall critera an need to be met
| GD | Scope of the Bid | Credentials | EPC | 1.1.10 | The Bidder, or the Lead company in case of JV is a EPC contractor | 1 | [6 empty] | This is a non-technical question. We suggest such question should be separated from technical questions and placed in checklist for "General/Substantive Responsiveness of Bid" | a question of reliability and experience of solid understanding of the task/System Technology. See also 1.1.10
| GD | Conditions for Disqualification and Additional Information Required | Credentials | EPC | 1.2.6 | Detailed list of all the sites with the affirmation that the bidder played the leading EPC role in the turnkey installation of these systems. | 3 | [9 empty] | Informative
| GD | Conditions for Disqualification and Additional Information Required | Credentials | EPC | 1.2.6 | Cumulative MWp of ground mounted PV turnkey installations >5 MWp with stating of actual MWp per project, project location, date of commissioning, module type and Inverter type. | 1 | [7 empty] | experience of Bidder / EPC |  | Informative
| GD | Conditions for Disqualification and Additional Information Required | Credentials | EPC | 1.2.6 | References and contact data (mail and phone) from owners of all installations > 5 MW with quotes of the corresponding system Performance Ratios, as well as system performance vs. initial yield assessment per year since the installation. | 1 | [7 empty] | for selection of referenz objects |  | Informative
| GD | Conditions for Disqualification and Additional Information Required | Credentials | EPC | 1.2.6 | Approval from bidder to owners or owner representatives to answer questions freely regarding the past performance of the bidder and performance of the system against contractual obligations. | 2 | [9 empty] | Informative
| GD | Conditions for Disqualification and Additional Information Required | Credentials | O&M | 1.2.6 | Cumulative MWp of ground mounted PV installations for which O&M services have been delivered by the bidder or his O&M subcontractor. | 2 | [9 empty] | Informative
| GD | Conditions for Disqualification and Additional Information Required | Credentials | O&M | 1.2.6 | References, contact data and approval from owners or owner representatives of all installations > 5 MW from bidder or his O&M subcontractor to answer questions freely regarding the past performance of the bidder and performance of the system against contractual obligations. | 1 | [9 empty] | Informative
| GD | Technical Bid Evaluation Criteria | Credentials | Guarantees | 1.3.1 | To have met the contractual requirements of the EPC and O&M deliverables including certificate to the effect that the entire equipment is brand new as required vide notification number NEPRA/UTS-01/777-779 dated Jan 21 ,2014, | 1 |  |  |  | 1 |  |  | Only to be checked in list of deviations.
| GD | Technical Bid Evaluation Criteria | Credentials | EPC | 1.3.1 | the systems have been completed on time and within budget, | 1 | [9 empty] | Informative
| GD | Technical Bid Evaluation Criteria | Credentials | O&M | 1.3.1 | that they have started supplying electricity to the grid and are still operating satisfactorily in 9 out of 10 MW for all the cases | 1 | [9 empty] | Informative
| GD | Technical Bid Evaluation Criteria | Credentials | O&M | 1.3.1 | In case of a non-performance, comprehensible evidence has to be given why this case will not affect this project. | 3 | [9 empty] | Informative
| GD | Technical Bid Evaluation Criteria | Credentials | O&M | 1.3.2 | Prove at least 100 MW of EPC experience and 50 MW of full O&M experience for a period longer than 24 months. | 1 | [9 empty] | Informative
| GD | Technical Bid Evaluation Criteria | Due Diligence | Quality Assurance | 1.3.5 | The cost of the due diligence to be carried out by the Employer through an independent technical consultant before contract signature will be taken over by the successful bidder up to an amount of 50,000 USD independent of the result. The due diligence will cover a module factory visit, an inverter factory inspection and a due diligence on the provided financial, EPC and O&M credentials including up to three site visits. | 1 | [6 empty] | Only to be checked in list of deviations.
| GD | PR and System Performance Guarantee | System PR | Guarantees | 1.4.1 | A 25 years commitment, in the form of a whole System performance guarantee, is required. The performance guarantee is based on measuring the PR with the actual kWh-AC delivery per year adjusted for the actual POA irradiation for the same period | 1 | [6 empty] | Only to be checked in list of deviations.
| GD | PR and System Performance Guarantee | System PR | System PR | 1.4.1 | The billing system/metering system will be installed at interconnection point of 132 kV bus bar of HV substation to be installed by the EPC Contractor and the 132 kV Transmission line of NTDC existing at site. | 2 | [6 empty] | Only to be checked in list of deviations.
| GD | PR and System Performance Guarantee | System PR | System PR | 1.4.2 | Guaranteed PR values in the form of the Table in 1.4.1 for the acceptance phase and annual output of the PV system shall be specified. | 1 | [6 empty] | Link to table in Documents sheet
| GD | PR and System Performance Guarantee | System PR | System PR | 1.4.4 | The initial PR will be first measured after the time of commissioning of the completed PV System during the acceptance phase of 30 days. | 1 | [6 empty] | Cannot be evaluated at this stage. Only to be checked in list of deviations.
| GD | PR and System Performance Guarantee | Compensations | System PR | 1.4.4 | The successful Bidder shall conduct the initial PR test for the daylight hours of at least 30 consecutive days, recording data at a frequency of fifteen minute intervals or less, to validate the guaranteed PR value for acceptance. Any excused downtime (e.g., from Grid Operator ordered shutdowns, grid failure, theft, force majeure) will be excluded from that calculation by an independent consultant (Auditing Body). That day will be taken out and another day added, if the initial PR falls short of the guaranteed PR value, the successful Bidder shall be obliged to identify and rectify the causes for the performance shortfall at their own cost. | 2 | [6 empty] | Cannot be evaluated at this stage. Only to be checked in list of deviations.
| GD | PR and System Performance Guarantee | Compensations | System PR | 1.4.4 | If the measured PR within further 30 days does not reach the guaranteed PR, the Employer can demand that the price of the system will be reduced by the percentage of shortfall times 1.2 for liquidated damages or the contractor will have to install more power at its own cost or combination of both. | 1 | [6 empty] | Cannot be evaluated at this stage. Only to be checked in list of deviations.
| GD | PR and System Performance Guarantee | Compensations | O&M | 1.4.5 | If the annual measured PR falls below the guaranteed PR value according to Table 1.4.1, the liquidated damages will be levied on the successful Bidder at the rate of USD 0.20-per-kWh or the kWh Value the Employer receives for each kWh of shortfall – whichever is higher. Adjustments shall be made for any events outside the control of the O&M operator as grid outages, from grid operator ordered shutdowns, or force majeure events during the year. | 2 | [6 empty] | Cannot be evaluated at this stage. Only to be checked in list of deviations. | Only to be checked in list of deviations.
| GD | PR and System Performance Guarantee | Compensations | O&M | 1.4.5 | In case the PR is higher than the guaranteed PR value, the net value of this excess energy will be shared as follows: 50% towards the asset replacement fund, 25% towards the Employer, 25% towards the O&M contractor | 3 | [6 empty] | Cannot be evaluated at this stage. Only to be checked in list of deviations.
| GD | PR and System Performance Guarantee | Compensations | O&M | 1.4.5 | For timely compensation the PR Calculation will be carried out provisionally for each quarter whereby the contractor and employer might jointly agree on different PR values for each quarter. In the last quarter of each calendar year the annual PR compensation of the full year will be carried out and any provisions will be offset by the annual compensation. | 3 | [6 empty] | Cannot be evaluated at this stage. Only to be checked in list of deviations.
| GD | PR and System Performance Guarantee | Compensations | O&M | 1.4.6 | If the successful Bidder defaults in being able to provide the O&M services required for the Systems performance guarantee, then it will be liable to cover all costs – but at least in the amount of Liquidated Damages imposed to the Employer by its PPA agreements - incurred by the Employer, including the loss of the guaranteed electricity export to the grid (but at a minimum rate of USD 0.20-per-kWh) for the disrupted period, in finding and hiring a replacement for the purpose. | 1 | [6 empty] | Cannot be evaluated at this stage. Only to be checked in list of deviations.
| JBS | System PR Specification | System PR | O&M | 1.5.1 | annual PR values will be calculated based on independent 2-yearly calibrated irradiation sensors | 2 | [6 empty] | Cannot be evaluated at this stage. Only to be checked in list of deviations.
| JBS | System PR Specification | System PR | O&M | 1.5.2 | The target PR specification at the time of commissioning the System is equal to or greater than 0.75 (75%). | 1
| JBS | System PR Specification | System PR | Losses included in PR calculation | 1.5.4 | Module Array (temperature dependence, soiling, low light inefficiency, shading, mismatches in array) | 1 | [6 empty] | We don’t understand the question. Kindly clarify. | we want to see these losses specified. Thos need to be aligned with O+M Startegy and System composition
| JBS | System PR Specification | System PR | Losses included in PR calculation | 1.5.4 | Inverter (operating efficiency, operating voltage variations, power/voltage levels) | 1 | [6 empty] | We don’t understand the question. Kindly clarify. | see relevant chapter 1.5.4 List of technical losses that make the PR
| JBS | System PR Specification | System PR | Losses included in PR calculation | 1.5.4 | Transformer losses | 1 | [6 empty] | We don’t understand the question. Kindly clarify. | see relevant chapter 1.5.4 List of technical losses that make the PR
| JBS | System PR Specification | System PR | Losses included in PR calculation | 1.5.4 | Ohmic losses in cables | 1 | [6 empty] | We don’t understand the question. Kindly clarify. | see relevant chapter 1.5.4 List of technical losses that make the PR
| JBS | System PR Specification | System PR | Losses included in PR calculation | 1.5.4 | Auxiliary loads | 1 | [6 empty] | We don’t understand the question. Kindly clarify. | see relevant chapter 1.5.4 List of "losses" = auxilary loads from PV Energy that make the PR
| JBS | Basic Scope of Supply | General items | Specific Requirements | 1.6 | The maximum DC voltage shall not exceed 1500 V | 1
| JBS | Basic Scope of Supply | General items | Specific Requirements | 1.6 | The required AC voltage / frequency at grid connection shall 132 kV/50 Hz | 1
| JBS | Basic Scope of Supply | General items | Guarantees | 1.6 | Complete power plant has to comply with all applicable national and international standards and the Applicable Standards | 2 | [6 empty] | Only to be checked in list of deviations.
| JBS | Basic Scope of Supply | General items | Specific Requirements | 1.6 | The components and building materials shall be stored within the property | 2 | [6 empty] | cannot be evaluated at this stage
| JBS | Basic Scope of Supply | General items | Specific Requirements | 1.6 | The bidder shall be responsible for accommodation and transport of the staff during construction and warranty period | 2 | [6 empty] | Cannot be evaluated at this stage. Only to be checked in list of deviations.
| JBS | Basic Scope of Supply | General items | Specific Requirements | 1.6 | Permanent office with telephone and internet connection for at least 4 persons (in separate rooms) shall be provided by the successful bidder | 2 | [6 empty] | Cannot be evaluated at this stage. Only to be checked in list of deviations.
| JBS | Basic Scope of Supply | Warranty | Quality Assurance | 1.6 | The Product Warranties shall be given for a duration of at least 5 years | 1 | [6 empty] | Cannot be evaluated at this stage. Only to be checked in list of deviations.
| JBS | Basic Scope of Supply | General items | General applicable standards | 1.6 | IEC | 3 | [6 empty] | We don’t understand the question. Kindly clarify. | applicable standards in general
| JBS | Basic Scope of Supply | General items | General applicable standards | 1.6 | ASTM | 3 | [6 empty] | We don’t understand the question. Kindly clarify. | applicable standards in general
| JBS | Basic Scope of Supply | General items | General applicable standards | 1.6 | IEEE | 3 | [6 empty] | We don’t understand the question. Kindly clarify. | applicable standards in general
| JBS | Basic Scope of Supply | General items | General applicable standards | 1.6 | BS | 3 | [6 empty] | We don’t understand the question. Kindly clarify. | applicable standards in general
| JBS | Basic Scope of Supply | General items | General applicable standards | 1.6 | ASCE | 3 | [6 empty] | We don’t understand the question. Kindly clarify. | applicable standards in general
| JBS | Basic Scope of Supply | General items | General applicable standards | 1.6 | ACI | 3 | [6 empty] | We don’t understand the question. Kindly clarify. | applicable standards in general
| JBS | Basic Scope of Supply | General items | General applicable standards | 1.6 | ISO | 3 | [6 empty] | We don’t understand the question. Kindly clarify. | applicable standards in general
| JBS | Physical layout | Layout | Specific Requirements | 1.7.1 | System design in excellent detail: All descriptive values for design factors and variables associated with System functions and components, including detailed drawings where applicable, must be documented and explained | 2 | [6 empty] | This question should be removed as detailed design of every component/sub-system will be checked and evaluated thoroughly in technical evaluation | As we don´t know what documents will be delivered, this is a generel request. its an overall criteria an need to be met.
| JBS | Physical layout | System PR | Specific Requirements | 1.7.1, 1.1.8 | Layout calculations of predicted kWh over the system lifetime and PR using the tool PVSyst V5.62 or higher | 1
| JBS | Physical layout | System PR | Specific Requirements | 1.7.1 | Provide a report using Solar GIS data provided by the Employer | 1 | [6 empty] | Replace 'Report' with ' PV-Syst report'. | 'Report' is original wording in ER in 1.7.1
| JBS | Physical layout | System PR | Specific Requirements | 1.7.1 | Besides the PVSyst report, the data files must be submitted | 1
| JBS | Physical layout | Layout | Specific Requirements | 1.7.2 | Provide a schematic electrical Single Line Diagram (SLD) of the entire System layout from the modules to the grid-connection, identifying and listing all of the following DC and AC components. | 1
| JBS | Physical layout | Layout | Specific Requirements | 1.7.2 | The system design shall be such as to ensure ease of maintenance and a multiple ring main unit (RMU) philosophy (on MV level) must be followed for circuit breaker configuration. | 1
| JBS | Physical layout | Layout | Specific Requirements | 1.7.2 | The ring capacity of connected inverter output power shall be 5 to 10 MW (AC). | 2
| JBS | Physical layout | Layout | Specific Requirements | 1.7.3 | Provide data sheets, installation instructions, operating and service manuals for each component shown in the diagram | 3
| JBS | Physical layout | Layout | Specific Requirements | 1.7.4 | The DC and AC sub-systems should be clearly demarcated in the SLD. | 2
| JBS | Physical layout | Layout | Specific Requirements | 1.7.5 | The Bidders shall identify all the system components for the following DC functions with numbered references to the corresponding locations on the SLD: | 1
| JBS | Physical layout | Layout | Numbered DC system components in SLD | 1.7.5 | Module Arrays (fixed-tilt) | 1
| JBS | Physical layout | Layout | Numbered DC system components in SLD | 1.7.5 | Combiner and Recombiner Boxes | 1
| JBS | Physical layout | Layout | Numbered DC system components in SLD | 1.7.5 | Inverters | 1
| JBS | Physical layout | Layout | Numbered DC system components in SLD | 1.7.5 | DC cables | 1
| JBS | Physical layout | Layout | Numbered DC system components in SLD | 1.7.5 | DC connectors | 1
| JBS | Physical layout | Layout | Numbered DC system components in SLD | 1.7.5 | Disconnects, switches, protection, fuses | 1
| JBS | Physical layout | Layout | Numbered DC system components in SLD | 1.7.5 | Grounding | 1
| JBS | Physical layout | Layout | Numbered AC system components in SLD | 1.7.6 | Switchgear | 1
| JBS | Physical layout | Layout | Numbered AC system components in SLD | 1.7.6 | Transformers (including LV/MV and MV/132kV) | 1
| JBS | Physical layout | Layout | Numbered AC system components in SLD | 1.7.6 | AC cables | 1
| JBS | Physical layout | Layout | Numbered AC system components in SLD | 1.7.6 | AC connectors | 1
| JBS | Physical layout | Layout | Numbered AC system components in SLD | 1.7.6 | Protection | 1
| JBS | Physical layout | Layout | Numbered AC system components in SLD | 1.7.6 | Grounding | 1
| JBS | Physical layout | Layout | Numbered AC system components in SLD | 1.7.6 | Grid Connection | 1
| JBS | Physical layout | Layout | Numbered AC system components in SLD | 1.7.6 | Electric meter | 1
| JBS | Physical layout | Physical layout plan | Specific Requirements | 1.7.7 | Area needed per MWp installation | 2
| JBS | Physical layout | Physical layout plan | Specific Requirements | 1.7.7 | Standards and specifications for civil works | 2
| JBS | Physical layout | Physical layout plan | Specific Requirements | 1.7.7 | Dimensions of the field of installed equipment | 2
| JBS | Physical layout | Physical layout plan | Specific Requirements | 1.7.7 | Floor plans and elevations for all buildings, housing units, containers on site: e.g. , substations, the SCADA operational room, inverters, O&M, storage facilities | 1
| JBS | Physical layout | Physical layout plan | Specific Requirements | 1.7.7 | Detailed view of the distribution of inverters and connections to the PV string/array | 1
| JBS | Physical layout | Physical layout plan | Specific Requirements | 1.7.7 | Detailed top view of the PV mounting structure, including module sizes and spacing between the module rows | 1
| JBS | Physical layout | Physical layout plan | Specific Requirements | 1.7.7 | Detailed side and front view of the PV mounting structure | 1
| JBS | Physical layout | Physical layout plan | Specific Requirements | 1.7.7 | Detailed top view of electrical cabling interconnections | 1
| JBS | Physical layout | Physical layout plan | Specific Requirements | 1.7.7 | Dimensions of cable trenches | 2
| JBS | Physical layout | Physical layout plan | Specific Requirements | 1.7.7 | Dimensions and weight bearing capacities of access and maintenance roads, with a description of the required vehicles for transporting materials | 2
| JBS | Physical layout | Physical layout plan | Specific Requirements | 1.7.7 | Construction staging and parking areas | 2
| JBS | Physical layout | Physical layout plan | Specific Requirements | 1.7.7 | Location of the system metering and grid connection point | 1
| JBS | Physical layout | Auxiliary equipment | Specific Requirements | 1.7.8 | The earthing system shall consist of main copper earthing mesh along with copper earth bars installed at various locations around the parameter of plant. Subsidiary branch copper connections shall be made between the main earthing mesh and various items of the plant, metal frame works and housings etc. | 2
| JBS | Physical layout | Auxiliary equipment | Specific Requirements | 1.7.8 | The earthing system shall provide over-voltage protection system connected to proper earth mats. | 2
| JBS | Physical layout | Auxiliary equipment | Specific Requirements | 1.7.8 | The Bidder shall carry out site tests for soil resistivity to determine the parameters of the earthing system. | 2
| JBS | Physical layout | Auxiliary equipment | Specific Requirements | 1.7.8 | Provide complete indicating, regulating, controlling, protecting and interlocking equipment necessary for safe and efficient operation of the plant and substation, including complete protection scheme. | 1
| JBS | Physical layout | Auxiliary equipment | Specific Requirements | 1.7.8 | Protective Equipment & Interlocking Devices complies with IEC-60255 | 2
| JBS | Physical layout | Auxiliary equipment | Specific Requirements | 1.7.8 | The outline of protection schemes shall be shown on the single line diagram (SLD) | 1
| JBS | Physical layout | Auxiliary equipment | Specific Requirements | 1.7.8 | All parts of the installation are covered by two high speed protection schemes, which shall be independent to avoid common mode failures | 1
| JBS | Physical layout | Auxiliary equipment | Specific Requirements | 1.7.8 | The protection equipment shall be complete with all relay panels, instruments, meters, interposing current and voltage transformers, transducers and all auxiliary equipment. | 2
| JBS | Physical layout | Auxiliary equipment | Specific Requirements | 1.7.8 | The Bidder shall include a fire prevention and response plan | 1
| JBS | Physical layout | Auxiliary equipment | Specific Requirements | 1.7.8 | The fire prevention and response plan shall include a mobile fire protection system | 2
| JBS | Physical layout | Auxiliary equipment | Specific Requirements | 1.7.8 | The fire prevention and response plan shall include a fire alarm und detection system with a main panel in the control room | 1
| JBS | Physical layout | Auxiliary equipment | Specific Requirements | 1.7.8 | The fire prevention and response plan shall include carbon dioxide fire extinguishers for control room, indoor building and for outdoor installations in the switchyard. | 2
| JBS | Physical layout | Auxiliary equipment | Specific Requirements | 1.7.9 | The documentation includes design drawings having accurate scales, | 2
| JBS | Physical layout | Auxiliary equipment | Specific Requirements | 1.7.9 | The documentation includes clearly labelled objects and figures annotated in English language. | 1
| JBS | Physical layout | Auxiliary equipment | Specific Requirements | 1.7.9 | The scope of the documentation shall cover at least the requirements of IEC 62446. | 1
| JBS | Workflow, Project Management Plan and Timelines | Project schedule / Project management | Project schedule | 1.8.1 | Provide installation schedule in compliance with sub-clause 8.2 of Particular Conditions (Time for Completion is 225 days after Commencement Date). | 1 | [6 empty] | Find sub-clause 8.2 of Particular Conditions
| JBS | Workflow, Project Management Plan and Timelines | Project schedule / Project management | Project schedule | 1.8.1 | Provide work breakdown structures, activity decomposition and sequencing and dependability with the baseline schedule clearly showing the critical path | 1
| JBS | Workflow, Project Management Plan and Timelines | Project schedule / Project management | Project schedule | 1.8.1 | Schedule of tasks | 1
| JBS | Workflow, Project Management Plan and Timelines | Project schedule / Project management | Project schedule | 1.8.1 | Interdependencies between the tasks | 1
| JBS | Workflow, Project Management Plan and Timelines | Project schedule / Project management | Project schedule | 1.8.1 | Interdependencies of tasks with equipment order and delivery times | 1
| JBS | Workflow, Project Management Plan and Timelines | Project schedule / Project management | Project schedule | 1.8.1 | Preparatory work that can be done in advance | 3 | [7 empty] | information
| JBS | Workflow, Project Management Plan and Timelines | Project schedule / Project management | Project schedule | 1.8.1 | Parallel processing of tasks | 2
| JBS | Workflow, Project Management Plan and Timelines | Project schedule / Project management | Project schedule | 1.8.1 | Key milestones to indicate that the progress in on schedule | 1
| JBS | Workflow, Project Management Plan and Timelines | Project schedule / Project management | Project schedule | 1.8.1 | Teams, the number and skills of personnel to be deployed for each task | 1
| JBS | Workflow, Project Management Plan and Timelines | Project schedule / Project management | Project schedule | 1.8.1 | Schedule Performance Index (SPI) | 2
| JBS | Workflow, Project Management Plan and Timelines | Project schedule / Project management | Project schedule | 1.8.2 | Average installation speed is greater than 5 MWp-per-week | 2
| JBS | Workflow, Project Management Plan and Timelines | Project schedule / Project management | Quality Assurance | 1.8.3 | Quality control of delivered modules | 1
| JBS | Workflow, Project Management Plan and Timelines | Project schedule / Project management | Quality Assurance | 1.8.3 | Inspection of equipment delivery | 1
| JBS | Workflow, Project Management Plan and Timelines | Project schedule / Project management | Quality Assurance | 1.8.3 | Milestones for the completion of civil, mechanical, and electrical works | 1 | [7 empty] | dobble to 105 and 111
| JBS | Workflow, Project Management Plan and Timelines | Project schedule / Project management | Quality Assurance | 1.8.3 | Unit, sub-system, and system testing deadlines | 2
| JBS | Workflow, Project Management Plan and Timelines | Project schedule / Project management | Quality Assurance | 1.8.3 | Risk analysis and mitigation plan | 1
| JBS | Workflow, Project Management Plan and Timelines | Project schedule / Project management | Quality Assurance | 1.8.3 | System acceptance QA procedure by the Employer | 1
| RM | Supervisory Control and Data Acquisition (SCADA) | SCADA | Specific Requirements | 1.9.1 | Safe and redundant archive for operational data. | 1
| RM | Supervisory Control and Data Acquisition (SCADA) | SCADA | Specific Requirements | 1.9.1 | Remote access to all operational data for independent monitoring purposes shall be possible (NTDC requirements) | 1
| RM | Supervisory Control and Data Acquisition (SCADA) | SCADA | Specific Requirements | 1.9.1 | The system has to provide different access-levels with different access rights allocated. | 1
| RM | Supervisory Control and Data Acquisition (SCADA) | SCADA | Specific Requirements | 1.9.1 | Long-term availability of spare parts shall be assured. | 2
| RM | Supervisory Control and Data Acquisition (SCADA) | SCADA | Specific Requirements | 1.9.1 | Standardized communication protocols have to be used. | 2
| RM | Supervisory Control and Data Acquisition (SCADA) | SCADA | Specific Requirements | 1.9.2 | Control room to remotely monitor and manage the whole system, on a 24 x 7 basis, with the capability of Web-based information sharing | 1
| RM | Supervisory Control and Data Acquisition (SCADA) | SCADA | Specific Requirements | 1.9.2 | Frequent data collection (1 min interval), analysis, and display of the fundamental parameters of the system output and that of its sub-systems | 2
| RM | Supervisory Control and Data Acquisition (SCADA) | SCADA | Specific Requirements | 1.9.2 | Alarms/alerts and timely notification of key performance indicators | 1
| RM | Supervisory Control and Data Acquisition (SCADA) | SCADA | Specific Requirements | 1.9.2 | Monthly, quarterly, and yearly reporting of deviations from the guaranteed PR | 3 | [6 empty] | Related to O&M, not to scada system Cannot be evaluated at this stage.
| RM | Supervisory Control and Data Acquisition (SCADA) | SCADA | Specific Requirements | 1.9.2 | Bi-annual reports for the O&M service contract: system availability, system output (characterisation of spatial and temporal variations), capacity factor, degradation trends, average and cumulative output | 3 | [6 empty] | Cannot be evaluated at this stage. | statement
| RM | Supervisory Control and Data Acquisition (SCADA) | SCADA | Specific Requirements | 1.9.2 | Data must be readily available for the fulfilment of all warranties and performance guarantees | 1 | [6 empty] | Cannot be evaluated at this stage. | statement
| RM | Supervisory Control and Data Acquisition (SCADA) | SCADA | Specific Requirements | 1.9.2 | Network analysis with a closed feedback loop | 2
| RM | Supervisory Control and Data Acquisition (SCADA) | SCADA | Specific Requirements | 1.9.2 | Metering, interfaces, and protection | 2
| RM | Supervisory Control and Data Acquisition (SCADA) | SCADA | Specific Requirements | 1.9.2 | Data logging at intervals of not less than one minute, processing, transmission, and back-up | 1 | [7 empty] | not more (!)
| RM | Supervisory Control and Data Acquisition (SCADA) | SCADA | Specific Requirements | 1.9.2 | Data rate shall be 1HZ | 2
| RM | Supervisory Control and Data Acquisition (SCADA) | SCADA | Specific Requirements | 1.9.2 | Equipment condition monitoring | 2
| RM | Supervisory Control and Data Acquisition (SCADA) | SCADA | Specific Requirements | 1.9.2 | Status of overvoltage protection and grounding protection DC | 2
| RM | Supervisory Control and Data Acquisition (SCADA) | SCADA | Specific Requirements | 1.9.2 | Separate inverter, zone, and string level (current and voltage) monitoring | 1
| RM | Supervisory Control and Data Acquisition (SCADA) | SCADA | Specific Requirements | 1.9.2 | String, array, and combiner box measurements | 2
| RM | Supervisory Control and Data Acquisition (SCADA) | SCADA | Specific Requirements | 1.9.2 | Consolidated meteorological data collection and presentation (temperature, weather, and irradiation measurements) | 2
| RM | Supervisory Control and Data Acquisition (SCADA) | SCADA | Specific Requirements | 1.9.2 | Back-up power for a minimum of twelve hours | 1
| RM | Supervisory Control and Data Acquisition (SCADA) | SCADA | Specific Requirements | 1.9.2 | Data protocol shall be provided | 2
| RM | Supervisory Control and Data Acquisition (SCADA) | SCADA | Specific Requirements | 1.9.2 | Data shall be provided via FTP (Push/Pull) to the Employer | 1
| RM | Supervisory Control and Data Acquisition (SCADA) | SCADA | Specific Requirements | 1.9.2 | The data shall be available for export in ASCII format | 3
| RM | Supervisory Control and Data Acquisition (SCADA) | SCADA | Specific Requirements | 1.9.2 | All communication/data cables outside of buildings must be fiber-optic cables | 1
| RM | Supervisory Control and Data Acquisition (SCADA) | SCADA | Specific Requirements | 1.9.3 | IT systems architecture is described | 2
| RM | Supervisory Control and Data Acquisition (SCADA) | SCADA | Specific Requirements | 1.9.3 | The Bidder shall provide hardware and software descriptions of servers, bus drivers, communication cables, the security and information exchange protocols for the data management | 3
| RM | Supervisory Control and Data Acquisition (SCADA) | SCADA | Specific Requirements | 1.9.3 | The Bidder shall provide business processes of how it will be used to deliver timely information for preventive and corrective measures and how to back-up data. | 2
| RM | Meteorological Sensors | Auxiliary Systems | Specific Requirements | 1.10.1 | Irradiation and temperature measurements are to be recorded at intervals of 15 min or less. | 1
| RM | Meteorological Sensors | Auxiliary Systems | Specific Requirements | 1.10.1 | The equipment should have the capability of recording and storing data for 24 hours using auxiliary DC power. | 1 | [6 empty] | Should be priority 1 question
| RM | Meteorological Sensors | Auxiliary Systems | Specific Requirements | 1.10.1 | Measurement equipment fits to the environmental conditions of the area. | 2
| RM | Meteorological Sensors | Auxiliary Systems | Specific Requirements | 1.10.2 | The irradiation measurement equipment should be calibrated by an independent certified third party at least every two years. The calibration must be traceable to international standards. | 1 | [6 empty] | Should be checked in list of deviations
| RM | Meteorological Sensors | Auxiliary Systems | Specific Requirements | 1.10.2 | Seven pyranometers shall be placed : three for measuring the horizontal plane irradiation and the others for the in-plane irradiation. | 1 | [6 empty] | As in 1.10.2, it is seven pyranometer per system, please clarify the word "per system" | 1.1.1: "100 MWp (DC capacity at Standard Testing Conditions, abbreviated STC … hereinafter called 'the System') "
| RM | Meteorological Sensors | Auxiliary Systems | Specific Requirements | 1.10.2 | The pyranometers should conform to the standards of ISO 9060 (SR5: secondary standard) or the WMO classification, and IEC 60904. | 1 | [6 empty] | Do we need to know some parameter values according to standards mentioned or just a statement of comlience with the standard would be sufficient? | compliance will be necessary, no data due diligence right now.
| RM | Meteorological Sensors | Auxiliary Systems | Specific Requirements | 1.10.2 | A sensor calibration tolerance of within +/- 2% | 2
| RM | Meteorological Sensors | Auxiliary Systems | Specific Requirements | 1.10.2 | Contemporary best-in-class commercial specifications are shown in Schedule A. | 2 | [6 empty] | find schedule A and link to it | ?? page ER-57
| RM | Meteorological Sensors | Auxiliary Systems | Specific Requirements | 1.10.2 | The ground based sensor data is to be supplemented with satellite data to quantify longer term variations | 2 | [6 empty] | Cannot be evaluated at this stage.
| RM | Meteorological Sensors | Auxiliary Systems | Specific Requirements | 1.10.3 | Ambient air and the module temperature shall be measured at every 5 installed MWp in conformity with IEC 60751 AA | 1
| RM | Meteorological Sensors | Auxiliary Systems | Specific Requirements |  | The dependence of the System and sub-systems performance on temperature variations should be characterised by the SCADA. | 3
| RM | Meteorological Sensors | Auxiliary Systems | Specific Requirements | 1.10.4 | Provide a weather monitoring station at a minimum of four different locations per System with redundant humidity sensors, a rain gauge, and a wind profiling unit/anemometer (speed and direction), preferably capable of data telemetry or other electronic connectivity to the SCADA server. | 2
| RM | Meteorological Sensors | Auxiliary Systems | Specific Requirements | 1.10.5 | Use of consolidated measuring equipment, supported by an integrated UPS, with the above-mentioned functionality and modelling software capable of predictive functions will be required. | 2
| RM | Site Preparation and site access | Site Preparation and site access | Specific Requirements | 1.11.1 | The Bidder shall provide foundations and structures in accordance with the actual soil conditions. | 1 | [7 empty] | refer to Soil study
| RM | Earthworks | Site Preparation and site access | Specific Requirements | 1.12 | Within the plant boundary limits, access roads to all stations shall be suitable for heavy load trucks (axle load: min. 12 tonn). | 1
| RM | Earthworks | Site Preparation and site access | Specific Requirements | 1.12 | Cable trench design (depth, cable bedding, filling material) to prevent damage to underground cables in trenches, e.g., by bedding material, rodents or other means. | 2
| RM | Earthworks | Site Preparation and site access | Specific Requirements | 1.12 | Position and specification of underground cable connections must be documented during installation | 1 | [6 empty] | Cannot be avaluated at this stage.
| RM | Earthworks | Site Preparation and site access | Specific Requirements | 1.12, 1.13.4, 1.7.7 | Cross-sections of foundations for stations shall be provided, including explanation of the foundations laying down, height, penetration, and method of installing foundation posts, mounting fixtures | 1
| RM | Earthworks | Site Preparation and site access | Design factors to be provided | 1.12 | All earth works required have to be specified and included in the offer | 1
| RM | Earthworks | Site Preparation and site access | Specific Requirements | 1.12 | After completion of construction and all earthworks ground shall be levelled and stabilized. | 1 | [7 empty] | (maintanance, dust)
| RM | Earthworks | Site Preparation and site access | Specific Requirements | 1.12 | Pathways shall be covered with sufficient material to minimize dust swirling. | 2
| RM | Earthworks | Site Preparation and site access | Specific Requirements | 1.12 | In other internal areas seeds of local herb or grass should be sowed. | 2
| RM | Mounting | Mounting | Specific Requirements | 1.13.1 | The system is fixed-tilted. Tilt angle is specified. | 1
| RM | Mounting | Mounting | Specific Requirements | 1.13.3 | Mounting structure is made of durable material, resistant to sandstorms and compatible with the module frame material so as to avoid any adverse electrolytic/galvanic effects. | 1 | [6 empty] | Information about materials to be known before evaluation. | right
| RM | Mounting | Mounting | Specific Requirements | 1.13.3 | Mounting system resists high wind speeds (up to 40 m/s) | 1
| RM | Mounting | Mounting | Specific Requirements | 1.13.3 | Mounting system resists corrosion (passing the salt spray test IEC 61701, among other verification), | 1 | [6 empty] | Information about materials to be known before evaluation. | right
| RM | Mounting | Mounting | Specific Requirements | 1.13.3 | Mounting system resists UV induced degradation | 1
| RM | Mounting | Mounting | Specific Requirements | 1.13.5 | All fastening structures must be verified for durability and resistance to environmental degradation for 25 years | 1 | [6 empty] | What sort of mechanism is required for verification? | Sub structure description / materials double to line 172 - 175
| RM | Mounting | Mounting | Specific Requirements | 1.13.5 | Stainless steel fasteners with anti-seize lubricant are provided | 3
| RM | Mounting | Mounting | Specific Requirements | 1.13.5 | The structural elements consist of anodized aluminium, galvanised steel as per ASTM A123/A 123M, or materials with equivalent if not better properties. | 2 | [6 empty] | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? | no, just a statement of compliance
| RM | Mounting | Mounting | Specific Requirements | 1.13.5 | The applicable construction codes for each structural element are quoted | 2
| RM | Mounting | Mounting | Specific Requirements | 1.13.7 | The mounting structure comes with an anti-theft protection to impede demounting of modules. | 2 | [6 empty] | Priority needs to be disscussed | 24/7 personell on site solid wall arround site
| RM | Mounting | Mounting | Specific Requirements | 1.13.8 | The mounting structures must be earthed | 1
| RM | Mounting | Mounting | Specific Requirements | 1.13.9 | Specific site conditions have been considered. | 1 | [6 empty] | Needs to be discussed. | … specific requirements of the soil conditions Static
| RM | Mounting | Mounting | Standards | 1.13.9 | IEC 61730 (as above) | 1 | [6 empty] | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? | no, just a statement of compliance
| RM | Mounting | Mounting | Standards | 1.13.9 | STS 531 | 1 | [6 empty] | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? | no, just a statement of compliance
| RM | Mounting | Mounting | Standards | 1.13.9 | IEC 61730 | 1 | [6 empty] | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? | no, just a statement of compliance
| RM | Mounting | Mounting | Standards | 1.13.9 | STS 531 | 3 | [6 empty] | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? | douple to line 184 STS: SwissTestService STS 531 is accreditation number of test center http://www.sqts.ch
| MAW | Modules | Modules | Guarantees | 1.14.1 | The specifications match the the requirements mentioned in Schedule B. | 1
| MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Bills of Materials, BoMs: (glass, encapsulant, backsheet, ribbon, adhesives, cable, junction box, connector) | 1
| MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Maximum rated power | 1
| MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Rated power tolerance | 1
| MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Minimum efficiency at 200 W/m² (25°, AM 1.5) | 1
| MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Power conversion efficiency at STC | 3
| MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Fill factor | 3
| MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Series fuse rating | 3
| MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Connector type | 2
| MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Cable length | 3
| MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Materials and workmanship warranty of a minimum of 10 years | 1
| MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Power warranty/performance guarantee of a minimum of 25 years: the power output should not fall below 90% within 10 years, and below 80% within 25 years; linear warranty mandatory | 1
| MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Cross-sectional view of the module materials | 3
| MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Type of cells comprising the module, and number of cells in series | 1 | [7 empty] | manufacturer
| MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Use of integrated bypass diodes | 3
| MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Voltage at the maximum power point | 1
| MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Current at the maximum current point | 1
| MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Open-circuit voltage | 1
| MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Short-circuit current | 1 |  |  | x
| MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Maximum system voltage | 1 | [7 empty] | … at SK-II safety class
| MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Temperature coefficient of short-circuit current | 2 | [6 empty] | What range is acceptable | There is as small range anyway Will result in the PR losses
| MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Temperature coefficient of open-circuit voltage | 2 | [6 empty] | What range is acceptable | There is as small range anyway Will result in the PR losses
| MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Temperature coefficient of maximum power | 2 | [6 empty] | What range is acceptable | There is as small range anyway Will result in the PR losses
| MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Operating temperature range and nominal operating cell temperature NOCT | 1 | [6 empty] | What range is acceptable | There is as small range anyway Will result in the PR losses
| MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Tolerance to wind (maximum load) impact (mechanical load) | 1 | [7 empty] | minimum 2400 Pa
| MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Relative Power Conversion Efficiency reduction and I-V curves for different light intensities / weak light efficiency | 2 | [7 empty] | minimum for 200 W/m²
| MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Compatibility to different inverter designs | 3
| MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Dimensions and weight | 3
| MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Type of frame with weatherproof specifications | 3
| MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Junction box degree of protection (IP class) | 2 | [6 empty] | Which class is required for what type of location in the system? | IP65 minimum
| MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Manufacturers installation guidelines | 1
| MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Manufacturers confirmation for the suitability of module for specific weather conditions and the high UV-radiation | 1 | [7 empty] | especially reliability at high UV irridiance / Product warranty
| MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Provide guarantees and data sheets (to be transferred to Employer upon COD) | 1
| MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Specify number of modules and total MWp to be provided | 1
| MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Degradation Curve from Manufacturer | 1
| MAW | Modules | Modules | Design factors to be provided | 1.14.2 | Modules per box and 40 feet container | 2
| MAW | Modules | Modules | Standards (as applicable to crystalline silicion or thin-film) | 1.14.3 | IEC 61215 | 1 | [6 empty] | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? | no, just a statement of compliance
| MAW | Modules | Modules | Standards (as applicable to crystalline silicion or thin-film) | 1.14.3 | IEC 61416 | [7 empty] | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? | not existing
| MAW | Modules | Modules | Standards (as applicable to crystalline silicion or thin-film) | 1.14.3 | IEC 61646 | 1 | [6 empty] | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? | no, just a statement of compliance
| MAW | Modules | Modules | Standards (as applicable to crystalline silicion or thin-film) | 1.14.3 | IEC 61730 | 1 | [6 empty] | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? | no, just a statement of compliance
| MAW | Modules | Modules | Standards (as applicable to crystalline silicion or thin-film) | 1.14.3 | IEC 60364-4-41 | 1 | [6 empty] | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? | no, just a statement of compliance 'protection against electric shock
| MAW | Modules | Modules | Standards (as applicable to crystalline silicion or thin-film) | 1.14.3 | IEC 61701 | 1 | [6 empty] | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? | no, just a statement of compliance
| MAW | Modules | Modules | Standards (as applicable to crystalline silicion or thin-film) | 1.14.3 | IEC 60904-1, IEC 60904-3 | 1 | [6 empty] | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? | no, just a statement of compliance
| MAW | Modules | Modules | Pre-shipment quality assurance | 1.14.4 | Pre-shipment flash tested data Quality assurance for PV modules on-site and in laboratory simulator must meet the class AAA requirements of IEC 60904-9. The sun simulator must be calibrated with a reference cell, which itself was calibrated by a member of the WPVS scheme, with a maximum uncertainty of Isc of 1%. unique barcode (SNr) and labelled performance headlines (P(mpp), I(sc), U(oc), I(mpp), U(mpp) maximum current, maximum voltage Positive power sorting | 1 | [6 empty] | Cannot be evaluated at this stage. | compliance necessary
| MAW | Modules | Modules | Pre-shipment quality assurance | 1.14.4 | All modules must undergo Electroluminiscense (EL) inspection with a resolution of minimum 4 MPixel prior to shipment. | 1 | [6 empty] | Cannot be evaluated at this stage. | compliance necessary
| MAW | Modules | Modules | Pre-shipment quality assurance | 1.14.4 | The EL pictures must be sharp (not possible to test at this time) and inspected by an independent module testing agency. | 3 | [6 empty] | Cannot be evaluated at this stage. | compliance necessary
| MAW | Modules | Modules | Pre-shipment quality assurance | 1.14.4 | A sufficient EVA cross linking has to be verified per production line through a gel content test supervised by an accredited (IEC 17025 or national pendant) independent certified module testing agency. | 1 | [6 empty] | Cannot be evaluated at this stage. | compliance necessary
| MAW | Modules | Modules | Quality assurance on site | 1.14.5 | The modules shall undergo an incoming inspection at arrival on construction site. | 1 | [6 empty] | Cannot be evaluated at this stage. | stated and accepted
| MAW | Modules | Modules | Quality assurance on site | 1.14.5 | Electroluminescence: Per 40” container 20 Modules will undergo EL-inspection, in case of one or more major defect(s) in one of the modules, the container shall be rejected. In this case the supplier may inspect all modules on site of the same category within two days and remove the modules with major defects. This inspection shall be supervised by an independent third party named by the Employer. | 2 | [6 empty] | Cannot be evaluated at this stage. | compliance necessary
| MAW | Modules | Modules | Quality assurance on site | 1.14.5 | Real power: A sample size of IEC 60410 inspection level III of the modules (level II for crystalline modules) shall be flash tested for STC-power after arrival at site. | 2 | [6 empty] | Cannot be evaluated at this stage. | compliance necessary
| MAW | Modules | Modules | Quality assurance on site | 1.14.5 | Real power: The STC-power shall be measured on a class AAA simulator (IEC 60904) which is calibrated with a primary calibrated reference cell (reference cell for example calibrated by NREL/USA or AIST/Japan or comparable institution providing first level calibration, uncertainty of Isc max. 1%) by an independent laboratory. From the results the percentage of deviation the STC flash tests of the Manufacturer for the tested lot shall be calculated to establish the initial correction factor for STC-power. | 2 | [6 empty] | Cannot be evaluated at this stage.
| MAW | Modules | Modules | Quality assurance on site | 1.14.5 | Real power: From the tested lot a 2nd sample size of IEC 60410 inspection level II of the modules (level I for crystalline modules) shall be exposed at site to natural sun light for at least 250 kWh/m² (crystalline modules 25 kWh) to achieve the light induced degradation. After the exposure the STC-power shall be measured with the same test procedure. | 2 | [6 empty] | Cannot be evaluated at this stage.
| MAW | Modules | Modules | Quality assurance on site | 1.14.5 | Real power: From the results the percentage of deviation of STC flash tests at arrival shall be calculated and added to the initial correction factor. The result shall be the final correction factor at acceptance. The final correction factor shall be applied to all STC flash tests of the manufacturer. The so established final DC power at acceptance shall become the relevant DC power of the system and for the PR calculation. | 2 | [6 empty] | Cannot be evaluated at this stage.
| MAW | Modules | Modules | Quality assurance on site | 1.14.5 | Real power: If the final DC power at acceptance is below the nameplate power of all modules, the Employer may demand that the price of the complete system shall be reduced by the same percentage of the shortfall times 1.2 for liquidated damages or the contractor will have to install more power at its own costs or combination of both. | 2 | [6 empty] | Cannot be evaluated at this stage.
| MAW | Modules | Modules | Quality assurance on site | 1.14.5 | Real power: If the final DC power at acceptance is higher than the nameplate power the price of the complete system will not be changed. | 3 | [6 empty] | Cannot be evaluated at this stage.
| MAW | Modules | Modules | Quality assurance on site | 1.14.5 | Power at 200 W/m2: For the 2 nd real power sample the efficiency at 200 W/m² shall be measured with the same test procedure and must be equal or more than 95% of the efficiency at STC for more than 90% of the samples. | 2 | [6 empty] | Cannot be evaluated at this stage.
| MAW | Modules | Modules | Quality assurance on site | 1.14.5 | One module per 3 MWp will undergo: Peel-Off test. Minimum peel off force shall be 60 N/cm | 2 | [6 empty] | Cannot be evaluated at this stage.
| MAW | Modules | Modules | Quality assurance on site | 1.14.5 | One module per 3 MWp will undergo: If EVA is used as encapsulant: EVA cross-linking analysis, Soxhlet analysis or comparable. Min. cross-linking rate > 75%. | 2 | [6 empty] | Cannot be evaluated at this stage.
| MAW | Modules | Modules | Quality assurance on site | 1.14.5 | One module per 3 MWp will undergo: PID test according to IEC 62804: Max accepted power loss is 5%; the Employer has the right to decide which version of the tests offered by IEC 62804 is applicable | 2 | [6 empty] | Cannot be evaluated at this stage.
| MAW | Modules | Modules | Quality assurance on site | 1.14.5 | One module per 3 MWp will undergo: Wet leakage test according to IEC 61215. Minimum insulation shall be >40mOhm*module area (if module area is over 0.1 square meter) | 2 | [6 empty] | Cannot be evaluated at this stage.
| MAW | Modules | Modules | Quality assurance on site | 1.14.5 | One module per 3 MWp will undergo: Hot spot test: Sample size, One module per MWp, following IEC 61215/61646. Between shaded and unshaded cells max. ΔT < 15°C | 2 | [6 empty] | Cannot be evaluated at this stage.
| MAW | Modules | Modules | Quality assurance on site | 1.14.5 | One module per 3 MWp will undergo: UV stability: It must be proven by a widely acknowledged independent third party, that the modules do not show visible yellowing after exposure to UV irradiance corresponding to the estimated UV irradiance at the construction site in five years. | 2 | [6 empty] | Cannot be evaluated at this stage.
| MAW | Modules | Due Diligence | Quality Assurance | 1.14.6 | The bidder will bear the cost of the Quality assurance for PV modules on-site and in laboratory to be carried out by the Employer through an independent technical consultant up to 150,000 USD. | 1
| MAW | Modules | Modules | Pre-shipment quality assurance | 1.14.7 | Warranties and evidence shall be given by the bidder that their selected modules have been tested for susceptibility to Potential Induced Degradation (PID). | 1
| MAW | Modules | Credentials | Project references | 1.14.8 | To show the proven technology a minimum of 500MW of proposed product type series must be in operation and reference projects shall be named. | 1 | [6 empty] | Related to project references
| MAW | DC Cables | DC Cables | Specific Requirements | 1.15.1 | Are Ohmic losses less than 1% at full power? | 1 | [7 empty] | DC+AC losses < 2%
| MAW | DC Cables | DC Cables | Design factors to be provided | 1.15.2 | String cable shall be of the following type: single conductor type, copper, 1000 V / Class II (according to protection class II / 1000V, IEC 61140, single core cable, tinned copper conductor, XLPE Insulation, double EVA jacket (resistant to heat and cold, resistant to ozone, UV, oil and chemicals), Temperature: 90 º C (Temperature Max. Allowable: 120 º C), Halogen free | 1 | [6 empty] | It should be in accordance with the inverter values. | possibly 1500V for such system design
| MAW | DC Cables | DC Cables | Design factors to be provided | 1.15.2 | Connectors of Modules and string cables shall be connected of self-locking type, have IP65 rating and shall be from same manufacturer and type | 1
| MAW | DC Cables | DC Cables | Design factors to be provided | 1.15.2 | The DC main (downstream of combiner box) wiring harness shall have the quality: Aluminum / Copper / 1000 V / Class II | 1 | [6 empty] | It should be in accordance with the inverter values. | possibly 1500V for such system design
| MAW | DC Cables | DC Cables | Design factors to be provided | 1.15.2 | All cables shall be capable of accommodating all electric loads without overheating. Current carrying capacity certificate is provided | 2 | [6 empty] | which related parameters to be checked
| MAW | DC Cables | DC Cables | Design factors to be provided | 1.15.2 | Cables shall be suitable for the environmental conditions at the project site, including UV protection (certified) | 2 | [6 empty] | UV protection certfied or in accordance to which standards.
| MAW | DC Cables | DC Cables | Design factors to be provided | 1.15.2 | Balance of electrical potential | 1 | [6 empty] | Need to be disscussed | equipotential bonding earthing mesh
| MAW | DC Cables | DC Cables | Design factors to be provided | 1.15.2 | Installation to be verified by measurement-protocols | 1 | [6 empty] | Cannot be evaluated at this stage. | blanc protocol
| MAW | DC Cables | DC Cables | Design factors to be provided | 1.15.2 | Technical documentation of DC-UV shall be provided by the Contractor | 3 | [7 empty] | ??
| MAW | DC Cables | DC Cables | Design factors to be provided | 1.15.2 | Clear and systematic labelling required | 1
| MAW | DC Cables | DC Cables | Design factors to be provided | 1.15.2 | Tests shall be carried out for response to fire (low smoke), damp heat, UV resistance, halogen free | 3 | [6 empty] | Cannot be evaluated at this stage. | Spec / Data sheet
| MAW | DC Cables | DC Cables | Design factors to be provided | 1.15.2 | Lifetime of 30 years is assured | 1 | [6 empty] | What proof is required. | Life time test of nonmetal materials IEC 60811-408:2012 / (DIN EN 60811-408; VDE 0473-811-408:2012-12) 30 y assurance never seen until today
| MAW | DC Cables | DC Cables | Design factors to be provided | 1.15.2 | Screening for lightning protection is provided | 3
| MAW | DC Cables | DC Cables | Design factors to be provided | 1.15.2 | Voltage rating shall be given | 2
| MAW | DC Cables | DC Cables | Design factors to be provided | 1.15.2 | Current carrying capacity shall be specified | 3
| MAW | DC Cables | DC Cables | Design factors to be provided | 1.15.2 | Over-current protection concept shall be followed. | 3 | [6 empty] | Importance to be discussed along with the stage at which it could be evaluated. | fuse size required by module spec
| MAW | DC Cables | DC Cables | Design factors to be provided | 1.15.2 | variation of number of cores x nominal cross-section | 3
| MAW | DC Cables | DC Cables | Design factors to be provided | 1.15.2 | shape of conductor | 3 | [6 empty] | What is the acceptable shape | ECSP / not relevant
| MAW | DC Cables | DC Cables | Design factors to be provided | 1.15.2 | nominal value of insulation thickness | 3 | [6 empty] | What is the acceptable Range | ECSP / not relevant
| MAW | DC Cables | DC Cables | Design factors to be provided | 1.15.2 | nominal value of sheath current capacity in air | 3 | [6 empty] | What is the acceptable Range | ECSP / not relevant
| MAW | DC Cables | DC Cables | Design factors to be provided | 1.15.2 | current carrying capacity in the ground | 2 | [6 empty] | What is the acceptable Range | ralf
| MAW | DC Cables | DC Cables | Design factors to be provided | 1.15.2 | weight | 2 | [7 empty] | kg/m
| MAW | DC Cables | DC Cables | Design factors to be provided | 1.15.2 | Characterisation of cable voltage drop and related power losses shall be provided | 2
| MAW | DC Cables | DC Cables | Design factors to be provided | 1.15.2 | Sizing of cables shall be specified according to the number of modules and strings per array | 1 | [7 empty] | voltage drop calculation
| MAW | DC Cables | DC Cables | Design factors to be provided | 1.15.2 | Sizing of main DC cable shall be determined to minimise the overall voltage drop between the PV arrays and inverters | 2 | [6 empty] | How can it be verified? | voltage drop calculation
| MAW | DC Cables | DC Cables | Design factors to be provided | 1.15.2 | Edge/bending protection shall be installed | 2
| MAW | DC Cables | DC Cables | Design factors to be provided | 1.15.2 | Underground cables shall be protected against damage from overpassing vehicles, damage by rodents | 2
| MAW | DC Cables | DC Cables | Design factors to be provided | 1.15.2 | Information about measurements to verify the Installation is provided | 3
| MAW | DC Cables | DC Cables | Design factors to be provided | 1.15.2 | Cable installation includes earthing and short-circuit protection | 3
| MAW | DC Cables | DC Cables | Standards | 1.15.3 | IEC 60228 | 3 | [6 empty] | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? | no, just a statement of compliance / not important Conductor dimensions
| MAW | DC Cables | DC Cables | Standards | 1.15.3 | IEC 60364-1 | 1 | [6 empty] | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient?
| MAW | DC Cables | DC Cables | Standards | 1.15.3 | IEC 60754 | 3 | [6 empty] | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? | not relevant Hand-held motor-operated electric tools - Safety
| MAW | DC Cables | DC Cables | Standards | 1.15.3 | IEC 61034 | 3 | [6 empty] | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? | not relevant smoke density of burning cables
| MAW | DC Cables | DC Cables | Standards | 1.15.3 | IEC 60811-2 | 2 | [6 empty] | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? | test methods for insulating and sheathing materials of electric and optical cables
| MAW | DC Cables | DC Cables | Standards | 1.15.3 | CSN-EN-ISO-4892 | 3 | [6 empty] | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? | see 263: Lifetime of 30 year lifetime / UV resistance lab-conditions
| MAW | DC Cables | DC Cables | Standards | 1.15.3 | IEC 60068:2011 - 12 | 3 | [6 empty] | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? | see 263: Lifetime of 30 year UV resistance sunlight
| MAW | DC Cables | DC Cables | Standards | 1.15.3 | IEC 60228 (Cable losses) | [7 empty] | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? | double to line 281
| MAW | DC Connectors | DC Connectors | Design factors to be provided | 1.16.1 | High current rating | 2 | [6 empty] | What is the acceptable Range | for information
| MAW | DC Connectors | DC Connectors | Design factors to be provided | 1.16.1 | Minimal contact resistance | 2 | [6 empty] | What is the acceptable Range | for information
| MAW | DC Connectors | DC Connectors | Design factors to be provided | 1.16.1 | Convenient handling | 3 | [6 empty] | How can it be verified? | for information
| MAW | DC Connectors | DC Connectors | Design factors to be provided | 1.16.1 | Broad compatibility | 3 | [7 empty] | assurance from both manufacturers if relvant
| MAW | DC Connectors | DC Connectors | Design factors to be provided | 1.16.1 | Incompatibility with AC connectors to avoid mistakes during installation | 2 | [7 empty] | unlikely
| MAW | DC Connectors | DC Connectors | Design factors to be provided | 1.16.1 | Force required to unlock connectors from cables, whether a tool is required for it or not | 3
| MAW | DC Connectors | DC Connectors | Standards | 1.16.2 | EN 50521 | 1 | [6 empty] | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? | PV Connectors no, just a statement of compliance
| MAW | DC Connectors | DC Connectors | Standards | 1.16.2 | IEC 60512 | 1 | [6 empty] | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? | Connectors E-Systems no, just a statement of compliance
| MAW | DC Connectors | DC Connectors | Standards | 1.16.3 | MC4 connectors are used, or comparable certified connectors. | 2 | [7 empty] | assurance from both manufacturers if relvant
| MAW | DC Junction Box | DC Junction Box | Design factors to be provided | 1.17.1 | At least IP54 | 1 | [6 empty] | DC Junction box is applicable in what conditions? | depending on DC Design
| MAW | DC Junction Box | DC Junction Box | Design factors to be provided | 1.17.1 | DC fuses shall permit up to maximum 1000 V (or 1500V if designed). String box design, including all operating elements shall satisfy safety requirements | 1 | [6 empty] | Will inverter voltage(1500V) effect the maximum voltage(1000V)? | depends on spec of inverter.
| MAW | DC Junction Box | DC Junction Box | Design factors to be provided | 1.17.1 | Monitored input-couples | 1
| MAW | DC Junction Box | DC Junction Box | Design factors to be provided | 1.17.1 | Load breaker switch of adequate size | 2
| MAW | DC Junction Box | DC Junction Box | Design factors to be provided | 1.17.1 | Class 2 DC surge arrestor | 1
| MAW | DC Junction Box | DC Junction Box | Design factors to be provided | 1.17.1 | Flexibility and maximum of input circuits | 2
| MAW | DC Junction Box | DC Junction Box | Design factors to be provided | 1.17.1 | Input wire size range | 3
| MAW | DC Junction Box | DC Junction Box | Design factors to be provided | 1.17.1 | Output wire size range | 3
| MAW | DC Junction Box | DC Junction Box | Design factors to be provided | 1.17.1 | Number of output conductors | 3
| MAW | DC Junction Box | DC Junction Box | Design factors to be provided | 1.17.1 | Maximum operating continuous current | 2
| MAW | DC Junction Box | DC Junction Box | Design factors to be provided | 1.17.1 | Number of output terminals | 3
| MAW | DC Junction Box | DC Junction Box | Design factors to be provided | 1.17.1 | Configurable for positive and negative grounded arrays | 2
| MAW | DC Junction Box | DC Junction Box | Design factors to be provided | 1.17.1 | Remote disconnection under load | 3
| MAW | DC Junction Box | DC Junction Box | Design factors to be provided | 1.17.1 | Maximum fuse size | 3
| MAW | DC Junction Box | DC Junction Box | Design factors to be provided | 1.17.1 | Touch-safe fuse holders | 2
| MAW | DC Junction Box | DC Junction Box | Design factors to be provided | 1.17.1 | Relative humidity | 2
| MAW | DC Junction Box | DC Junction Box | Design factors to be provided | 1.17.1 | Dust and heat protection | 1
| MAW | DC Junction Box | DC Junction Box | Design factors to be provided | 1.17.1 | Disconnection | 3
| MAW | DC Junction Box | DC Junction Box | Specifications | 1.17.2 | Flexibility and maximum number of input circuits | 3
| MAW | DC Junction Box | DC Junction Box | Specifications | 1.17.2 | Fuse Ampacity | 2 | [7 empty] | spec characteristic
| MAW | DC Junction Box | DC Junction Box | Specifications | 1.17.2 | Number of output terminals | 3
| MAW | DC Junction Box | DC Junction Box | Specifications | 1.17.2 | Maximum continuous output current | 3
| MAW | DC Junction Box | DC Junction Box | Specifications | 1.17.2 | Configurable for positive/negative grounded and floating arrays | 3
| MAW | DC Junction Box | DC Junction Box | Specifications | 1.17.2 | Ground fault detection | 2
| MAW | DC Junction Box | DC Junction Box | Specifications | 1.17.2 | Current monitoring | 1
| MAW | DC Junction Box | DC Junction Box | Specifications | 1.17.2 | Interruption with ground fault monitoring | 3
| MAW | DC Junction Box | DC Junction Box | Specifications | 1.17.2 | Transient surge suppression | 2
| MAW | DC Junction Box | DC Junction Box | Specifications | 1.17.2 | Touch-safe protective cover | 1
| MAW | DC Junction Box | DC Junction Box | Specifications | 1.17.2, 1.17.1 | Operating temperature | 2
| MAW | DC Junction Box | DC Junction Box | Specifications | 1.17.2, 1.17.1 | Relative humidity | 2
| MAW | DC Junction Box | DC Junction Box | Specifications | 1.17.2, 1.17.1 | NEMA 3R rating | 2 | [7 empty] | US-coding corresponds to IP
| MAW | DC Junction Box | DC Junction Box | Specifications | 1.17.2, 1.17.1 | Dimensions and weight | 3
| MAW | DC Junction Box | DC Junction Box | Specifications | 1.17.2, 1.17.1 | Monitoring interface for SCADA | 1
| MAW | DC Junction Box | DC Junction Box | Standards | 1.17.3 | EN 61000-6 | 1 | [6 empty] | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? | EMV no, just a statement of compliance
| MAW | DC Junction Box | DC Junction Box | Standards | 1.17.3 | EN 60439-1 | 1 | [6 empty] | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? | arcing fault / Störlichtbogen Verhalten no, just a statement of compliance
| MAW | DC Junction Box | DC Junction Box | Standards | 1.17.3 | EN 50178 | 1 | [6 empty] | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? | High currat devices no, just a statement of compliance
| MAW | Inverters | Warranty | Warranty option | 1.18.1 | The Bidder shall arrange a full-service package for the selected inverters for a product warranty period of 5 years, with an option to cover additional 20 years including provisions for any necessary replacements including O&M service plan guaranteeing 99% availability. | 1
| MAW | Inverters | Inverters | Strategic Reason for Inverter Selection | 1.18.2 | The distribution/centralization of inverters is explained | 2
| MAW | Inverters | Inverters | Strategic Reason for Inverter Selection | 1.18.2 | Balance of System (BOS) costs of inverter and labour | 1 | [7 empty] | financial bid
| MAW | Inverters | Inverters | Strategic Reason for Inverter Selection | 1.18.2 | Dust and heat protection | 1 | [7 empty] | derating?
| MAW | Inverters | Inverters | Strategic Reason for Inverter Selection | 1.18.2 | Increased fault tolerance | 2
| MAW | Inverters | Design | Strategic Reason for Inverter Selection | 1.18.2 | Optimising the inverter’s DC capacity with respect to the PV array | 2 | [6 empty] | Will be given in the PV Syst report? | PVSyst
| MAW | Inverters | Inverters | Strategic Reason for Inverter Selection | 1.18.2 | Physical placement | 2 | [6 empty] | Physical placement in complience with the overall design.
| MAW | Inverters | Inverters | Strategic Reason for Inverter Selection | 1.18.2 | Timely and effective monitoring at a granular/zoomed-in level | 1
| MAW | Inverters | Inverters | Strategic Reason for Inverter Selection | 1.18.2 | Available uptime | 1
| MAW | Inverters | Inverters | Strategic Reason for Inverter Selection | 1.18.2 | Ease of replacement | 2 | [6 empty] | How can it be verified? | installation guidelines
| MAW | Inverters | Inverters | Strategic Reason for Inverter Selection | 1.18.2 | Cost of maintenance | 2
| MAW | Inverters | Inverters | Strategic Reason for Inverter Selection | 1.18.2 | Consideration of master-slave designs | 2
| MAW | Inverters | Inverters | Strategic Reason for Inverter Selection | 1.18.2 | Description of MPP tracking | 2
| MAW | Inverters | Inverters | Strategic Reason for Inverter Selection | 1.18.2 | Concept of protection against overload, short-circuit, grid-failure, internal failure, over-temperature (de-rating), surge protection | 1 | [6 empty] | Its too general, needs to be reviewed. | failure codes and consquences (automatic/manual restart, throw away safety devices)
| MAW | Inverters | Inverters | Strategic Reason for Inverter Selection | 1.18.2 | Test run procedures and results for every WR in factory | 2 | [6 empty] | Cannot be evaluated at this stage
| MAW | Inverters | O&M | Guarantees | 1.18.2 | For central inverters concept: the bidder shall ensure with an undertaking from the manufacturer that the concerned skilled staff will be made available at the site within 24 hours of reporting the defect to the manufacturer. | 1
| MAW | Inverters | Inverters | Functionalities | 1.18.3 | Maximum Power Point Tracking (MPPT) and string/sub-array management | 1
| MAW | Inverters | Inverters | Functionalities | 1.18.3 | Matching grid voltage and frequency at point-of-coupling | 1
| MAW | Inverters | Inverters | Functionalities | 1.18.3 | Anti-islanding protection | 1
| MAW | Inverters | Inverters | Functionalities | 1.18.3 | Voltage regulation through reactive power support: remotely set point control for voltage stability | 1 | [6 empty] | 8.2 needs to ensure these questions are answered in the bids.
| MAW | Inverters | Inverters | Functionalities | 1.18.3 | Frequency regulation | 1 | [6 empty] | 8.2 needs to ensure these questions are answered in the bids.
| MAW | Inverters | Inverters | Functionalities | 1.18.3 | Voltage and frequency fault ride-through: no disconnection of the connection through voltage dip and change of active power generation, feed-in of reactive power during the fault for voltage stabilisation | 1 | [6 empty] | 8.2 needs to ensure these questions are answered in the bids.
| MAW | Inverters | Inverters | Functionalities | 1.18.3 | Limitation of voltage fluctuation due to switching operations and long-term flicker | 1 | [6 empty] | 8.2 needs to ensure these questions are answered in the bids.
| MAW | Inverters | Inverters | Functionalities | 1.18.3 | Limitation of short-circuit current | 1 | [6 empty] | 8.2 needs to ensure these questions are answered in the bids.
| MAW | Inverters | Inverters | Functionalities | 1.18.3 | Limitation of steady-stage voltage changes to 2% of the nominal value | 1
| MAW | Inverters | Inverters | Functionalities | 1.18.3 | Limitation of current harmonics and higher frequency components up to 9 kHz | 1
| MAW | Inverters | Inverters | Functionalities | 1.18.3 | Active power control reduction: remotely set point of control in case of network congestions or risk of system collapse, if deemed necessary | 1 | [6 empty] | 8.2 needs to ensure these questions are answered in the bids.
| MAW | Inverters | Monitoring | Functionalities | 1.18.3 | Advanced communication, with intelligent alerts/warnings, to the SCADA server | 1
| MAW | Inverters | Inverters | Functionalities | 1.18.3 | Calibrated power meter on AC side, integrated into power plant control system | 2
| MAW | Inverters | Inverters | Functionalities | 1.18.4 | The inverter design should take into account the requirements of the National Transmission and Despatch Company’s (NTDC) Grid Connection Code for PV systems (Refer Appendix-8) | 2 | [6 empty] | Link to code, define requirements | Operation permit from NTDC?! For device
| MAW | Inverters | Inverters | The 3-phase voltage imbalance at the grid connection point | 1.18.5 | Imbalance of negative sequence voltage less than 2% and 4% in the long and short run respectively | 2 | [6 empty] | 8.2 needs to ensure these questions are answered in the bids.
| MAW | Inverters | Inverters | The 3-phase voltage imbalance at the grid connection point | 1.18.5 | Imbalance of positive sequence voltage less than 1.3% and 2.6% in the long and short run respectively | 2 | [6 empty] | 8.2 needs to ensure these questions are answered in the bids.
| MAW | Inverters | Inverters | Specific Requirements | 1.18.6 | Specifications of table in Schedule C shall be met | 1 | [6 empty] | Link to table
| MAW | Inverters | Inverters | Design factors to be provided | 1.18.7 | Input voltage range (The voltage window for MPP tracking shall accommodate the expected degradation of the modules.) | 1
| MAW | Inverters | Inverters | Design factors to be provided | 1.18.7 | Maximum operating input current | 2
| MAW | Inverters | Inverters | Design factors to be provided | 1.18.7 | PV array configuration options: positive ground, negative ground | 1
| MAW | Inverters | Inverters | Design factors to be provided | 1.18.7 | DC input combiner options | 2
| MAW | Inverters | Inverters | Design factors to be provided | 1.18.7 | Integrated transformer/transformerless / Outside Dry Type Transformer | 1
| MAW | Inverters | Inverters | Design factors to be provided | 1.18.7 | Peak efficiency/ Weighted efficiency | 1
| MAW | Inverters | Inverters | Design factors to be provided | 1.18.7 | Efficiency variation for various AC loads | 3
| MAW | Inverters | Inverters | Design factors to be provided | 1.18.7 | MPP tracking efficiency | 3
| MAW | Inverters | Inverters | Design factors to be provided | 1.18.7 | Nominal power | 1
| MAW | Inverters | Inverters | Design factors to be provided | 1.18.7 | Nominal output voltage | 1
| MAW | Inverters | Inverters | Design factors to be provided | 1.18.7 | Output voltage range | 1
| MAW | Inverters | Inverters | Design factors to be provided | 1.18.7 | Maximum output current | 1
| MAW | Inverters | Inverters | Design factors to be provided | 1.18.7 | Standby power consumption | 2
| MAW | Inverters | Inverters | Design factors to be provided | 1.18.7 | Nominal output frequency, 3-phase | 1
| MAW | Inverters | Inverters | Design factors to be provided | 1.18.7 | Harmonic distortion | 2
| MAW | Inverters | Inverters | Design factors to be provided | 1.18.7 | Power factor at full load | 3
| MAW | Inverters | Inverters | Design factors to be provided | 1.18.7 | Dynamic power factor control | 3
| MAW | Inverters | Inverters | Design factors to be provided | 1.18.7 | Power curtailment range and unit steps | 2
| MAW | Inverters | Inverters | Design factors to be provided | 1.18.7 | Fault tolerance and automatic system recovery | 2
| MAW | Inverters | Inverters | Design factors to be provided | 1.18.7 | Operating temperature range | 1 | [6 empty] | What is the acceptable range? | 60°C Derating?
| MAW | Inverters | Inverters | Design factors to be provided | 1.18.7 | Conversion efficiency dependence on temperature | 2
| MAW | Inverters | Inverters | Design factors to be provided | 1.18.7 | Cooling method | 1
| MAW | Inverters | Inverters | Design factors to be provided | 1.18.7 | Detection of insulation faults | 1
| MAW | Inverters | Inverters | Design factors to be provided | 1.18.7 | Noise levels at a distance of five metres | 3
| MAW | Inverters | Inverters | Design factors to be provided | 1.18.7 | Humidity tolerance | 2
| MAW | Inverters | Inverters | Design factors to be provided | 1.18.7 | Dimensions and weight | 3
| MAW | Inverters | Inverters | Design factors to be provided | 1.18.7 | Anti-discharge, reverse polarity, and lightning protection | 2
| MAW | Inverters | Inverters | Design factors to be provided | 1.18.7 | Protection rating: NEMA 3R, IP54/IP55/IP60 | 1
| MAW | Inverters | Inverters | Standards | 1.18.8 | IEEE 1547 | 1 | [6 empty] | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? | no, just a statement of compliance Interconnecting Distributed Resources
| MAW | Inverters | Inverters | Standards | 1.18.8 | ANSI/IEEE C37.90-2 | nn | [6 empty] | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? | no, just a statement of compliance
| MAW | Inverters | Inverters | Standards | 1.18.8 | ANSI/IEEE C37.98 | nn | [6 empty] | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? | no, just a statement of compliance
| MAW | Inverters | Inverters | Standards | 1.18.8 | ANSI/IEEE C37.2 | nn | [6 empty] | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? | no, just a statement of compliance
| MAW | Inverters | Inverters | Standards | 1.18.8 | IEC 60255-21-1 | nn | [6 empty] | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? | no, just a statement of compliance
| MAW | Inverters | Inverters | Standards | 1.18.8 | IEC 60255-22-2 | nn | [6 empty] | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? | no, just a statement of compliance
| MAW | Inverters | Inverters | Standards | 1.18.8 | IEC 60255-5 | nn | [6 empty] | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? | no, just a statement of compliance
| MAW | Inverters | Inverters | Standards | 1.18.8 | IEEE 519 | nn | [6 empty] | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? | no, just a statement of compliance
| MAW | Inverters | Inverters | Standards | 1.18.8 | EN 50160 | nn | [6 empty] | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? | no, just a statement of compliance
| MAW | Inverters | Inverters | Standards | 1.18.8 | IEC 61000 | nn | [6 empty] | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? | no, just a statement of compliance
| MAW | Inverters | Inverters | Standards | 1.18.8 | IEC 60439-1 | nn | [6 empty] | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? | no, just a statement of compliance
| MAW | Inverters | Inverters | Standards | 1.18.8 | IEC 62109-1 | nn | [6 empty] | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? | no, just a statement of compliance
| MAW | Inverters | Inverters | Standards | 1.18.8 | IEC 62109-2 | nn | [6 empty] | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? | no, just a statement of compliance
| MAW | Inverters | Inverters | Standards | 1.18.8 | IEC 60529/IP20 | nn | [6 empty] | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? | no, just a statement of compliance
| MAW | Inverters | Inverters | Standards | 1.18.8 | IEC 60721-3-3 Class 3M3 | nn | [6 empty] | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? | no, just a statement of compliance
| MAW | Inverters | Inverters | Standards | 1.18.8 | TUV, VDE, or equivalent certification of passing the relevant standards | 1
| MAW | Inverters | Inverters | Manufacturers confirmation | 1.18.9 | The Bidder shall deliver a manufacturer's confirmation in his Bid for the suitability of the inverter for the specific weather conditions applicable in Bahawalpur Pakistan. | 1
| MAW | Inverters | Credentials | Project references | 1.18.10 | A minimum of 100 MWp of similar product/type must be in operation and reference projects shall be named. | 1
| MAW | Inverters | Inverters | Quality Assurance | 1.18.11 | Check of protection against overload, short-circuit, grid-failure, internal failure, over-temperature (de-rating), surge protection, detection of insulation faults of AC Cables. Bidder shall firmly specify the manufacturer, types and length of cables to be installed | 1 | [6 empty] | 8.2 needs to ensure these questions are answered in the bids.
| MAW | Inverters | Inverters | Quality Assurance | 1.18.11 | Test run in the field for maximum and EU-efficiency of all Inverters | 1 | [6 empty] | 8.2 needs to ensure these questions are answered in the bids.
| MAW | Inverters | Inverters | Quality Assurance | 1.18.11 | Test run and check of MPP tracking of all inverters | 1 | [6 empty] | 8.2 needs to ensure these questions are answered in the bids.
| MAW | Inverters | Inverters | Quality Assurance | 1.18.11 | The DC Power connected to an inverter is defined by the provided flash list of STC power of relevant modules corrected by the real power test defined in the Modules chapter (Clausel 1.14 in RfP) | 2 | [6 empty] | To be discussed | what is the question?
| MAW | Inverters | Inverters | Quality Assurance | 1.18.11 | The Bidder shall deliver detailed protocols of performance test run (warm power test) for every single inverter | 1 | [6 empty] | Cannot be evaluated at this stage
| MAW | Inverters | Inverters | Quality Assurance | 1.18.11 | After commissioning, 1 of 10 inverters will be measured on site (power curve and efficiency) by an approved independent technical consultant on behalf of the Employer. The on-site measurements shall be accepted by the Bidder as average values for all inverters | 1 | [6 empty] | Cannot be evaluated at this stage | compliance!
| MAW | Inverters | Inverters | Quality Assurance | 1.18.11 | Inverter measurement: a precision inverter measurement device LMG 500 (or better) | 2 | [6 empty] | To be discussed
| MAW | Inverters | Inverters | Quality Assurance | 1.18.11 | Inverter measurement: the closest installed temperature and irradiations sensors | 2 | [6 empty] | To be discussed
| MAW | Inverters | Inverters | Quality Assurance | 1.18.11 | Inverter measurement: the average mismatch and cable losses of the guaranteed yield analysis | 2 | [6 empty] | To be discussed
| MAW | Inverters | Due diligence | Quality Assurance | 1.18.12 | The Bidder accepts that the cost of the Quality assurance for Inverters to be carried by the Employer through an independent technical consultant shall be taken over by the successful bidder up to an amount of 100,000 USD. | 1
| JBU | AC Cabling | AC Cabling | Design factors to be provided | 1.19.1 | AC cable shall be of Copper. Rated voltage, nominal voltage between phase and neutral and nominal voltage between phases to be specified by the Bidder | 1
| JBU | AC Cabling | AC Cabling | Design factors to be provided | 1.19.1 | Appropriate sizing to minimise voltage drop and losses | 1 | [6 empty] | What is the appropriate size? | leeway to allow MPP tracking when module voltage drops. At least 10%. Ralf, ist Vital kriterium.
| JBU | AC Cabling | AC Cabling | Design factors to be provided | 1.19.1 | All cable shall be capable of accommodating all electrical loads without overheating | 3 | [6 empty] | How it can be checked? | ralf
| JBU | AC Cabling | AC Cabling | Design factors to be provided | 1.19.1 | Current carrying capacity: capable of operating at short-circuit currents to be provided | 3
| JBU | AC Cabling | AC Cabling | Design factors to be provided | 1.19.1 | Number and type of conductors, conductor's material, nominal cross-section, resistance and classification of wire to be specified by the Bidder | 3
| JBU | AC Cabling | AC Cabling | Design factors to be provided | 1.19.1 | Type of insulation material and thickness, sheath properties and thickness, external diameter | 3
| JBU | AC Cabling | AC Cabling | Design factors to be provided | 1.19.1 | Lifetime longer than 25 years | 1
| JBU | AC Cabling | AC Cabling | Design factors to be provided | 1.19.1 | Rated voltage | 1
| JBU | AC Cabling | AC Cabling | Design factors to be provided | 1.19.1 | Flame tested | 2
| JBU | AC Cabling | AC Cabling | Design factors to be provided | 1.19.1 | Bending radius | 1
| JBU | AC Cabling | AC Cabling | Design factors to be provided | 1.19.1 | Choice of single core or multi-core | 3
| JBU | AC Cabling | AC Cabling | Design factors to be provided | 1.19.1 | Core insulation (typically cross-linked polyethylene) | 2
| JBU | AC Cabling | AC Cabling | Design factors to be provided | 1.19.1 | Weight | 3
| JBU | AC Cabling | AC Cabling | Design factors to be provided | 1.19.1 | Packaging detail | 3
| JBU | AC Cabling | AC Cabling | Design factors to be provided | 1.19.1 | Cables shall be suitable for the environmental conditions at the project site, including UV protection (The Bidder shall provide certification from manufacturer) | 1
| JBU | AC Cabling | AC Cabling | Design factors to be provided | 1.19.1 | Installation to be verified by measurement-protocols | 1
| JBU | AC Cabling | AC Cabling | Design factors to be provided | 1.19.1 | Cable installation shall ensure grounding and short-circuit protection | 1
| JBU | AC Cabling | AC Cabling | Design factors to be provided | 1.19.1 | Sufficient and effective cable protection against attacks of rodents for any cabling underground or above is required | 1
| JBU | AC Cabling | AC Cabling | Standards | 1.19.2 | IEC 60502 | 1 | [6 empty] | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient?
| JBU | AC Cabling | AC Cabling | Standards | 1.19.2 | IEC 60364 | 1 | [6 empty] | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient?
| JBU | AC Cabling | AC Cabling | Standards | 1.19.2 | DIN-VDE-0276 | 1 | [6 empty] | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient?
| JBU | AC Cabling | AC Cabling | Standards | 1.19.2 | EN 60332-1-1 and EN 60332-2-1 | 1 | [6 empty] | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient?
| JBU | AC Cabling | AC Cabling | Specific Requirements | 1.19.3 | The runs of both the main DC and AC cables, in the System layout, should be adjusted to keep power losses below <1% at STC (Design calculations through cable loss simulation to be provided for review & comment). | 1 | [6 empty] | Part of system design | Kategorie ?
| JBU | AC Combiner Box | AC Combiner Box | Design factors to be provided | 1.20.1 | Fast and easy cable connections, whether special tool is required or not | 2
| JBU | AC Combiner Box | AC Combiner Box | Design factors to be provided | 1.20.1 | Rated voltage | 1
| JBU | AC Combiner Box | AC Combiner Box | Design factors to be provided | 1.20.1 | Rated current | 1
| JBU | AC Combiner Box | AC Combiner Box | Design factors to be provided | 1.20.1 | Class 2 AC surge arrestor | 1
| JBU | AC Combiner Box | AC Combiner Box | Design factors to be provided | 1.20.1 | Load breaker switch of adequate size | 1
| JBU | AC Combiner Box | AC Combiner Box | Design factors to be provided | 1.20.1 | Monitored input-couples | 2
| JBU | AC Combiner Box | AC Combiner Box | Design factors to be provided | 1.20.1 | Contact resistance | 3
| JBU | AC Combiner Box | AC Combiner Box | Design factors to be provided | 1.20.1 | Current carrying capacity | 2
| JBU | AC Combiner Box | AC Combiner Box | Design factors to be provided | 1.20.1 | Type of material | 2
| JBU | AC Combiner Box | AC Combiner Box | Design factors to be provided | 1.20.1 | Flame test | 1
| JBU | AC Combiner Box | AC Combiner Box | Design factors to be provided | 1.20.1 | Waterproof test | 1
| JBU | AC Combiner Box | AC Combiner Box | Design factors to be provided | 1.20.1 | Chemical resistance | 2
| JBU | AC Combiner Box | AC Combiner Box | Design factors to be provided | 1.20.1 | Halogen free | 2
| JBU | AC Combiner Box | AC Combiner Box | Design factors to be provided | 1.20.1 | Operating temperature range | 1
| JBU | AC Combiner Box | AC Combiner Box | Design factors to be provided | 1.20.1 | Connection method | 2
| JBU | AC Combiner Box | AC Combiner Box | Design factors to be provided | 1.20.1 | Locking force | 2
| JBU | AC Combiner Box | AC Combiner Box | Design factors to be provided | 1.20.1 | Insertion force | 2
| JBU | AC Combiner Box | AC Combiner Box | Design factors to be provided | 1.20.1 | Disengagement force | 3
| JBU | AC Combiner Box | AC Combiner Box | Design factors to be provided | 1.20.1 | External cable diameter range | 3
| JBU | AC Combiner Box | AC Combiner Box | Design factors to be provided | 1.20.1 | Stripping length of the individual wire | 1
| JBU | AC Combiner Box | AC Combiner Box | Design factors to be provided | 1.20.1 | Dimensions of conductor cross-section | 3
| JBU | AC Combiner Box | AC Combiner Box | Design factors to be provided | 1.20.1 | Weight | 3
| JBU | AC Combiner Box | AC Combiner Box | Standards | 1.20.2 | TUV 2 PIG 1915 AC Solar Connector certificate Or equivalent standard | 3 | [6 empty] | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient?
| JBU | AC Combiner Box | AC Combiner Box | Standards | 1.20.2 | IP 67 | 1
| JBU | AC Combiner Box | AC Combiner Box | Standards | 1.20.2 | EN 60529, DIN-VDE-0472 | 1 | [6 empty] | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient?
| JBU | Step-up Transformers/MV Switchgear | Step-up Transformers/MV Switchgear | Guarantees | 1.21.1 | Compatibility with NTDC grid connection code must be ensured | 1
| JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Design factors to be provided | 1.21.2 | 3-phase, double wound, continuously rated, oil-cooled, enclosed transformers, use of low loss core steel and close coupled copper windings | 1
| JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Design factors to be provided | 1.21.2 | Enclosure specifications (e.g., steel floor, fluid tight, sealed tank) | 3
| JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Design factors to be provided | 1.21.2 | Incoming terminals | 1
| JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Design factors to be provided | 1.21.2 | Outgoing terminals | 1
| JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Design factors to be provided | 1.21.2 | kVA rating | 1
| JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Design factors to be provided | 1.21.2 | Primary side voltage | 1
| JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Design factors to be provided | 1.21.2 | Secondary side voltage | 1
| JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Design factors to be provided | 1.21.2 | Vector group | 3
| JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Design factors to be provided | 1.21.2 | Insulation type | 1
| JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Design factors to be provided | 1.21.2 | Frequency rating | 2
| JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Design factors to be provided | 1.21.2 | Short-circuit impedance | 1
| JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Design factors to be provided | 1.21.2 | Own consumption | 3
| JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Design factors to be provided | 1.21.2 | No-load losses | 1
| JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Design factors to be provided | 1.21.2 | Efficiency | 1
| JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Design factors to be provided | 1.21.2 | Operating temperature range | 1
| JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Design factors to be provided | 1.21.2 | Maximum ambient temperature and altitude | 1
| JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Design factors to be provided | 1.21.2 | Humidity tolerance | 1
| JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Design factors to be provided | 1.21.2 | Cooling method | 1
| JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Design factors to be provided | 1.21.2 | Dimensions and weight | 3
| JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Design factors to be provided | 1.21.2 | Oil weight | 2
| JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Design factors to be provided | 1.21.2 | Protection system | 1
| JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Design factors to be provided | 1.21.2 | Auxiliary service lines | 2
| JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Design factors to be provided | 1.21.2 | Fittings with the transformer | 3
| JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Design factors to be provided | 1.21.2 | Noise levels | 2
| JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Design factors to be provided | 1.21.2 | Warranty and insurance | 2
| JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Design factors to be provided | 1.21.2 | Tests and inspection routines | 2
| JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Design factors to be provided | 1.21.2 | Operational data shall be logged in central operating system (e.g. oil temperature, oil level, pressure, Temperature probes (one per phase): Alarm and trip of cell etc.) | 1
| JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Design factors to be provided | 1.21.2 | All documentation, certificates and test protocols shall be provided | 2
| JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Standards | 1.21.3 | IEC 62446 | 1 | [6 empty] | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient?
| JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Standards | 1.21.3 | IEC 60076 | 1 | [6 empty] | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient?
| JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Standards | 1.21.3 | IEC 60085 | 1 | [6 empty] | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient?
| JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Standards | 1.21.3 | IEC 60214 | 1 | [6 empty] | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient?
| JBU | Step-up Transformers/MV Switchgear | Step up transformer (LV to MV) | Standards | 1.21.3 | IEC 60137 | 1 | [6 empty] | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient?
| JBU | Step-up Transformers/MV Switchgear | Due Diligence | Quality Assurance | 1.21.3 | Factory witness testing will be required for MV transformer and switchgear to be installed at this project. The cost of the due diligence to be carried by the Employer through an independent technical consultant will be taken over by the successful bidder up to an amount of 30,000 USD. | 1
| JBU | Step-up Transformers/MV Switchgear | MV Switchgear | Specific Requirements | 1.21.4 | MV Switchgears shall be SF6 gas insulated or VCB (Vacuum circuit breaker). | 1
| JBU | Step-up Transformers/MV Switchgear | MV Switchgear | Specific Requirements | 1.21.4 | The separating equipment shall be installed with visible disconnection (pivotable disconnectors). | 1 | [6 empty] | Cannot be evaluated at this stage
| JBU | Step-up Transformers/MV Switchgear | MV Switchgear | Specific Requirements | 1.21.4 | Interlocks will also be mechanically interlocked between line MV switchgears. | 1
| JBU | Step-up Transformers/MV Switchgear | MV Switchgear | Design factors to be provided | 1.21.4 | System nominal voltage | 1
| JBU | Step-up Transformers/MV Switchgear | MV Switchgear | Design factors to be provided | 1.21.4 | System maximum voltage | 1
| JBU | Step-up Transformers/MV Switchgear | MV Switchgear | Design factors to be provided | 1.21.4 | Rated lightning impulse voltage | 1
| JBU | Step-up Transformers/MV Switchgear | MV Switchgear | Design factors to be provided | 1.21.4 | Rated power frequency withstand voltage | 1
| JBU | Step-up Transformers/MV Switchgear | MV Switchgear | Design factors to be provided | 1.21.4 | Rated short circuit current | 1
| JBU | Step-up Transformers/MV Switchgear | MV Switchgear | Design factors to be provided | 1.21.4 | Rated duration of short circuit current | 2
| JBU | Step-up Transformers/MV Switchgear | MV Switchgear | Standards | 1.21.5 | IEC 62446 | 1 | [6 empty] | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient?
| JBU | Step-up Transformers/MV Switchgear | MV Switchgear | Standards | 1.21.5 | IEC 62271-200 | 1 | [6 empty] | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient?
| JBU | Step-up Transformers/MV Switchgear | MV Switchgear | Standards | 1.21.5 | IEC 60529 | 1 | [6 empty] | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient?
| JBU | Inverter/Transformer Station | Inverter/Transformer Station | Specific Requirements | 1.22 | Bidder shall firmly specify the number of stations, manufacturer, capacity and type of equipment. | 1
| JBU | Inverter/Transformer Station | Inverter/Transformer Station | Specific Requirements | 1.22 | All stations shall be equipped with fire and smoke detectors and alarm, connected to security and surveillance system | 1
| JBU | Inverter/Transformer Station | Inverter/Transformer Station | Specific Requirements | 1.22 | Fine sand filters shall be installed | 1
| JBU | Inverter/Transformer Station | Inverter/Transformer Station | Specific Requirements | 1.22 | Stations shall have regular electricity supply, and shall contain power outlet and light installations | 2
| JBU | Inverter/Transformer Station | Inverter/Transformer Station | Specific Requirements | 1.22 | Sufficient cooling and ventilation for operation of all installed components shall be ensured, considering the extreme ambient conditions. Air conditioning shall be provided. Own consumption of these systems shall be provided | 2
| JBU | Inverter/Transformer Station | Inverter/Transformer Station | Specific Requirements | 1.22 | All stations shall be equipped with adequate warning signs where applicable | 2
| JBU | Inverter/Transformer Station | Inverter/Transformer Station | Specific Requirements | 1.22 | All stations shall be equipped with first aid kit and fire extinguisher | 2
| JBU | Inverter/Transformer Station | Inverter/Transformer Station | Specific Requirements | 1.22 | The station shall enable the grounding of hardware and neutral will be left ground isolated | 1
| JBU | Inverter/Transformer Station | Inverter/Transformer Station | Specific Requirements | 1.22 | Every ten (10) or lesser number of stations shall be equipped with an earthing and short-circuiting equipment | 1
| JBU | Inverter/Transformer Station | Inverter/Transformer Station | Specific Requirements | 1.22 | Stations shall have sufficient interlocks | 3 | [6 empty] | To be discussed
| AR | HV Substation | HV Substation | Specific Requirements | 1.23.1 | The HV Substation includes the respective MV switch gears, Transformer MV/ HV. The HV connection is designed to connect to the HV line. | 3
| AR | HV Substation | HV Substation | Specific Requirements | 1.23.2 | Availability and delivery time of the chosen components is detailed | 1
| AR | HV Substation | HV Substation -HV part | Specific Requirements | 1.23.3 | The substation is separated into 2 parts: Medium Voltage part including HV transformer and HV portion of the plant excluding the HV transformer | 1
| AR | HV Substation | HV Substation -HV part | Specific Requirements | 1.23.3 | Double Busbar single breaker scheme shall be designed for HV portion of HV substation | 1
| AR | HV Substation | HV Substation -HV part | HV portion components | 1.23.3 | 132 kV Transformer Bays as per design | 1
| AR | HV Substation | HV Substation -HV part | HV portion components | 1.23.3 | 2x132 kV Line Bays | 1
| AR | HV Substation | HV Substation -HV part | HV portion components | 1.23.3 | 2x132 kV PT bays | 1
| AR | HV Substation | HV Substation -HV part | HV portion components | 1.23.3 | 132 kV Bus Coupler Bay | 1
| AR | HV Substation | HV Substation -HV part | HV portion components | 1.23.3 | Telecom and PLC Equipment | 1 | [6 empty] | Which speification are acepted
| AR | HV Substation | HV Substation -HV part | Standards | 1.23.3 | All the schemes including SCADA, PLC, protection scheme, control and monitoring scheme and other design factors, shall be in compliance with the NTDC grid code. | 1 | [6 empty] | Link to NTDC grid code
| AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | 3-phase, double wound, continuously rated, oil-cooled, enclosed transformers, use of low loss core steel and close coupled copper windings | 1
| AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | Enclosure specifications (e.g., steel floor, fluid tight, sealed tank) | 1
| AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | Incoming terminals | 1
| AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | Outgoing terminals | 1
| AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | kVA rating | 1
| AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | Primary side voltage | 1
| AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | Secondary side voltage | 1
| AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | Vector group | 3 | [6 empty] | to be discussed
| AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | Insulation type | 1
| AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | Frequency rating | 1
| AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | Short-circuit impedance | 1
| AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | Own consumption | 3
| AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | No-load losses | 1
| AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | Efficiency | 1
| AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | Operating temperature range | 1
| AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | Maximum ambient temperature and altitude | 1 | [6 empty] | to be discussed
| AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | Humidity tolerance | 2
| AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | Cooling method | 1
| AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | Dimensions and weight | 3
| AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | Oil weight | 3
| AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | Protection system | 1
| AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | Auxiliary service lines | 1
| AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | Fittings with the transformer | 3
| AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | Noise levels | 3
| AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | Warranty and insurance | 1
| AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | Tests and inspection routines | 1
| AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | Operational data shall be logged in central operating system (e.g. oil temperature, oil level, pressure, temperature probes (one per phase): Alarm and trip of cell etc.) | 2
| AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | All documentation, certificates and test protocols shall be provided | 2
| AR | HV Substation | HV Substation -MV/HV Transformer | Standards | 1.23.7 | IEC 62446 | 1 | [6 empty] | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient?
| AR | HV Substation | HV Substation -MV/HV Transformer | Standards | 1.23.7 | IEC 60076 | 1 | [6 empty] | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient?
| AR | HV Substation | HV Substation -MV/HV Transformer | Standards | 1.23.7 | IEC 60085 | 1 | [6 empty] | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient?
| AR | HV Substation | HV Substation -MV/HV Transformer | Standards | 1.23.7 | IEC 60214 | 1 | [6 empty] | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient?
| AR | HV Substation | HV Substation -MV/HV Transformer | Standards | 1.23.7 | IEC 60137 | 1 | [6 empty] | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient?
| AR | HV Substation | HV Substation -MV/HV Transformer | Standards | 1.23.7 | ASTM d-3487 | 1 | [6 empty] | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient?
| AR | HV Substation | HV Substation -MV/HV Transformer | Quality Assurance | 1.23.7 | Factory witness testing shall be required for MV/HV transformer and switchgear to be installed at this project. | 1 | [6 empty] | Cannot be evaluated at this stage
| AR | HV Substation | HV Substation -MV/HV Transformer | Quality Assurance | 1.23.7 | Type test reports from an independent reputable laboratory shall be submitted with the bid. | 1
| AR | HV Substation | Due Diligence | Quality Assurance | 1.23.7 | The cost of the due diligence for the HV station to be carried by the Employer through an independent technical consultant will be taken over by the successful bidder up to an amount of 30,000 USD. | 1
| AR | HV Substation | HV Substation -MV/HV Transformer | Design | 1.23.8 | The separating equipment shall be installed with visible disconnection (pivotable disconnectors). | 1 | [6 empty] | Cannot be evaluated at this stage
| AR | HV Substation | HV Substation -MV/HV Transformer | Design | 1.23.9 | Insulation with PCB (polychlorinated biphenyl) has not been used. | 1
| AR | HV Substation | HV Substation -MV/HV Transformer | Design | 1.23.10 | The preliminary design of the substation is submitted with the technical bid according to the requirements of Appendix 1 | 1 | [6 empty] | Link to Appendix 1
| AR | HV Substation | HV Substation -MV/HV Transformer | Energy Metering System | 1.23.11 | The Energy Metering System will be placed on the HV side of the substation | 1
| AR | HV Substation | HV Substation -MV/HV Transformer | Energy Metering System -NTDC specifications | 1.23.11 | Metering Equipment for Electric Energy Transfer between the Companies (Specification No. P-199-08) | 1
| AR | HV Substation | HV Substation -MV/HV Transformer | Energy Metering System -NTDC specifications | 1.23.11 | Energy Meters for Grid Metering (Specification No. P-202-2012) | 1
| AR | HV Substation | HV Substation -MV/HV Transformer | Energy Metering System -NTDC specifications | 1.23.11 | Voltage Transformers for Special Application (Energy Metering; Specifications No. P-206-05) | 1
| AR | HV Substation | HV Substation -MV/HV Transformer | Energy Metering System -NTDC specifications | 1.23.11 | Current Transformers for Special Application (spec.No P-205-2005) | 1
| AR | HV Switchgear | HV Switchgear | Project Schedule | 1.24.1 | The switchgear design and order time, for the 132 kV transmission line is detailed and corresponds with the envisaged project schedule. | 1
| AR | HV Switchgear | HV Switchgear | Functionalities | 1.24.1 | Nominal system voltage, kV 132 | 1
| AR | HV Switchgear | HV Switchgear | Functionalities | 1.24.1 | Rated voltage of switch gear, kV 145 | 1
| AR | HV Switchgear | HV Switchgear | Functionalities | 1.24.1 | Maximum system voltage, kV 145 | 1
| AR | HV Switchgear | HV Switchgear | Functionalities | 1.24.1 | Rated frequency, Hz 50 | 1
| AR | HV Switchgear | HV Switchgear | Design factors to be provided | 1.24.2 | Rated voltage | 1
| AR | HV Switchgear | HV Switchgear | Design factors to be provided | 1.24.2 | Short-duration power withstand frequency voltage | 3
| AR | HV Switchgear | HV Switchgear | Design factors to be provided | 1.24.2 | Rated lightning impulse withstand voltage | 3
| AR | HV Switchgear | HV Switchgear | Design factors to be provided | 1.24.2 | Rated frequency | 3
| AR | HV Switchgear | HV Switchgear | Design factors to be provided | 1.24.2 | Peak-withstand current | 2
| AR | HV Switchgear | HV Switchgear | Design factors to be provided | 1.24.2 | Short-circuit making current | 2
| AR | HV Switchgear | HV Switchgear | Design factors to be provided | 1.24.2 | Short-time withstand current | 2
| AR | HV Switchgear | HV Switchgear | Design factors to be provided | 1.24.2 | Short-circuit breaking current | 2
| AR | HV Switchgear | HV Switchgear | Design factors to be provided | 1.24.2 | Insulating medium | 2
| AR | HV Switchgear | HV Switchgear | Design factors to be provided | 1.24.2 | Second fault rating | 2
| AR | HV Switchgear | HV Switchgear | Design factors to be provided | 1.24.2 | Busbars | 3
| AR | HV Switchgear | HV Switchgear | Design factors to be provided | 1.24.2 | Rated normal current for busbars | 3
| AR | HV Switchgear | HV Switchgear | Design factors to be provided | 1.24.2 | Rated normal current for feeders | 3
| AR | HV Switchgear | HV Switchgear | Design factors to be provided | 1.24.2 | Degree of protection | 2
| AR | HV Switchgear | HV Switchgear | Design factors to be provided | 1.24.2 | Second internal arc rating | 3
| AR | HV Switchgear | HV Switchgear | Design factors to be provided | 1.24.2 | Circuit breakers: protection and metering | 1
| AR | HV Switchgear | HV Switchgear | Design factors to be provided | 1.24.2 | Protection relay | 1
| AR | HV Switchgear | HV Switchgear | Design factors to be provided | 1.24.2 | Switch disconnector panel | 2
| AR | HV Switchgear | HV Switchgear | Design factors to be provided | 1.24.2 | Operating temperature range | 1
| AR | HV Switchgear | HV Switchgear | Design factors to be provided | 1.24.2 | Warranty and insurance | 1
| AR | HV Switchgear | HV Switchgear | Design factors to be provided | 1.24.2 | Dimensions and weight | 3
| AR | HV Switchgear | HV Switchgear | Design factors to be provided | 1.24.2 | NEMA enclosure type and IP code | 1
| AR | HV Switchgear | HV Switchgear | Standards | 1.24.2 | IEC 60038 | 1 | [6 empty] | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient?
| AR | HV Switchgear | HV Switchgear | Standards | 1.24.2 | IEC 60095 | 1 | [6 empty] | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient?
| AR | HV Switchgear | HV Switchgear | Standards | 1.24.2 | IEC 62271-200 | 1 | [6 empty] | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient?
| AR | HV Switchgear | HV Switchgear | Standards | 1.24.2 | IEC 60364 | 1 | [6 empty] | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient?
| AR | HV Switchgear | HV Switchgear | Standards | 1.24.2 | Factory witness testing will are required for HV switchgear | 1 | [6 empty] | Cannot be evaluated at this stage
| AR | HV Switchgear | HV Switchgear | Standards | 1.24.3 | Type test reports from an independent reputable laboratory shall be submitted | 1
| AR | HV Switchgear | Due Diligence | Quality Assurance | 1.24.3 | The cost of the due diligence to be carried by the Employer through an independent technical consultant will be taken over by the successful bidder up to an amount of 50,000 USD. | 1
| RM | Other infrastructure | Auxiliary systems | Design factors to be provided | 1.25.1 | One administration and office building with car port for 10 vehicles shall be provided, with sufficient space for operating personal, control room, security office, regular office rooms for permanent and visiting staff, meeting room, kitchen sanitary systems (toilet, showers separate for male and female), first aid, control room, electrical rooms, etc. The building shall have windows for office rooms and air conditioning system (split units) for all office rooms. | 1 | [6 empty] | Priority to be discussed
| RM | Other infrastructure | Auxiliary systems | Design factors to be provided | 1.25.1 | Warehouse for spare parts and workshop for minor mechanical/electrical works. | 1
| RM | Other infrastructure | Auxiliary systems | Design factors to be provided | 1.25.1 | Water storage facility for drinking water, sanitary water (sufficient for 1 week) | 1
| RM | Other infrastructure | Auxiliary systems | Design factors to be provided | 1.25.1 | Service water system sufficiently sized for cleaning cycle of modules | 1
| RM | Other infrastructure | Auxiliary systems | Design factors to be provided | 1.25.1 | Sewage system including sewage disposal for Construction and O&M phase | 1
| RM | Other infrastructure | Auxiliary systems | Design factors to be provided | 1.25.1 | Gatehouse and facilities (toilet, Air-conditioning) | 2
| RM | Other infrastructure | Auxiliary systems | Design factors to be provided | 1.25.2 | Cabling for internal remote control and monitoring grid must be fiber optic | 2
| RM | Other infrastructure | Auxiliary systems | Lighting & Small Power system | 1.25.3 | Distribution boards | 2
| RM | Other infrastructure | Auxiliary systems | Lighting & Small Power system | 1.25.3 | Electric lighting fittings | 2
| RM | Other infrastructure | Auxiliary systems | Lighting & Small Power system | 1.25.3 | Switches, sockets outlets and other accessories | 2
| RM | Other infrastructure | Auxiliary systems | Guarantees | 1.25.4 | All buildings should be designed in accordance with the requirements of the Pakistan Building Code (available at www.pec.org.pk/buildingcode.aspx) and latest Seismic Provisions 2007. | 1 | [6 empty] | Link to code
| RM | Other infrastructure | Auxiliary systems | Security Surveillance System | 1.25.5 | Automatic detection devices (wireless) | 2
| RM | Other infrastructure | Auxiliary systems | Security Surveillance System | 1.25.5 | Perimeter Locator System (with e.g. RFID tags) | 2
| RM | Other infrastructure | Auxiliary systems | Security Surveillance System | 1.25.5 | Security control station (prepared for 24/7 staffing), from where all systems can be operated and monitored | 2
| RM | Other infrastructure | Auxiliary systems | Security Surveillance System | 1.25.5 | Centralized Surveillance system, covering all subsystems and analysis tools. Communication via fiber-optical Alarm and action plan and Video from alarm segment | 2
| RM | Other infrastructure | Auxiliary systems | Security Surveillance System | 1.25.5 | Video surveillance to document and verify alarm signals (during day and night time). The video system shall be capable of a continuous and gap-free surveillance (e.g., high speed dome cameras, body heat detection system, algorithmic video analysis) | 2
| RM | Other infrastructure | Auxiliary systems | Security Surveillance System | 1.25.5 | Light installations through Infrared and/or floodlight | 2
| RM | Other infrastructure | Auxiliary systems | Security Surveillance System | 1.25.5 | Immediate alarm of local guards allowing fast response times | 2
| RM | Other infrastructure | Auxiliary systems | Security Surveillance System | 1.25.5 | Display of clear text alarm cause at monitoring station | 2
| RM | Other infrastructure | Auxiliary systems | Security Surveillance System | 1.25.5 | Protection of electric rooms/building against intrusion and fire | 2
| RM | Other infrastructure | Auxiliary systems | Security Surveillance System | 1.25.5 | Full functionality through UPS-system (for at least 24hrs), system function and capacity (e.g., battery) to be monitored by control system | 2
| RM | Other infrastructure | Auxiliary systems | Security Surveillance System | 1.25.5 | Remote access for diagnosis, maintenance and change of settings (via Modem) | 3
| RM | Other infrastructure | Auxiliary systems | Security Surveillance System | 1.25.5 | All stations shall be secured by Access-code with Code-card | 3 | [6 empty] | Cannot be evaluated at this stage
| RM | Other infrastructure | Auxiliary systems | Security Surveillance System | 1.25.5 | The security system provider shall provide all certificates as required | 3 | [6 empty] | Priority to be discussed
| RM | Other infrastructure | Auxiliary systems | Security Surveillance System | 1.25.5 | The system shall comply with insurance requirements | 1
| RM | Other infrastructure | Auxiliary systems | Security Surveillance System | 1.25.5 | The Bidder shall provide security personnel for 24 h / 7 days a week for the whole year | 1
| RM | Other infrastructure | Auxiliary systems | DC Backup System / uninterrupted power supply (UPS) | 1.25.6 | The design and related battery sizing calculations shall be submitted. | 2
| RM | Other infrastructure | Auxiliary systems | DC Backup System / uninterrupted power supply (UPS) | 1.25.6 | Independent UPS systems for control and relaying equipment as well as for operation of all alarms shall be designed for high reliability and supply period of 8 hours | 2
| RM | Other infrastructure | Auxiliary systems | DC Backup System / uninterrupted power supply (UPS) | 1.25.6 | IEC-60051 and IEC-60439 standards apply | 1 | [6 empty] | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient?
| RM | Other infrastructure | Auxiliary systems | DC Backup System / uninterrupted power supply (UPS) | 1.25.6 | Battery chargers for both the DC systems shall be fully automatic | 2
| RM | Other infrastructure | Auxiliary systems | DC Backup System / uninterrupted power supply (UPS) | 1.25.6 | voltage stabilized and solid state type and designed for an input voltage of 400 V, 3-phase, 50 Hz. They shall be without fan or moving parts. | 2
| JBS | Labelling | General items | Labelling | 1.26 | the ID numbering / coding system shall allow unique identification of all components and be understandable | 1 | [6 empty] | Cannot be evaluated at this stage
| JBS | Labelling | General items | Labelling | 1.26 | It shall follow international best practice. | 2 | [6 empty] | Cannot be evaluated at this stage
| JBS | Labelling | General items | Labelling | 1.26 | A manual shall be provided to the Employer for review and comment. | 2 | [6 empty] | Cannot be evaluated at this stage
| JBS | Labelling | General items | Labelling | 1.26 | Tags shall be weather and UV resistant. | 1 | [6 empty] | Cannot be evaluated at this stage
| JBS | Labelling | General items | Labelling | 1.26 | Warning signs shall be placed at outer existing wall, entrance gate and on the exterior of all components according to International Standards | 2 | [6 empty] | Cannot be evaluated at this stage
| JBS | Labelling | General items | Labelling | 1.26 | Labelling shall be provided for the following: Fields, rows, tables, string cables (on both ends at table and stringbox, AC cables, grounding system, components, security system components) | 2 | [6 empty] | Cannot be evaluated at this stage
| JBS | Labelling | General items | Labelling | 1.26 | Numbering system shall already be applied during the offer stage | 2 | [6 empty] | Cannot be evaluated at this stage
| JBS | Labelling | General items | Labelling | 1.26 | The ID’s shall correspond to all drawings, plant documentation and control system. | 1 | [6 empty] | Cannot be evaluated at this stage
| JBS | Power plant documentation | Power plant documentation | Quality Assurance | 1.27.1 | The Bidder shall confirm that the complete as-built documentation of the plant will be provided in compliance with IEC 62446. Additionally all module serial numbers shall be listed with their individual location. | 1 | [6 empty] | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient?
| JBS | Power plant documentation | Power plant documentation | Quality Assurance | 1.27.1 | Flash report list of all modules shall be provided in digital form. | 1
| JBS | Power plant documentation | Spare parts | Warranty | 1.27.2 | The successful bidder shall provide all warranty spares for a warranty period of 5 years. | 1
| JBS | Power plant documentation | Spare parts | Warranty | 1.27.2 | All operational spare parts for 5 years operation shall be listed and approved by the manufacturer and shall be supplied after warranty. These shall not consider those spare parts consumed during warranty period to rectify warranty defects. Spare parts shall cover the complete power plant with all subsystems, e.g., Modules, inverter, Mounting system and tracker, electrical system, security system, control system, measurement equipement | 2
| JBS | Equipment guarantees | Warranty | Guarantees | 1.28 | The overall Guarantee and Power Plant Acceptance Procedures required for the Project are described in Sections 1.3, 1.4, 1.14, 1.18 and Schedule D and shall be met. | 1 | [6 empty] | Link
| JBS | Equipment guarantees | Modules | Guarantees | 1.28.1 | The Successful bidder shall provide a Module warranty of at least 10 years. The performance warranty of the module shall be linear with a fixed factor over 25 years. | 1 | [6 empty] | To be discussed
| JBS | Equipment guarantees | Inverter | Guarantees | 1.28.2 | The Successful Bidder shall provide an Inverter warranty of at least 5 years. A spare parts warranty shall be included for the 25 years operational period. | 1
| JBS | Equipment guarantees | Mounting | Guarantees | 1.28.3 | The Successful Bidder shall provide a product warranty for the structure of at least 10 years. | 1
| JBS | Equipment guarantees | Warranty | Guarantees | 1.28.4, 1.6 | A detailed list of all guarantee conditions for the main equipments (beside modules and inverters) shall be provided by the Successful Bidder with the technical offer. The product warranty shall be at least 5 years. | 1
| JBS | Miscellaneous | Auxiliary systems | Power supply | 1.29.1 | An off-grid power station may need to be provided by the Bidder for commencing the work. Diesel generators shall be arranged by the bidder on its own. | 1
| JBS | Miscellaneous | Project schedule / Project management | Specific Requirements | 1.29.9 | The Bidder shall submit an organizational chart illustrating management and functional relationships among all project team members including consultants, sub-contractors and vendors at each significant stage of the work, such as permitting, design, construction, testing and commissioning and O&M. | 1
[6 empty] | Vital | 354
[6 empty] | Valuable | 187
[6 empty] | Not important | 108

## O&M (hidden)
Bidder | Expert | Chapter in RfP | Subtopic | Clause | Question | 1 Vital 2 Valuable 3 Not Important | Link to Bidders Documents | Pass =1 | Fail =1 | Open =1 | Question to bidder for clarification | Comments
|  | Scope of the Bid | General Requirements | 2.1.2 | Responsibility to keep Performance Ratio and Availability at highest levels | 1
|  | Scope of the Bid | General Requirements | 2.1.2 | Preventive maintenance | 2
|  | Scope of the Bid | General Requirements | 2.1.2 | Provision and Installation of spare parts, keeping of spare parts stock (refill of used spares). Reporting of status and consumption to be continuously updated | 2
|  | Scope of the Bid | General Requirements | 2.1.2 | Corrective maintenance with guaranteed response times | 1
|  | Scope of the Bid | General Requirements | 2.1.2 | Daily, monthly and yearly performance and production reporting | 1
|  | Scope of the Bid | General Requirements | 2.1.2 | Operation of the Plant (including 24/7 presence of O&M and security staff on the project site). | 1
|  | Scope of the Bid | General Requirements | 2.1.2 | Cleaning of the Plant, preventive and corrective maintenance of the civil works and the fences. | 1
|  | Scope of the Bid | General Requirements | 2.1.2 | Cleaning of Modules and irradiation sensors to prevent dust accumulation to undesirable level. | 1
|  | Scope of the Bid | General Requirements | 2.1.2 | Ordinary road and land maintenance to the extent required for proper maintenance of the Plant. | 3
|  | Scope of the Bid | General Requirements | 2.1.2 | Smooth functioning of all interconnections and data communications of the system performance | 2
|  | Scope of the Bid | General Requirements | 2.1.2 | Coordination and compliance with NTDC requirements | 1
|  | Scope of the Bid | General Requirements | 2.1.2 | Maintaining a customer support hotline for the Employer/NTDC | 3
|  | Scope of the Bid | General Requirements | 2.1.2 | Providing regular reports of repairs, maintenance, and tests | 3
|  | Scope of the Bid | General Requirements | 2.1.2 | Performance variance analysis of the module strings and inverters | 1
|  | Scope of the Bid | General Requirements | 2.1.2 | Periodic maintenance of inverter, transformer, combiner boxes etc., according manufacturer's requirements | 1
|  | Scope of the Bid | General Requirements | 2.1.2 | Scheduled maintenance routines: e.g., inspections of modules with polarized sunglasses to check for discolouration, the first signs of de-lamination, loose wires in the electronics, corrosion of mounting structures, erosion | 1
|  | Scope of the Bid | General Requirements | 2.1.2 | Track chronic negative deviations in the module string output, i.e., power tolerances consistently in the negative | 3
|  | Scope of the Bid | General Requirements | 2.1.2 | Negotiating a warranty reserve for replacements with the suppliers | 3
|  | Scope of the Bid | General Requirements | 2.1.2 | Maintaining adequate reserves for timely replacement | 2
|  | Scope of the Bid | General Requirements | 2.1.2 | Insuring products at different levels but for sensible costs; the insurance policy shall not become expensive compared to the replacement cost of the item | 3
|  | Scope of the Bid | General Requirements | 2.1.2 | Warranties and insurance policies should be assignable/transferrable to the Employer in case it decides to take over the O&M | 1
|  | Scope of the Bid | General Requirements | 2.1.2 | Reporting the monitoring and surveillance system. | 3
|  | Scope of the Bid | General Requirements | 2.1.2 | Technical report elaboration. | 3
|  | Scope of the Bid | General Requirements | 2.1.2 | On site Security services. | 3
|  | Scope of the Bid | General Requirements | 2.1.2 | Provide all O&M Staff, trained and certified as far as applicable. For security reasons, a 24 h/ 7 days a week staffing of security and maintenance shall be provided. The staffing concept and selected key employees shall be presented to the Employer for approval. | 1
|  | Initial Inspection | General Requirements | 2.2.1 | familiarize himself with the specific plant equipment and specific maintenance requirements / training of staff | 1
|  | Initial Inspection | General Requirements | 2.2.2 | Maintenance routines, inspection check-lists, working files, | 1
|  | Initial Inspection | General Requirements | 2.2.3 | coordinate with the Employer and keep him updated regarding his progress of preparation, status of construction, pending issues of Construction, Commissioning and testing. | 2 | [5 empty] | Cannot be evaluated at this stage
|  | Bi-annual inspection | PV Generator | 2.3.1 | 100% visual inspection of modules regarding damage in spring | 1
|  | Bi-annual inspection | PV Generator | 2.3.1 | Random visual inspection of modules regarding damage in autumn | 2 | [5 empty] | Cannot be evaluated at this stage
|  | Bi-annual inspection | PV Generator | 2.3.1 | Random check of module clip with respect to loosening; if necessary replacement of clips (min. 10%, documentation of location, during 5 years inspection of whole PV plant) | 2 | [5 empty] | Cannot be evaluated at this stage
|  | Bi-annual inspection | PV Generator | 2.3.1 | Random testing of the steadiness of the mounting foundation/system and random inspection regarding corrosion at substructure (min. 10%, documentation of location, during 10 years inspection of whole PV plant) | 1
|  | Bi-annual inspection | PV Generator | 2.3.1 | Documentation of wear and tear of moving components, monitoring of dust intrusion and corrosion. | 2
|  | Bi-annual inspection | PV Generator | 2.3.1 | Cleaning of sensors and switches | 1 | [5 empty] | sensors shall be done by independent Meteo Station Operator
|  | Bi-annual inspection | PV Generator | 2.3.1 | Cleaning of all modules | 1
|  | Bi-annual inspection | Inverter (100%) | 2.3.2 | Functional check of ventilator system of inverter station | 1
|  | Bi-annual inspection | Inverter (100%) | 2.3.2 | Cleaning of the filter mats in the air leaks | 2
|  | Bi-annual inspection | Inverter (100%) | 2.3.2 | Replacement of dirty filter mats | 2
|  | Bi-annual inspection | Inverter (100%) | 2.3.2 | Inspection of the interior of the electrical cabinet regarding dust deposit, dirtiness, humidity, water penetration from outside. If necessary the cabinet has to be cleaned. | 1
|  | Bi-annual inspection | Inverter (100%) | 2.3.2 | Testing of inverter features according to maintenance schedule of manufacturer. | 1
|  | Bi-annual inspection | Inverter (100%) | 2.3.2 | Maintenance of inverters according to manufacturer's instruction. | 1
|  | Bi-annual inspection | Monitoring | 2.3.3 | Functionality testing of the monitoring system | 3
|  | Bi-annual inspection | Maintenance | 2.3.3 | Maintenance of all Power plant components according to manufacturer's instructions | 1
|  | Main Annual Inspection | PV Generator | 2.4.1 | Visual inspection of all accessible cable trenches and cable trays regarding damage | 1
|  | Main Annual Inspection | PV Generator | 2.4.1 | Visual inspection and random testing of string connector (min. 10% with Documentation of location , during 10 years testing of whole PV plant) | 1
|  | Main Annual Inspection | PV Generator | 2.4.1 | Inspection of DC distribution box: Visual inspection of all clamps and degree of pollution. Testing of over-voltage protection | 1
|  | Main Annual Inspection | PV Generator | 2.4.1 | Maintenance of sensors based on manufacturer’s instructions | 1
|  | Main Annual Inspection | Inverter (100%) | 2.4.2 | Test of the internal miniature circuit breakers and power switch, test of emergency shut-off | 1
|  | Main Annual Inspection | Inverter (100%) | 2.4.2 | Visual inspection of all fuses | 1
|  | Main Annual Inspection | Inverter (100%) | 2.4.2 | Inspection of over-voltage protection and upstream fuses regarding external damage | 1
|  | Main Annual Inspection | Inverter (100%) | 2.4.2 | Functional check of internal and external over- and under-voltage monitoring through operation of test terminal | 1
|  | Main Annual Inspection | Inverter (100%) | 2.4.2 | Functional check of insulation monitoring | 1
|  | Main Annual Inspection | Inverter (100%) | 2.4.2 | Check of control and auxiliary voltages | 2
|  | Main Annual Inspection | Inverter (100%) | 2.4.2 | Check of the safety circuit for the interruption of the AC-grid protection in the case of failure (emergency shut-off, over-/ under-voltage, over temperature, etc.) based on the local conditions | 1
|  | Main Annual Inspection | Inverter (100%) | 2.4.2 | Visual inspection of AC and DC clamps regarding tightness and colouring, tightening of clamps | 1
|  | Main Annual Inspection | Inverter (100%) | 2.4.2 | Maintenance of inverters according to manufacturer instruction | 1
|  | Main Annual Inspection | Roads | 2.4.3 | Visual inspection of roads within the PV plant shall be carried out to ascertain that these are maintained in good condition for the intended purpose. | 2
|  | Main Annual Inspection | Substation and Transmission Line | 2.4.4 | Visual inspection of transformer and switchboard rooms and cleaning if necessary | 1
|  | Main Annual Inspection | Substation and Transmission Line | 2.4.4 | Visual inspection of Transmission Line and report of damage to the grid operator | 2
|  | Main Annual Inspection | Substation and Transmission Line | 2.4.4 | Maintenance of substation and transmission line according to manufacturer instruction | 1
|  | Main Annual Inspection | Auxiliary system | 2.4.5 | Inspection of security system inclusive fence, all gates, all cameras etc. Random test of the fence fastening, if necessary retightening of the screws | 2
|  | Main Annual Inspection | Auxiliary system | 2.4.5 | If existing: inspection of requirements out of the building permit | 2
|  | Main Annual Inspection | Auxiliary system | 2.4.5 | Maintenance of all components according to manufacturer instruction | 1
|  | Special inspection (every 4 years) | Specific Requirements | 2.5.1 | Measurement of inverters and generators according to recognized international standards and according to results from commissioning certificates (insulation, loop resistance, earthing, DC-open circuit voltage) | 2
|  | Special inspection (every 4 years) | Specific Requirements | 2.5.1 | Protection systems of medium voltage switching panels of the stations | 1
|  | Special inspection (every 4 years) | Specific Requirements | 2.5.1 | Oil check of transformers | 1
|  | Special inspection (every 4 years) | Specific Requirements | 2.5.1 | Control of station equipment | 2
|  | Deactivation | Allowed deactivation periods | 2.6.1 | Times with irradiation level < 300 W/m² | 2
|  | Deactivation | Allowed deactivation periods | 2.6.1 | Approved by The Employer to ensure consideration of Employer's obligations | 2
|  | Deactivation | Allowed deactivation periods | 2.6.1 | Approved from grid operator | 2
|  | Deactivation | Specific Requirements | 2.6.2 | All deactivations during maintenance works shall be completely documented. | 2
|  | Deactivation | Specific Requirements | 2.6.3 | Deactivation shall not be considered as permitted downtime. | 2
|  | Performance of maintenance and repair works | Specific Requirements | 2.8.1 | Corresponding regulations of the respective component manufacturer shall have to be followed during maintenance works | 1
|  | Performance of maintenance and repair works | Specific Requirements | 2.8.2 | Report document for maintenance works (blanc sample requiered for bid) | 1
|  | Performance of maintenance and repair works | Specific Requirements | 2.8.3 | Observe and respect the maintenance and operation specifications of the manufacturer of the components | 3
|  | Performance of maintenance and repair works | Specific Requirements | 2.8.4 | Observe and respect the local law, regulations and international PV standards. | 3
|  | Performance of maintenance and repair works | Specific Requirements | 2.8.5 | During his work the Bidder shall be held responsible for the public safety of the PV plant | 2
|  | On-site monitoring | Specific Requirements | 2.9.1 | Permanent (24/7) staffing of the Power Plant, consisting of security and O&M personnel. | 1
|  | On-site monitoring | Specific Requirements | 2.9.2 | Bidder shall arrange service contracts with specialized sub-contractors | 2
|  | On-site monitoring | Specific Requirements | 2.9.3 | All operational data shall be logged on-site in parallel to the remote data storage | 2
|  | On-site monitoring | Specific Requirements | 2.9.4 | The data of irradiation sensors shall be monitored by an independent expert on a continuous basis | 2
|  | Remote Supervision | Specific Requirements | 2.10.1 | On-call service provided for the Employer for availability outside business hours and during weekends (24/7). | 1
|  | Remote Supervision | Specific Requirements | 2.10.2 | Any reductions in performance shall have to be logged. | 1
|  | Remote Supervision | Specific Requirements | 2.10.3 | The data will comprise, apart from electrical parameters of the PV plant: currents, voltages, irradiation values, kind and period of reductions in performance such as curtailment by the grid operator | 2
|  | Remote Supervision | Specific Requirements | 2.10.4 | The data shall present the status of the plant such as the performance ratio annual overview and the current feed-in power | 2
|  | Remote Supervision | Specific Requirements | 2.10.5 | The remote supervision shall also control the operation of the PV plant. | 2
|  | Remote Supervision | Specific Requirements | 2.10.6 | The remote supervision shall also include the taking of measures for removal of faults. | 2
|  | Remote Supervision | Specific Requirements | 2.10.7 | The Bidder shall provide to the Employer permanent online access to the power plant control system for parallel monitoring | 1
|  | Remote Supervision | Specific Requirements | 2.10.8 | Monthly / quarterly and annual reports based on the data of the remote supervision provided to the Employer 4 weeks after the last period of reporting at the latest. | 1
|  | Remote Supervision | Specific Requirements | 2.10.9 | The fees for telephone connection and/or data transfer services are included in the annual remuneration. | 2
|  | Reaction to Fault Messages / Response Times | Specific Requirements | 2.11.1 | Every fault message has to be registered in the monitoring software. According to the fault message, the Bidder shall issue a fault diagnosis within a response time of 2 hours (24/7) | 1
|  | Reaction to Fault Messages / Response Times | Specific Requirements | 2.11.2 | profit relevant Fault Events: Downtime registration/ reasons/ repair/ in monthly report (blanc of monthly report?) | 1
|  | Fault Management / Warranty defects | Specific Requirements | 2.12.1 | Fault Management: all handling and communication | 2
|  | Fault Management / Warranty defects | Specific Requirements | 2.12.2 | Fault Management: Handling / correspondence with third parties | 2
|  | Fault Management / Warranty defects | Specific Requirements | 2.12.3 | Fault Management = without repair works | 3
|  | Fault Management / Warranty defects | Specific Requirements | 2.12.4 | Product warranties in favour of contractor / Bidder (responsible) to claim all warranties for at least 5 years | 1
|  | Fault Management / Warranty defects | Specific Requirements | 2.12.5 | Operational defects, which are not considered as warranty defects - see repair works section below | 3
|  | Fault Management / Warranty defects | Specific Requirements | 2.12.6 | All defects shall be documented within the same day of detection, | 2
|  | Fault Calls | Specific Requirements | 2.13.1 | The scope of service shall include any working times for all fault calls including travelling times and costs. | 1
|  | Fault Calls | Specific Requirements | 2.13.2 | The minimum response time in case of failure must meet the EPA requirements | 1
|  | Fault Calls | Specific Requirements | 2.13.2 | --> Time Model: Response Times for Priorities 1-3 (12h / 24h / 1 week) | 1
|  | Fault Calls | Specific Requirements | 2.13.3 | failure time response does not match the response time of EPA >> failure time response does not match the response time of EPA | 3
|  | Fault Calls | Specific Requirements | 2.13.4 | The fault call shall include the fault diagnosis on site as well as an immediate error correction if possible. The fault shall have to be corrected within the response time and, failing this, a diagnosis of the fault has to be effect indicating further measures. | 2
|  | Fault Calls | Specific Requirements | 2.13.5 | Fault calls can be performed without prior consent of the Employer. | 3
|  | Fault Calls | Specific Requirements | 2.13.6 | If the elimination of faults is not possible within the response time / and additional travelling, this is Repair Work | 3
|  | Spare Parts and Tools | Specific Requirements | 2.14 | provide the necessary set of spare parts and maintenance tools as required to perform the services | 1
|  | Spare Parts and Tools | Specific Requirements | 2.14.1 | cover all cost for supply and re-stocking of spare parts from his annual remuneration. | 1
|  | Spare Parts and Tools | Specific Requirements | 2.14.2 | refill spare parts immediately after consumption | 2
|  | Reduced Output of the Plant | Specific Requirements | 2.15 | Monthly comparison of the specific performance of all measuring channels among each other. 5% reduced output results in general check of all the channels and shall be documented. | 1
|  | Reduced Output of the Plant | Specific Requirements | 2.15.1 | Identified reduced output shall be justified. Reduced output shall be recovered and liquidated damages determined. | 1
|  | Repair time and cost | Specific Requirements | 2.16 | Repair times are considered as part of the availability guaranty of the Bidder. All cost of repair shall be part of the Bidders annual remuneration. For the avoidance of doubt that includes any repairs due to lightening, theft and vandalism. | 1
|  | Working Time | Specific Requirements | 2.17 | All working times of Bidders personnel shall be included in the Bidders annual remuneration. | 1
|  | Approval | Specific Requirements | 2.18 | Extensive repairs have to be approved by the Employer. | 2
|  | Documentation | Specific Requirements | 2.19 | All repair works and compensations shall have to be documented and to be submitted to the Employer within two weeks. | 2
|  | Inspection of Repair Works | Specific Requirements | 2.20 | The Employer can inspect the repair works within one month (30 days) after receiving the documentation | 2
|  | Ground Maintenance | Specific Requirements | 2.21 | Ground maintenance shall include all procedures that are necessary to avoid module shading and an incorrect operation of the trackers. This shall include the levelling of sand drifts. Necessary switching operations shall be coordinated by the Bidder with responsible authorities | 2
|  | Person in Control of PV plant | Specific Requirements | 2.22 | The Bidder shall propose an organigram for the O& M personnel with one main responsible | 2
|  | Reporting | Specific Requirements | 2.23 | The Bidder shall deliver to the Employer regular reports on monthly, quarterly and annual basis. | 1

## Documents (hidden)
Schedule B
Appendix 8 (for WR) | Schedule D - Warranty
NTDC grid connection code
Appendix 1 HV Station
Energy Purchase Agreements (EPA) - Question 1.1.5
Schedule C

## AR (hidden)
Bidder | Expert | Chapter in RfP | Topic | Subtopic | Clause | Criteria | 1 Vital 2 Valuable 3 Not Important | Link to Bidders Documents | Pass =1 | Fail =1 | Open =1 | Question to bidder for clarification | Comments | Comments QA on Criteria | Comment on "Comments" | Typical Questions to be send to bidders if Open status | Standard Text | Check | Prio | Result
Juwi | AR | HV Substation | HV Substation | Specific Requirements | 1.23.1 | The HV Substation includes the respective MV switch gears, Transformer MV/ HV. The HV connection is designed to connect to the HV line. | 3 |  | 1 | [8 empty] | 1 |  | Pass
Juwi | AR | HV Substation | HV Substation | Specific Requirements | 1.23.2 | Availability and delivery time of the chosen components is detailed | 1 |  |  |  | 1 | [5 empty] | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | 1 |  | Open
Juwi | AR | HV Substation | HV Substation -HV part | Specific Requirements | 1.23.3 | The substation is separated into 2 parts: Medium Voltage part including HV transformer and HV portion of the plant excluding the HV transformer | 1 |  |  |  | 1 | Layout to be submitted | [5 empty] | 1 |  | Open
Juwi | AR | HV Substation | HV Substation -HV part | Specific Requirements | 1.23.3 | Double Busbar single breaker scheme shall be designed for HV portion of HV substation | 1 |  | 1 | [8 empty] | 1 |  | Pass
Juwi | AR | HV Substation | HV Substation -HV part | HV portion components | 1.23.3 | 132 kV Transformer Bays as per design | 1 |  | 1 | [8 empty] | 1 |  | Pass
Juwi | AR | HV Substation | HV Substation -HV part | HV portion components | 1.23.3 | 2x132 kV Line Bays | 1 |  | 1 | [8 empty] | 1 |  | Pass
Juwi | AR | HV Substation | HV Substation -HV part | HV portion components | 1.23.3 | 2x132 kV PT bays | 1 |  |  |  | 1 | to be confirmed not shown in SLD, but in BOM | [5 empty] | 1 |  | Open
Juwi | AR | HV Substation | HV Substation -HV part | HV portion components | 1.23.3 | 132 kV Bus Coupler Bay | 1 |  | 1 | [8 empty] | 1 |  | Pass
Juwi | AR | HV Substation | HV Substation -HV part | HV portion components | 1.23.3 | Telecom and PLC Equipment | 1 |  |  |  | 1 | details are required |  | Which speification are acepted |  |  |  | 1 |  | Open
Juwi | AR | HV Substation | HV Substation -HV part | Standards | 1.23.3 | All the schemes including SCADA, PLC, protection scheme, control and monitoring scheme and other design factors, shall be in compliance with the NTDC grid code. | 1 |  |  |  | 1 | details are required |  | Link to NTDC grid code |  |  |  | 1 |  | Open
Juwi | AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | 3-phase, double wound, continuously rated, oil-cooled, enclosed transformers, use of low loss core steel and close coupled copper windings | 1 |  | 1 |  |  | No Specification or Tech data | No Specification or Tech data |  |  |  |  | 1 |  | Pass
Juwi | AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | Enclosure specifications (e.g., steel floor, fluid tight, sealed tank) | 1 |  |  |  | 1 | [5 empty] | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | 1 |  | Open
Juwi | AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | Incoming terminals | 1 |  |  |  | 1 | [5 empty] | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | 1 |  | Open
Juwi | AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | Outgoing terminals | 1 |  |  |  | 1 | [5 empty] | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | 1 |  | Open
Juwi | AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | kVA rating | 1 |  | 1 | [8 empty] | 1 |  | Pass
Juwi | AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | Primary side voltage | 1 |  | 1 | [8 empty] | 1 |  | Pass
Juwi | AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | Secondary side voltage | 1 |  | 1 | [8 empty] | 1 |  | Pass
Juwi | AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | Vector group | 3 |  | 1 |  |  |  |  | to be discussed |  |  |  | 1 |  | Pass
Juwi | AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | Insulation type | 1 |  |  |  | 1 | [5 empty] | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | 1 |  | Open
Juwi | AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | Frequency rating | 1 |  | 1 | [8 empty] | 1 |  | Pass
Juwi | AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | Short-circuit impedance | 1 |  |  |  | 1 | [5 empty] | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | 1 |  | Open
Juwi | AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | Own consumption | 3 |  |  |  | 1 | [5 empty] | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | 1 |  | Open
Juwi | AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | No-load losses | 1 |  |  |  | 1 | [5 empty] | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | 1 |  | Open
Juwi | AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | Efficiency | 1 |  |  |  | 1 | [5 empty] | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | 1 |  | Open
Juwi | AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | Operating temperature range | 1 |  |  |  | 1 | [5 empty] | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | 1 |  | Open
Juwi | AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | Maximum ambient temperature and altitude | 1 |  |  |  | 1 |  |  | to be discussed |  |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | 1 |  | Open
Juwi | AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | Humidity tolerance | 2 |  |  |  | 1 | [5 empty] | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | 1 |  | Open
Juwi | AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | Cooling method | 1 |  |  |  | 1 | [5 empty] | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | 1 |  | Open
Juwi | AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | Dimensions and weight | 3 |  |  |  | 1 | [5 empty] | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | 1 |  | Open
Juwi | AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | Oil weight | 3 | [10 empty] | 0 |  | Open
Juwi | AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | Protection system | 1 |  | 1 |  |  | need to submitt detail and layout | [5 empty] | 1 |  | Pass
Juwi | AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | Auxiliary service lines | 1 |  | 1 | [8 empty] | 1 |  | Pass
Juwi | AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | Fittings with the transformer | 3 |  |  |  | 1 | [5 empty] | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | 1 |  | Open
Juwi | AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | Noise levels | 3 |  |  |  | 1 | [5 empty] | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | 1 |  | Open
Juwi | AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | Warranty and insurance | 1 |  |  |  | 1 | [5 empty] | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | 1 |  | Open
Juwi | AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | Tests and inspection routines | 1 |  |  |  | 1 | [5 empty] | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | 1 |  | Open
Juwi | AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | Operational data shall be logged in central operating system (e.g. oil temperature, oil level, pressure, temperature probes (one per phase): Alarm and trip of cell etc.) | 2 |  |  |  | 1 | need confirmatation | [5 empty] | 1 |  | Open
Juwi | AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | All documentation, certificates and test protocols shall be provided | 2 |  |  |  | 1 | need to submitt | [5 empty] | 1 |  | Open
Juwi | AR | HV Substation | HV Substation -MV/HV Transformer | Standards | 1.23.7 | IEC 62446 | 1 |  |  |  | 1 | need to confirm |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  |  |  | 1 |  | Open
Juwi | AR | HV Substation | HV Substation -MV/HV Transformer | Standards | 1.23.7 | IEC 60076 | 1 |  |  |  | 1 | need to confirm |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  |  |  | 1 |  | Open
Juwi | AR | HV Substation | HV Substation -MV/HV Transformer | Standards | 1.23.7 | IEC 60085 | 1 |  |  |  | 1 | need to cofirm |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  |  |  | 1 |  | Open
Juwi | AR | HV Substation | HV Substation -MV/HV Transformer | Standards | 1.23.7 | IEC 60214 | 1 |  |  |  | 1 | nee to confirm |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  |  |  | 1 |  | Open
Juwi | AR | HV Substation | HV Substation -MV/HV Transformer | Standards | 1.23.7 | IEC 60137 | 1 |  |  |  | 1 | need to confirm |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  |  |  | 1 |  | Open
Juwi | AR | HV Substation | HV Substation -MV/HV Transformer | Standards | 1.23.7 | ASTM d-3487 | 1 |  |  |  | 1 | need to confirm |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  |  |  | 1 |  | Open
Juwi | AR | HV Substation | HV Substation -MV/HV Transformer | Quality Assurance | 1.23.7 | Factory witness testing shall be required for MV/HV transformer and switchgear to be installed at this project. | 1 |  |  |  | 1 | need to confirm |  | Cannot be evaluated at this stage |  |  |  | 1 |  | Open
Juwi | AR | HV Substation | HV Substation -MV/HV Transformer | Quality Assurance | 1.23.7 | Type test reports from an independent reputable laboratory shall be submitted with the bid. | 1 |  |  |  | 1 | need to submitt | [5 empty] | 1 |  | Open
Juwi | AR | HV Substation | Due Diligence | Quality Assurance | 1.23.7 | The cost of the due diligence for the HV station to be carried by the Employer through an independent technical consultant will be taken over by the successful bidder up to an amount of 30,000 USD. | 1 |  |  |  | 1 | [5 empty] | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | 1 |  | Open
Juwi | AR | HV Substation | HV Substation -MV/HV Transformer | Design | 1.23.8 | The separating equipment shall be installed with visible disconnection (pivotable disconnectors). | 1 |  |  |  | 1 | need to confirm |  | Cannot be evaluated at this stage |  |  |  | 1 |  | Open
Juwi | AR | HV Substation | HV Substation -MV/HV Transformer | Design | 1.23.9 | Insulation with PCB (polychlorinated biphenyl) has not been used. | 1 |  |  |  | 1 | need to confirm | [5 empty] | 1 |  | Open
Juwi | AR | HV Substation | HV Substation -MV/HV Transformer | Design | 1.23.10 | The preliminary design of the substation is submitted with the technical bid according to the requirements of Appendix 1 | 1 |  |  |  | 1 | not complete , no layout , no techincadate , no supplier name for HV equipments |  | Link to Appendix 1 |  |  |  | 1 |  | Open
Juwi | AR | HV Substation | HV Substation -MV/HV Transformer | Energy Metering System | 1.23.11 | The Energy Metering System will be placed on the HV side of the substation | 1 |  |  |  | 1 | need confirmation | [5 empty] | 1 |  | Open
Juwi | AR | HV Substation | HV Substation -MV/HV Transformer | Energy Metering System -NTDC specifications | 1.23.11 | Metering Equipment for Electric Energy Transfer between the Companies (Specification No. P-199-08) | 1 |  |  |  | 1 | need confirmation | [5 empty] | 1 |  | Open
Juwi | AR | HV Substation | HV Substation -MV/HV Transformer | Energy Metering System -NTDC specifications | 1.23.11 | Energy Meters for Grid Metering (Specification No. P-202-2012) | 1 |  |  |  | 1 | need confirmation | [5 empty] | 1 |  | Open
Juwi | AR | HV Substation | HV Substation -MV/HV Transformer | Energy Metering System -NTDC specifications | 1.23.11 | Voltage Transformers for Special Application (Energy Metering; Specifications No. P-206-05) | 1 |  |  |  | 1 | not shown in SLD , but mentioned in BOM need clear confirmation | [5 empty] | 1 |  | Open
Juwi | AR | HV Substation | HV Substation -MV/HV Transformer | Energy Metering System -NTDC specifications | 1.23.11 | Current Transformers for Special Application (spec.No P-205-2005) | 1 | 1 |  |  |  | subject for CT adequacy calculation | [5 empty] | 0 |  | Open
Juwi | AR | HV Switchgear | HV Switchgear | Project Schedule | 1.24.1 | The switchgear design and order time, for the 132 kV transmission line is detailed and corresponds with the envisaged project schedule. | 1 |  |  |  | 1 | no detail | [5 empty] | 1 |  | Open
Juwi | AR | HV Switchgear | HV Switchgear | Functionalities | 1.24.1 | Nominal system voltage, kV 132 | 1 |  | 1 | [8 empty] | 1 |  | Pass
Juwi | AR | HV Switchgear | HV Switchgear | Functionalities | 1.24.1 | Rated voltage of switch gear, kV 145 | 1 |  | 1 | [8 empty] | 1 |  | Pass
Juwi | AR | HV Switchgear | HV Switchgear | Functionalities | 1.24.1 | Maximum system voltage, kV 145 | 1 |  | 1 | [8 empty] | 1 |  | Pass
Juwi | AR | HV Switchgear | HV Switchgear | Functionalities | 1.24.1 | Rated frequency, Hz 50 | 1 |  | 1 | [8 empty] | 1 |  | Pass
Juwi | AR | HV Switchgear | HV Switchgear | Design factors to be provided | 1.24.2 | Rated voltage | 1 |  | 1 | [8 empty] | 1 |  | Pass
Juwi | AR | HV Switchgear | HV Switchgear | Design factors to be provided | 1.24.2 | Short-duration power withstand frequency voltage | 3 |  |  |  | 1 | Techincal data sheet is missing | [5 empty] | 1 |  | Open
Juwi | AR | HV Switchgear | HV Switchgear | Design factors to be provided | 1.24.2 | Rated lightning impulse withstand voltage | 3 |  |  |  | 1 | Techincal data sheet is missing | [5 empty] | 1 |  | Open
Juwi | AR | HV Switchgear | HV Switchgear | Design factors to be provided | 1.24.2 | Rated frequency | 3 |  | 1 | [8 empty] | 1 |  | Pass
Juwi | AR | HV Switchgear | HV Switchgear | Design factors to be provided | 1.24.2 | Peak-withstand current | 2 |  |  |  | 1 | Technical data sheet is missing | [5 empty] | 1 |  | Open
Juwi | AR | HV Switchgear | HV Switchgear | Design factors to be provided | 1.24.2 | Short-circuit making current | 2 |  |  |  | 1 | Technical data sheet is missing | [5 empty] | 1 |  | Open
Juwi | AR | HV Switchgear | HV Switchgear | Design factors to be provided | 1.24.2 | Short-time withstand current | 2 |  |  |  | 1 | Technical data sheet is missing | [5 empty] | 1 |  | Open
Juwi | AR | HV Switchgear | HV Switchgear | Design factors to be provided | 1.24.2 | Short-circuit breaking current | 2 |  |  |  | 1 | Technical data sheet is missing | [5 empty] | 1 |  | Open
Juwi | AR | HV Switchgear | HV Switchgear | Design factors to be provided | 1.24.2 | Insulating medium | 2 |  |  |  | 1 | Technical data sheet is missing | [5 empty] | 1 |  | Open
Juwi | AR | HV Switchgear | HV Switchgear | Design factors to be provided | 1.24.2 | Second fault rating | 2 |  | 1 | [8 empty] | 1 |  | Pass
Juwi | AR | HV Switchgear | HV Switchgear | Design factors to be provided | 1.24.2 | Busbars | 3 |  | 1 |  |  | calculation is required | [5 empty] | 1 |  | Pass
Juwi | AR | HV Switchgear | HV Switchgear | Design factors to be provided | 1.24.2 | Rated normal current for busbars | 3 |  | 1 | [8 empty] | 1 |  | Pass
Juwi | AR | HV Switchgear | HV Switchgear | Design factors to be provided | 1.24.2 | Rated normal current for feeders | 3 |  | 1 | [8 empty] | 1 |  | Pass
Juwi | AR | HV Switchgear | HV Switchgear | Design factors to be provided | 1.24.2 | Degree of protection | 2 |  |  |  | 1 | to be confirmed | [5 empty] | 1 |  | Open
Juwi | AR | HV Switchgear | HV Switchgear | Design factors to be provided | 1.24.2 | Second internal arc rating | 3 |  |  |  | 1 | to be confirmed | [5 empty] | 1 |  | Open
Juwi | AR | HV Switchgear | HV Switchgear | Design factors to be provided | 1.24.2 | Circuit breakers: protection and metering | 1 |  |  |  | 1 | to be confirmed | [5 empty] | 1 |  | Open
Juwi | AR | HV Switchgear | HV Switchgear | Design factors to be provided | 1.24.2 | Protection relay | 1 |  |  |  | 1 | to be confirmed | [5 empty] | 1 |  | Open
Juwi | AR | HV Switchgear | HV Switchgear | Design factors to be provided | 1.24.2 | Switch disconnector panel | 2 |  |  |  | 1 | to be confirmed | [5 empty] | 1 |  | Open
Juwi | AR | HV Switchgear | HV Switchgear | Design factors to be provided | 1.24.2 | Operating temperature range | 1 |  |  |  | 1 | to be confirmed | [5 empty] | 1 |  | Open
Juwi | AR | HV Switchgear | HV Switchgear | Design factors to be provided | 1.24.2 | Warranty and insurance | 1 |  |  |  | 1 | to be confirmed | [5 empty] | 1 |  | Open
Juwi | AR | HV Switchgear | HV Switchgear | Design factors to be provided | 1.24.2 | Dimensions and weight | 3 |  |  |  | 1 | to be submitted | [5 empty] | 1 |  | Open
Juwi | AR | HV Switchgear | HV Switchgear | Design factors to be provided | 1.24.2 | NEMA enclosure type and IP code | 1 |  |  |  | 1 | to be submitted | [5 empty] | 1 |  | Open
Juwi | AR | HV Switchgear | HV Switchgear | Standards | 1.24.2 | IEC 60038 | 1 |  |  |  | 1 | to be submitted |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  |  |  | 1 |  | Open
Juwi | AR | HV Switchgear | HV Switchgear | Standards | 1.24.2 | IEC 60095 | 1 |  |  |  | 1 | to be submitted |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  |  |  | 1 |  | Open
Juwi | AR | HV Switchgear | HV Switchgear | Standards | 1.24.2 | IEC 62271-200 | 1 |  |  |  | 1 | to be submitted |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  |  |  | 1 |  | Open
Juwi | AR | HV Switchgear | HV Switchgear | Standards | 1.24.2 | IEC 60364 | 1 |  |  |  | 1 | to be submitted |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  |  |  | 1 |  | Open
Juwi | AR | HV Switchgear | HV Switchgear | Standards | 1.24.2 | Factory witness testing will are required for HV switchgear | 1 |  |  |  | 1 | to be submitted |  | Cannot be evaluated at this stage |  |  |  | 1 |  | Open
Juwi | AR | HV Switchgear | HV Switchgear | Standards | 1.24.3 | Type test reports from an independent reputable laboratory shall be submitted | 1 |  |  |  | 1 | to be submitted | [5 empty] | 1 |  | Open
Juwi | AR | HV Switchgear | Due Diligence | Quality Assurance | 1.24.3 | The cost of the due diligence to be carried by the Employer through an independent technical consultant will be taken over by the successful bidder up to an amount of 50,000 USD. | 1 |  |  |  | 1 | to be confirmed | [5 empty] | 1 |  | Open
Sumec | AR | HV Substation | HV Substation | Specific Requirements | 1.23.1 | The HV Substation includes the respective MV switch gears, Transformer MV/ HV. The HV connection is designed to connect to the HV line. | 3 |  | 1 |  |  |  | detail layout |  |  |  |  | 1 |  | Pass
Sumec | AR | HV Substation | HV Substation | Specific Requirements | 1.23.2 | Availability and delivery time of the chosen components is detailed | 1 |  |  |  | 1 |  | not submitted |  |  |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | 1 |  | Open
Sumec | AR | HV Substation | HV Substation -HV part | Specific Requirements | 1.23.3 | The substation is separated into 2 parts: Medium Voltage part including HV transformer and HV portion of the plant excluding the HV transformer | 1 |  | 1 | [8 empty] | 1 |  | Pass
Sumec | AR | HV Substation | HV Substation -HV part | Specific Requirements | 1.23.3 | Double Busbar single breaker scheme shall be designed for HV portion of HV substation | 1 |  | 1 | [8 empty] | 1 |  | Pass
Sumec | AR | HV Substation | HV Substation -HV part | HV portion components | 1.23.3 | 132 kV Transformer Bays as per design | 1 |  | 1 |  |  |  | one Transformer only 100 MVA |  |  |  |  | 1 |  | Pass
Sumec | AR | HV Substation | HV Substation -HV part | HV portion components | 1.23.3 | 2x132 kV Line Bays | 1 |  | 1 |  |  |  | detail SLD |  |  |  |  | 1 |  | Pass
Sumec | AR | HV Substation | HV Substation -HV part | HV portion components | 1.23.3 | 2x132 kV PT bays | 1 |  | 1 |  |  |  | detail SLD |  |  |  |  | 1 |  | Pass
Sumec | AR | HV Substation | HV Substation -HV part | HV portion components | 1.23.3 | 132 kV Bus Coupler Bay | 1 |  | 1 |  |  |  | detail SLD |  |  |  |  | 1 |  | Pass
Sumec | AR | HV Substation | HV Substation -HV part | HV portion components | 1.23.3 | Telecom and PLC Equipment | 1 |  |  |  | 1 |  | detail required | Which speification are acepted |  |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | 1 |  | Open
Sumec | AR | HV Substation | HV Substation -HV part | Standards | 1.23.3 | All the schemes including SCADA, PLC, protection scheme, control and monitoring scheme and other design factors, shall be in compliance with the NTDC grid code. | 1 |  |  |  | 1 |  | detail is requied | Link to NTDC grid code |  |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | 1 |  | Open
Sumec | AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | 3-phase, double wound, continuously rated, oil-cooled, enclosed transformers, use of low loss core steel and close coupled copper windings | 1 |  | 1 |  |  |  | one Transformer only 100 MVA |  |  |  |  | 1 |  | Pass
Sumec | AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | Enclosure specifications (e.g., steel floor, fluid tight, sealed tank) | 1 |  | 1 |  |  | detail drawing | [5 empty] | 1 |  | Pass
Sumec | AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | Incoming terminals | 1 |  | 1 |  |  | detail drawing | [5 empty] | 1 |  | Pass
Sumec | AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | Outgoing terminals | 1 |  | 1 |  |  | detail drawing | [5 empty] | 1 |  | Pass
Sumec | AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | kVA rating | 1 |  | 1 | [8 empty] | 1 |  | Pass
Sumec | AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | Primary side voltage | 1 |  | 1 | [8 empty] | 1 |  | Pass
Sumec | AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | Secondary side voltage | 1 |  | 1 | [8 empty] | 1 |  | Pass
Sumec | AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | Vector group | 3 |  | 1 |  |  |  |  | to be discussed |  |  |  | 1 |  | Pass
Sumec | AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | Insulation type | 1 |  | 1 | [8 empty] | 1 |  | Pass
Sumec | AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | Frequency rating | 1 |  | 1 | [8 empty] | 1 |  | Pass
Sumec | AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | Short-circuit impedance | 1 |  | 1 |  |  |  | need verification |  |  |  |  | 1 |  | Pass
Sumec | AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | Own consumption | 3 |  | 1 |  |  |  | need verification |  |  |  |  | 1 |  | Pass
Sumec | AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | No-load losses | 1 |  |  |  | 1 |  | to submitt |  |  |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | 1 |  | Open
Sumec | AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | Efficiency | 1 |  |  |  | 1 |  | to submitt |  |  |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | 1 |  | Open
Sumec | AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | Operating temperature range | 1 | [5 empty] | to submitt |  |  |  |  | 0 |  | Open
Sumec | AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | Maximum ambient temperature and altitude | 1 |  |  |  | 1 |  | to submitt | to be discussed |  |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | 1 |  | Open
Sumec | AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | Humidity tolerance | 2 |  |  |  | 1 |  | to submitt |  |  |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | 1 |  | Open
Sumec | AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | Cooling method | 1 |  |  |  | 1 |  | to submitt |  |  |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | 1 |  | Open
Sumec | AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | Dimensions and weight | 3 |  |  |  | 1 |  | to submitt |  |  |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | 1 |  | Open
Sumec | AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | Oil weight | 3 |  |  |  | 1 |  | to submitt |  |  |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | 1 |  | Open
Sumec | AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | Protection system | 1 |  |  |  | 1 |  | to submitt |  |  |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | 1 |  | Open
Sumec | AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | Auxiliary service lines | 1 |  |  |  | 1 |  | to submitt |  |  |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | 1 |  | Open
Sumec | AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | Fittings with the transformer | 3 |  |  |  | 1 |  | to submitt |  |  |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | 1 |  | Open
Sumec | AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | Noise levels | 3 |  |  |  | 1 |  | to submitt |  |  |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | 1 |  | Open
Sumec | AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | Warranty and insurance | 1 |  |  |  | 1 |  | to submitt |  |  |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | 1 |  | Open
Sumec | AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | Tests and inspection routines | 1 |  |  |  | 1 |  | to submitt |  |  |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | 1 |  | Open
Sumec | AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | Operational data shall be logged in central operating system (e.g. oil temperature, oil level, pressure, temperature probes (one per phase): Alarm and trip of cell etc.) | 2 |  |  |  | 1 |  | to submitt |  |  |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | 1 |  | Open
Sumec | AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | All documentation, certificates and test protocols shall be provided | 2 |  |  |  | 1 |  | to submitt |  |  |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | 1 |  | Open
Sumec | AR | HV Substation | HV Substation -MV/HV Transformer | Standards | 1.23.7 | IEC 62446 | 1 |  |  |  | 1 |  | to submitt | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | 1 |  | Open
Sumec | AR | HV Substation | HV Substation -MV/HV Transformer | Standards | 1.23.7 | IEC 60076 | 1 |  |  |  | 1 |  | to submitt | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | 1 |  | Open
Sumec | AR | HV Substation | HV Substation -MV/HV Transformer | Standards | 1.23.7 | IEC 60085 | 1 |  |  |  | 1 |  | to submitt | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | 1 |  | Open
Sumec | AR | HV Substation | HV Substation -MV/HV Transformer | Standards | 1.23.7 | IEC 60214 | 1 |  |  |  | 1 |  | to submitt | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | 1 |  | Open
Sumec | AR | HV Substation | HV Substation -MV/HV Transformer | Standards | 1.23.7 | IEC 60137 | 1 |  |  |  | 1 |  | to submitt | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | 1 |  | Open
Sumec | AR | HV Substation | HV Substation -MV/HV Transformer | Standards | 1.23.7 | ASTM d-3487 | 1 |  |  |  | 1 |  | to submitt | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | 1 |  | Open
Sumec | AR | HV Substation | HV Substation -MV/HV Transformer | Quality Assurance | 1.23.7 | Factory witness testing shall be required for MV/HV transformer and switchgear to be installed at this project. | 1 |  |  |  | 1 |  | to confirm | Cannot be evaluated at this stage |  |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | 1 |  | Open
Sumec | AR | HV Substation | HV Substation -MV/HV Transformer | Quality Assurance | 1.23.7 | Type test reports from an independent reputable laboratory shall be submitted with the bid. | 1 |  |  |  | 1 |  | to submitt |  |  |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | 1 |  | Open
Sumec | AR | HV Substation | Due Diligence | Quality Assurance | 1.23.7 | The cost of the due diligence for the HV station to be carried by the Employer through an independent technical consultant will be taken over by the successful bidder up to an amount of 30,000 USD. | 1 |  |  |  | 1 |  | to confirm |  |  |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | 1 |  | Open
Sumec | AR | HV Substation | HV Substation -MV/HV Transformer | Design | 1.23.8 | The separating equipment shall be installed with visible disconnection (pivotable disconnectors). | 1 |  | 1 |  |  |  |  | Cannot be evaluated at this stage |  |  |  | 1 |  | Pass
Sumec | AR | HV Substation | HV Substation -MV/HV Transformer | Design | 1.23.9 | Insulation with PCB (polychlorinated biphenyl) has not been used. | 1 |  | 1 |  |  |  | to confirm |  |  |  |  | 1 |  | Pass
Sumec | AR | HV Substation | HV Substation -MV/HV Transformer | Design | 1.23.10 | The preliminary design of the substation is submitted with the technical bid according to the requirements of Appendix 1 | 1 |  |  |  | 1 |  | SLD , layout not included | Link to Appendix 1 |  |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | 1 |  | Open
Sumec | AR | HV Substation | HV Substation -MV/HV Transformer | Energy Metering System | 1.23.11 | The Energy Metering System will be placed on the HV side of the substation | 1 |  | 1 |  |  |  | detail |  |  |  |  | 1 |  | Pass
Sumec | AR | HV Substation | HV Substation -MV/HV Transformer | Energy Metering System -NTDC specifications | 1.23.11 | Metering Equipment for Electric Energy Transfer between the Companies (Specification No. P-199-08) | 1 |  | 1 |  |  |  | detail |  |  |  |  | 1 |  | Pass
Sumec | AR | HV Substation | HV Substation -MV/HV Transformer | Energy Metering System -NTDC specifications | 1.23.11 | Energy Meters for Grid Metering (Specification No. P-202-2012) | 1 |  | 1 |  |  |  | detail |  |  |  |  | 1 |  | Pass
Sumec | AR | HV Substation | HV Substation -MV/HV Transformer | Energy Metering System -NTDC specifications | 1.23.11 | Voltage Transformers for Special Application (Energy Metering; Specifications No. P-206-05) | 1 |  | 1899-12-31 |  |  |  | detal |  |  |  |  | 1 |  | Pass
Sumec | AR | HV Substation | HV Substation -MV/HV Transformer | Energy Metering System -NTDC specifications | 1.23.11 | Current Transformers for Special Application (spec.No P-205-2005) | 1 |  | 1 |  |  |  | subject to calculations |  |  |  |  | 1 |  | Pass
Sumec | AR | HV Switchgear | HV Switchgear | Project Schedule | 1.24.1 | The switchgear design and order time, for the 132 kV transmission line is detailed and corresponds with the envisaged project schedule. | 1 |  |  |  |  | 1 | need detail drawing |  |  |  |  | 0 |  | Open
Sumec | AR | HV Switchgear | HV Switchgear | Functionalities | 1.24.1 | Nominal system voltage, kV 132 | 1 |  | 1 | [8 empty] | 1 |  | Pass
Sumec | AR | HV Switchgear | HV Switchgear | Functionalities | 1.24.1 | Rated voltage of switch gear, kV 145 | 1 |  | 1 | [8 empty] | 1 |  | Pass
Sumec | AR | HV Switchgear | HV Switchgear | Functionalities | 1.24.1 | Maximum system voltage, kV 145 | 1 |  | 1 | [8 empty] | 1 |  | Pass
Sumec | AR | HV Switchgear | HV Switchgear | Functionalities | 1.24.1 | Rated frequency, Hz 50 | 1 |  | 1 | [8 empty] | 1 |  | Pass
Sumec | AR | HV Switchgear | HV Switchgear | Design factors to be provided | 1.24.2 | Rated voltage | 1 |  | 1 | [8 empty] | 1 |  | Pass
Sumec | AR | HV Switchgear | HV Switchgear | Design factors to be provided | 1.24.2 | Short-duration power withstand frequency voltage | 3 |  | 1 |  |  |  | detai report |  |  |  |  | 1 |  | Pass
Sumec | AR | HV Switchgear | HV Switchgear | Design factors to be provided | 1.24.2 | Rated lightning impulse withstand voltage | 3 |  | 1 |  |  |  | detai report |  |  |  |  | 1 |  | Pass
Sumec | AR | HV Switchgear | HV Switchgear | Design factors to be provided | 1.24.2 | Rated frequency | 3 |  | 1 | [8 empty] | 1 |  | Pass
Sumec | AR | HV Switchgear | HV Switchgear | Design factors to be provided | 1.24.2 | Peak-withstand current | 2 |  | 1 | [8 empty] | 1 |  | Pass
Sumec | AR | HV Switchgear | HV Switchgear | Design factors to be provided | 1.24.2 | Short-circuit making current | 2 |  |  |  | 1 |  | detail report |  |  |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | 1 |  | Open
Sumec | AR | HV Switchgear | HV Switchgear | Design factors to be provided | 1.24.2 | Short-time withstand current | 2 |  |  |  | 1 |  | detail report |  |  |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | 1 |  | Open
Sumec | AR | HV Switchgear | HV Switchgear | Design factors to be provided | 1.24.2 | Short-circuit breaking current | 2 |  |  |  | 1 |  | detail report |  |  |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | 1 |  | Open
Sumec | AR | HV Switchgear | HV Switchgear | Design factors to be provided | 1.24.2 | Insulating medium | 2 |  | 1 | [8 empty] | 1 |  | Pass
Sumec | AR | HV Switchgear | HV Switchgear | Design factors to be provided | 1.24.2 | Second fault rating | 2 |  | 1 | [8 empty] | 1 |  | Pass
Sumec | AR | HV Switchgear | HV Switchgear | Design factors to be provided | 1.24.2 | Busbars | 3 |  | 1 | [8 empty] | 1 |  | Pass
Sumec | AR | HV Switchgear | HV Switchgear | Design factors to be provided | 1.24.2 | Rated normal current for busbars | 3 |  |  |  | 1 | [5 empty] | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | 1 |  | Open
Sumec | AR | HV Switchgear | HV Switchgear | Design factors to be provided | 1.24.2 | Rated normal current for feeders | 3 |  |  |  | 1 | [5 empty] | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | 1 |  | Open
Sumec | AR | HV Switchgear | HV Switchgear | Design factors to be provided | 1.24.2 | Degree of protection | 2 |  |  |  | 1 | [5 empty] | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | 1 |  | Open
Sumec | AR | HV Switchgear | HV Switchgear | Design factors to be provided | 1.24.2 | Second internal arc rating | 3 |  |  |  | 1 | [5 empty] | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | 1 |  | Open
Sumec | AR | HV Switchgear | HV Switchgear | Design factors to be provided | 1.24.2 | Circuit breakers: protection and metering | 1 |  |  |  | 1 | detail | [5 empty] | 1 |  | Open
Sumec | AR | HV Switchgear | HV Switchgear | Design factors to be provided | 1.24.2 | Protection relay | 1 |  |  |  | 1 | detail | [5 empty] | 1 |  | Open
Sumec | AR | HV Switchgear | HV Switchgear | Design factors to be provided | 1.24.2 | Switch disconnector panel | 2 |  | 1 |  |  | detail | [5 empty] | 1 |  | Pass
Sumec | AR | HV Switchgear | HV Switchgear | Design factors to be provided | 1.24.2 | Operating temperature range | 1 |  |  |  | 1 | need confirmation | [5 empty] | 1 |  | Open
Sumec | AR | HV Switchgear | HV Switchgear | Design factors to be provided | 1.24.2 | Warranty and insurance | 1 |  |  |  | 1 | need confirmation | [5 empty] | 1 |  | Open
Sumec | AR | HV Switchgear | HV Switchgear | Design factors to be provided | 1.24.2 | Dimensions and weight | 3 |  |  |  | 1 | to submitt | [5 empty] | 1 |  | Open
Sumec | AR | HV Switchgear | HV Switchgear | Design factors to be provided | 1.24.2 | NEMA enclosure type and IP code | 1 |  |  |  | 1 | to submitt | [5 empty] | 1 |  | Open
Sumec | AR | HV Switchgear | HV Switchgear | Standards | 1.24.2 | IEC 60038 | 1 |  |  |  | 1 | to submitt |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  |  |  | 1 |  | Open
Sumec | AR | HV Switchgear | HV Switchgear | Standards | 1.24.2 | IEC 60095 | 1 |  |  |  | 1 | to submitt |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  |  |  | 1 |  | Open
Sumec | AR | HV Switchgear | HV Switchgear | Standards | 1.24.2 | IEC 62271-200 | 1 |  |  |  | 1 | to submitt |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  |  |  | 1 |  | Open
Sumec | AR | HV Switchgear | HV Switchgear | Standards | 1.24.2 | IEC 60364 | 1 |  |  |  | 1 | to submitt |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  |  |  | 1 |  | Open
Sumec | AR | HV Switchgear | HV Switchgear | Standards | 1.24.2 | Factory witness testing will are required for HV switchgear | 1 |  |  |  | 1 | to submitt |  | Cannot be evaluated at this stage |  |  |  | 1 |  | Open
Sumec | AR | HV Switchgear | HV Switchgear | Standards | 1.24.3 | Type test reports from an independent reputable laboratory shall be submitted | 1 |  |  |  | 1 | to submitt | [5 empty] | 1 |  | Open
Sumec | AR | HV Switchgear | Due Diligence | Quality Assurance | 1.24.3 | The cost of the due diligence to be carried by the Employer through an independent technical consultant will be taken over by the successful bidder up to an amount of 50,000 USD. | 1 |  |  |  | 1 | to confirm | [5 empty] | 1 |  | Open
CHINT | AR | HV Substation | HV Substation | Specific Requirements | 1.23.1 | The HV Substation includes the respective MV switch gears, Transformer MV/ HV. The HV connection is designed to connect to the HV line. | 3 |  |  |  | 1 | need confirmation | [5 empty] | 1 |  | Open
Chint | AR | HV Substation | HV Substation | Specific Requirements | 1.23.2 | Availability and delivery time of the chosen components is detailed | 1 |  |  |  | 1 | need confirmation | [5 empty] | 1 |  | Open
Chint | AR | HV Substation | HV Substation -HV part | Specific Requirements | 1.23.3 | The substation is separated into 2 parts: Medium Voltage part including HV transformer and HV portion of the plant excluding the HV transformer | 1 |  |  |  | 1 | need confirmation | [5 empty] | 1 |  | Open
Chint | AR | HV Substation | HV Substation -HV part | Specific Requirements | 1.23.3 | Double Busbar single breaker scheme shall be designed for HV portion of HV substation | 1 |  |  |  | 1 | need confirmation | [5 empty] | 1 |  | Open
Chint | AR | HV Substation | HV Substation -HV part | HV portion components | 1.23.3 | 132 kV Transformer Bays as per design | 1 |  |  |  | 1 | need confirmation | [5 empty] | 1 |  | Open
Chint | AR | HV Substation | HV Substation -HV part | HV portion components | 1.23.3 | 2x132 kV Line Bays | 1 |  |  |  | 1 | need confirmation | [5 empty] | 1 |  | Open
Chint | AR | HV Substation | HV Substation -HV part | HV portion components | 1.23.3 | 2x132 kV PT bays | 1 |  |  |  | 1 | need confirmation | [5 empty] | 1 |  | Open
Chint | AR | HV Substation | HV Substation -HV part | HV portion components | 1.23.3 | 132 kV Bus Coupler Bay | 1 |  |  |  | 1 | need confirmation | [5 empty] | 1 |  | Open
Chint | AR | HV Substation | HV Substation -HV part | HV portion components | 1.23.3 | Telecom and PLC Equipment | 1 |  |  |  | 1 | need confirmation |  | Which speification are acepted |  |  |  | 1 |  | Open
Chint | AR | HV Substation | HV Substation -HV part | Standards | 1.23.3 | All the schemes including SCADA, PLC, protection scheme, control and monitoring scheme and other design factors, shall be in compliance with the NTDC grid code. | 1 |  |  |  | 1 | need confirmation |  | Link to NTDC grid code |  |  |  | 1 |  | Open
Chint | AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | 3-phase, double wound, continuously rated, oil-cooled, enclosed transformers, use of low loss core steel and close coupled copper windings | 1 |  | 1 | [8 empty] | 1 |  | Pass
Chint | AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | Enclosure specifications (e.g., steel floor, fluid tight, sealed tank) | 1 |  | 1 | [8 empty] | 1 |  | Pass
Chint | AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | Incoming terminals | 1 |  | 1 | [8 empty] | 1 |  | Pass
Chint | AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | Outgoing terminals | 1 |  | 1 | [8 empty] | 1 |  | Pass
Chint | AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | kVA rating | 1 |  | 1 | [8 empty] | 1 |  | Pass
Chint | AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | Primary side voltage | 1 |  | 1 | [8 empty] | 1 |  | Pass
Chint | AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | Secondary side voltage | 1 |  | 1 | [8 empty] | 1 |  | Pass
Chint | AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | Vector group | 3 |  | 1 |  |  |  | need to be verified | to be discussed |  |  |  | 1 |  | Pass
Chint | AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | Insulation type | 1 |  | 1 | [8 empty] | 1 |  | Pass
Chint | AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | Frequency rating | 1 |  | 1 | [8 empty] | 1 |  | Pass
Chint | AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | Short-circuit impedance | 1 |  | 1 | [8 empty] | 1 |  | Pass
Chint | AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | Own consumption | 3 |  | 1 | [8 empty] | 1 |  | Pass
Chint | AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | No-load losses | 1 |  | 1 | [8 empty] | 1 |  | Pass
Chint | AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | Efficiency | 1 |  | 1 | [8 empty] | 1 |  | Pass
Chint | AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | Operating temperature range | 1 |  |  |  | 1 | [5 empty] | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | 1 |  | Open
Chint | AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | Maximum ambient temperature and altitude | 1 |  |  |  | 1 |  |  | to be discussed |  |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | 1 |  | Open
Chint | AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | Humidity tolerance | 2 |  | 1 | [8 empty] | 1 |  | Pass
Chint | AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | Cooling method | 1 |  | 1 | [8 empty] | 1 |  | Pass
Chint | AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | Dimensions and weight | 3 |  | 1 | [8 empty] | 1 |  | Pass
Chint | AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | Oil weight | 3 |  |  |  | 1 | to submitt | [5 empty] | 1 |  | Open
Chint | AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | Protection system | 1 |  |  |  | 1 | to submitt | [5 empty] | 1 |  | Open
Chint | AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | Auxiliary service lines | 1 |  |  |  | 1 | to submitt | [5 empty] | 1 |  | Open
Chint | AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | Fittings with the transformer | 3 |  | 1 | [8 empty] | 1 |  | Pass
Chint | AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | Noise levels | 3 |  | 1 | [8 empty] | 1 |  | Pass
Chint | AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | Warranty and insurance | 1 |  | 1 | [8 empty] | 1 |  | Pass
Chint | AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | Tests and inspection routines | 1 |  | 1 | [8 empty] | 1 |  | Pass
Chint | AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | Operational data shall be logged in central operating system (e.g. oil temperature, oil level, pressure, temperature probes (one per phase): Alarm and trip of cell etc.) | 2 |  |  |  |  | to submitt | [5 empty] | 0 |  | Open
Chint | AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | All documentation, certificates and test protocols shall be provided | 2 |  |  |  |  | to submitt | [5 empty] | 0 |  | Open
Chint | AR | HV Substation | HV Substation -MV/HV Transformer | Standards | 1.23.7 | IEC 62446 | 1 |  |  |  | 1 |  |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  |  | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | 1 |  | Open
Chint | AR | HV Substation | HV Substation -MV/HV Transformer | Standards | 1.23.7 | IEC 60076 | 1 |  |  |  | 1 | to confirm |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  |  |  | 1 |  | Open
Chint | AR | HV Substation | HV Substation -MV/HV Transformer | Standards | 1.23.7 | IEC 60085 | 1 |  |  |  | 1 | to confirm |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  |  |  | 1 |  | Open
Chint | AR | HV Substation | HV Substation -MV/HV Transformer | Standards | 1.23.7 | IEC 60214 | 1 |  |  |  | 1 | to confirm |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  |  |  | 1 |  | Open
Chint | AR | HV Substation | HV Substation -MV/HV Transformer | Standards | 1.23.7 | IEC 60137 | 1 |  |  |  | 1 | to confirm |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  |  |  | 1 |  | Open
Chint | AR | HV Substation | HV Substation -MV/HV Transformer | Standards | 1.23.7 | ASTM d-3487 | 1 |  |  |  | 1 | to confirm |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  |  |  | 1 |  | Open
Chint | AR | HV Substation | HV Substation -MV/HV Transformer | Quality Assurance | 1.23.7 | Factory witness testing shall be required for MV/HV transformer and switchgear to be installed at this project. | 1 |  |  |  | 1 | to confirm |  | Cannot be evaluated at this stage |  |  |  | 1 |  | Open
Chint | AR | HV Substation | HV Substation -MV/HV Transformer | Quality Assurance | 1.23.7 | Type test reports from an independent reputable laboratory shall be submitted with the bid. | 1 |  | 1 |  |  |  | need copyfrom orginal |  |  |  |  | 1 |  | Pass
Chint | AR | HV Substation | Due Diligence | Quality Assurance | 1.23.7 | The cost of the due diligence for the HV station to be carried by the Employer through an independent technical consultant will be taken over by the successful bidder up to an amount of 30,000 USD. | 1 |  |  |  | 1 | to confirm | [5 empty] | 1 |  | Open
Chint | AR | HV Substation | HV Substation -MV/HV Transformer | Design | 1.23.8 | The separating equipment shall be installed with visible disconnection (pivotable disconnectors). | 1 |  |  |  | 1 | to confirm |  | Cannot be evaluated at this stage |  |  |  | 1 |  | Open
Chint | AR | HV Substation | HV Substation -MV/HV Transformer | Design | 1.23.9 | Insulation with PCB (polychlorinated biphenyl) has not been used. | 1 |  | 1 | [8 empty] | 1 |  | Pass
Chint | AR | HV Substation | HV Substation -MV/HV Transformer | Design | 1.23.10 | The preliminary design of the substation is submitted with the technical bid according to the requirements of Appendix 1 | 1 |  |  |  | 1 | to be submitted |  | Link to Appendix 1 |  |  |  | 1 |  | Open
Chint | AR | HV Substation | HV Substation -MV/HV Transformer | Energy Metering System | 1.23.11 | The Energy Metering System will be placed on the HV side of the substation | 1 |  |  |  |  | to be submitted | [5 empty] | 0 |  | Open
Chint | AR | HV Substation | HV Substation -MV/HV Transformer | Energy Metering System -NTDC specifications | 1.23.11 | Metering Equipment for Electric Energy Transfer between the Companies (Specification No. P-199-08) | 1 |  |  |  | 1 | to be submitted | [5 empty] | 1 |  | Open
Chint | AR | HV Substation | HV Substation -MV/HV Transformer | Energy Metering System -NTDC specifications | 1.23.11 | Energy Meters for Grid Metering (Specification No. P-202-2012) | 1 |  |  |  | 1 | to be submitted | [5 empty] | 1 |  | Open
Chint | AR | HV Substation | HV Substation -MV/HV Transformer | Energy Metering System -NTDC specifications | 1.23.11 | Voltage Transformers for Special Application (Energy Metering; Specifications No. P-206-05) | 1 |  |  |  | 1 | to be submitted | [5 empty] | 1 |  | Open
Chint | AR | HV Substation | HV Substation -MV/HV Transformer | Energy Metering System -NTDC specifications | 1.23.11 | Current Transformers for Special Application (spec.No P-205-2005) | 1 |  |  |  | 1 | to be submitted | [5 empty] | 1 |  | Open
Chint | AR | HV Switchgear | HV Switchgear | Project Schedule | 1.24.1 | The switchgear design and order time, for the 132 kV transmission line is detailed and corresponds with the envisaged project schedule. | 1 |  |  |  | 1 | schedule to be submitted | [5 empty] | 1 |  | Open
Chint | AR | HV Switchgear | HV Switchgear | Functionalities | 1.24.1 | Nominal system voltage, kV 132 | 1 |  | 1 | [8 empty] | 1 |  | Pass
Chint | AR | HV Switchgear | HV Switchgear | Functionalities | 1.24.1 | Rated voltage of switch gear, kV 145 | 1 |  | 1 | [8 empty] | 1 |  | Pass
Chint | AR | HV Switchgear | HV Switchgear | Functionalities | 1.24.1 | Maximum system voltage, kV 145 | 1 |  | 1 | [8 empty] | 1 |  | Pass
Chint | AR | HV Switchgear | HV Switchgear | Functionalities | 1.24.1 | Rated frequency, Hz 50 | 1 |  | 1 | [8 empty] | 1 |  | Pass
Chint | AR | HV Switchgear | HV Switchgear | Design factors to be provided | 1.24.2 | Rated voltage | 1 |  | 1 | [8 empty] | 1 |  | Pass
Chint | AR | HV Switchgear | HV Switchgear | Design factors to be provided | 1.24.2 | Short-duration power withstand frequency voltage | 3 |  | 1 | [8 empty] | 1 |  | Pass
Chint | AR | HV Switchgear | HV Switchgear | Design factors to be provided | 1.24.2 | Rated lightning impulse withstand voltage | 3 |  | 1 | [8 empty] | 1 |  | Pass
Chint | AR | HV Switchgear | HV Switchgear | Design factors to be provided | 1.24.2 | Rated frequency | 3 |  | 1 | [8 empty] | 1 |  | Pass
Chint | AR | HV Switchgear | HV Switchgear | Design factors to be provided | 1.24.2 | Peak-withstand current | 2 |  | 1 | [8 empty] | 1 |  | Pass
Chint | AR | HV Switchgear | HV Switchgear | Design factors to be provided | 1.24.2 | Short-circuit making current | 2 |  |  |  | 1 | to be submitted | [5 empty] | 1 |  | Open
Chint | AR | HV Switchgear | HV Switchgear | Design factors to be provided | 1.24.2 | Short-time withstand current | 2 |  |  |  | 1 | to be submitted | [5 empty] | 1 |  | Open
Chint | AR | HV Switchgear | HV Switchgear | Design factors to be provided | 1.24.2 | Short-circuit breaking current | 2 |  |  |  | 1 | to be submitted | [5 empty] | 1 |  | Open
Chint | AR | HV Switchgear | HV Switchgear | Design factors to be provided | 1.24.2 | Insulating medium | 2 |  | 1 |  |  | to be submitted | [5 empty] | 1 |  | Pass
Chint | AR | HV Switchgear | HV Switchgear | Design factors to be provided | 1.24.2 | Second fault rating | 2 |  |  |  | 1 | to be submitted | [5 empty] | 1 |  | Open
Chint | AR | HV Switchgear | HV Switchgear | Design factors to be provided | 1.24.2 | Busbars | 3 |  | 1 |  |  | to be verified | [5 empty] | 1 |  | Pass
Chint | AR | HV Switchgear | HV Switchgear | Design factors to be provided | 1.24.2 | Rated normal current for busbars | 3 |  | 1 | [8 empty] | 1 |  | Pass
Chint | AR | HV Switchgear | HV Switchgear | Design factors to be provided | 1.24.2 | Rated normal current for feeders | 3 |  | 1 | [8 empty] | 1 |  | Pass
Chint | AR | HV Switchgear | HV Switchgear | Design factors to be provided | 1.24.2 | Degree of protection | 2 |  |  |  | 1 | to be submitted | [5 empty] | 1 |  | Open
Chint | AR | HV Switchgear | HV Switchgear | Design factors to be provided | 1.24.2 | Second internal arc rating | 3 |  |  |  | 1 | to be submitted | [5 empty] | 1 |  | Open
Chint | AR | HV Switchgear | HV Switchgear | Design factors to be provided | 1.24.2 | Circuit breakers: protection and metering | 1 |  |  |  | 1 | to be submitted | [5 empty] | 1 |  | Open
Chint | AR | HV Switchgear | HV Switchgear | Design factors to be provided | 1.24.2 | Protection relay | 1 |  |  |  | 1 | to be submitted | [5 empty] | 1 |  | Open
Chint | AR | HV Switchgear | HV Switchgear | Design factors to be provided | 1.24.2 | Switch disconnector panel | 2 |  |  |  | 1 | to be submitted | [5 empty] | 1 |  | Open
Chint | AR | HV Switchgear | HV Switchgear | Design factors to be provided | 1.24.2 | Operating temperature range | 1 |  |  |  | 1 | to be submitted | [5 empty] | 1 |  | Open
Chint | AR | HV Switchgear | HV Switchgear | Design factors to be provided | 1.24.2 | Warranty and insurance | 1 | 1 | [9 empty] | 0 |  | Open
Chint | AR | HV Switchgear | HV Switchgear | Design factors to be provided | 1.24.2 | Dimensions and weight | 3 |  |  |  | 1 | to be submitted | [5 empty] | 1 |  | Open
Chint | AR | HV Switchgear | HV Switchgear | Design factors to be provided | 1.24.2 | NEMA enclosure type and IP code | 1 |  |  |  | 1 | to be submitted | [5 empty] | 1 |  | Open
Chint | AR | HV Switchgear | HV Switchgear | Standards | 1.24.2 | IEC 60038 | 1 |  |  |  | 1 | to be submitted |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  |  |  | 1 |  | Open
Chint | AR | HV Switchgear | HV Switchgear | Standards | 1.24.2 | IEC 60095 | 1 |  |  |  | 1 | to be submitted |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  |  |  | 1 |  | Open
Chint | AR | HV Switchgear | HV Switchgear | Standards | 1.24.2 | IEC 62271-200 | 1 |  |  |  | 1 | to be submitted |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  |  |  | 1 |  | Open
Chint | AR | HV Switchgear | HV Switchgear | Standards | 1.24.2 | IEC 60364 | 1 |  |  |  | 1 | to be submitted |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  |  |  | 1 |  | Open
Chint | AR | HV Switchgear | HV Switchgear | Standards | 1.24.2 | Factory witness testing will are required for HV switchgear | 1 |  |  |  | 1 | to be confiremed |  | Cannot be evaluated at this stage |  |  |  | 1 |  | Open
Chint | AR | HV Switchgear | HV Switchgear | Standards | 1.24.3 | Type test reports from an independent reputable laboratory shall be submitted | 1 |  |  |  | 1 | [5 empty] | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | 1 |  | Open
Chint | AR | HV Switchgear | Due Diligence | Quality Assurance | 1.24.3 | The cost of the due diligence to be carried by the Employer through an independent technical consultant will be taken over by the successful bidder up to an amount of 50,000 USD. | 1 |  |  |  | 1 | to be confiremed | [5 empty] | 1 |  | Open
Zte | AR | HV Substation | HV Substation | Specific Requirements | 1.23.1 | The HV Substation includes the respective MV switch gears, Transformer MV/ HV. The HV connection is designed to connect to the HV line. | 3 |  | 1 | [8 empty] | 1 |  | Pass
Zte | AR | HV Substation | HV Substation | Specific Requirements | 1.23.2 | Availability and delivery time of the chosen components is detailed | 1 |  |  |  | 1 | need to submit detai | [5 empty] | 1 |  | Open
Zte | AR | HV Substation | HV Substation -HV part | Specific Requirements | 1.23.3 | The substation is separated into 2 parts: Medium Voltage part including HV transformer and HV portion of the plant excluding the HV transformer | 1 |  | 1 | [8 empty] | 1 |  | Pass
Zte | AR | HV Substation | HV Substation -HV part | Specific Requirements | 1.23.3 | Double Busbar single breaker scheme shall be designed for HV portion of HV substation | 1 |  | 1 | [8 empty] | 1 |  | Pass
Zte | AR | HV Substation | HV Substation -HV part | HV portion components | 1.23.3 | 132 kV Transformer Bays as per design | 1 |  | 1 | [8 empty] | 1 |  | Pass
Zte | AR | HV Substation | HV Substation -HV part | HV portion components | 1.23.3 | 2x132 kV Line Bays | 1 |  | 1 | [8 empty] | 1 |  | Pass
Zte | AR | HV Substation | HV Substation -HV part | HV portion components | 1.23.3 | 2x132 kV PT bays | 1 |  | 1 | [8 empty] | 1 |  | Pass
Zte | AR | HV Substation | HV Substation -HV part | HV portion components | 1.23.3 | 132 kV Bus Coupler Bay | 1 |  | 1 | [8 empty] | 1 |  | Pass
Zte | AR | HV Substation | HV Substation -HV part | HV portion components | 1.23.3 | Telecom and PLC Equipment | 1 |  |  |  | 1 | details of supply |  | Which speification are acepted |  |  |  | 1 |  | Open
Zte | AR | HV Substation | HV Substation -HV part | Standards | 1.23.3 | All the schemes including SCADA, PLC, protection scheme, control and monitoring scheme and other design factors, shall be in compliance with the NTDC grid code. | 1 |  |  |  | 1 | confirmation required |  | Link to NTDC grid code |  |  |  | 1 |  | Open
Zte | AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | 3-phase, double wound, continuously rated, oil-cooled, enclosed transformers, use of low loss core steel and close coupled copper windings | 1 |  | 1 | [8 empty] | 1 |  | Pass
Zte | AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | Enclosure specifications (e.g., steel floor, fluid tight, sealed tank) | 1 |  | 1 |  |  | details | [5 empty] | 1 |  | Pass
Zte | AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | Incoming terminals | 1 |  | 1 |  |  | details | [5 empty] | 1 |  | Pass
Zte | AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | Outgoing terminals | 1 |  | 1 |  |  | details | [5 empty] | 1 |  | Pass
Zte | AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | kVA rating | 1 |  | 1 | [8 empty] | 1 |  | Pass
Zte | AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | Primary side voltage | 1 |  | 1 | [8 empty] | 1 |  | Pass
Zte | AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | Secondary side voltage | 1 |  | 1 | [8 empty] | 1 |  | Pass
Zte | AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | Vector group | 3 |  | 1 |  |  | need confirmation |  | to be discussed |  |  |  | 1 |  | Pass
Zte | AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | Insulation type | 1 |  | 1 |  |  | need confirmation | [5 empty] | 1 |  | Pass
Zte | AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | Frequency rating | 1 |  | 1 | [8 empty] | 1 |  | Pass
Zte | AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | Short-circuit impedance | 1 |  | 1 |  |  | need confirmation | [5 empty] | 1 |  | Pass
Zte | AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | Own consumption | 3 |  |  |  | 1 | [5 empty] | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | 1 |  | Open
Zte | AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | No-load losses | 1 |  | 1 | [8 empty] | 1 |  | Pass
Zte | AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | Efficiency | 1 |  | 1 | [8 empty] | 1 |  | Pass
Zte | AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | Operating temperature range | 1 |  | 1 | [8 empty] | 1 |  | Pass
Zte | AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | Maximum ambient temperature and altitude | 1 |  | 1 |  |  |  |  | to be discussed |  |  |  | 1 |  | Pass
Zte | AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | Humidity tolerance | 2 |  |  |  | 1 | [5 empty] | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | 1 |  | Open
Zte | AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | Cooling method | 1 |  | 1 | [8 empty] | 1 |  | Pass
Zte | AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | Dimensions and weight | 3 |  |  |  | 1 | [5 empty] | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | 1 |  | Open
Zte | AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | Oil weight | 3 |  |  |  | 1 | [5 empty] | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | 1 |  | Open
Zte | AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | Protection system | 1 |  | 1 |  |  | details of supply | [5 empty] | 1 |  | Pass
Zte | AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | Auxiliary service lines | 1 |  | 1 |  |  | details | [5 empty] | 1 |  | Pass
Zte | AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | Fittings with the transformer | 3 |  | 1 | [8 empty] | 1 |  | Pass
Zte | AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | Noise levels | 3 |  |  |  | 1 | need to submitt | [5 empty] | 1 |  | Open
Zte | AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | Warranty and insurance | 1 |  |  |  | 1 | [5 empty] | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | 1 |  | Open
Zte | AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | Tests and inspection routines | 1 |  |  |  | 1 | [5 empty] | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | 1 |  | Open
Zte | AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | Operational data shall be logged in central operating system (e.g. oil temperature, oil level, pressure, temperature probes (one per phase): Alarm and trip of cell etc.) | 2 |  | 1 |  |  | system details | [5 empty] | 1 |  | Pass
Zte | AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | All documentation, certificates and test protocols shall be provided | 2 |  |  |  | 1 | to be provided | [5 empty] | 1 |  | Open
Zte | AR | HV Substation | HV Substation -MV/HV Transformer | Standards | 1.23.7 | IEC 62446 | 1 |  |  |  | 1 | to be confirmed |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  |  |  | 1 |  | Open
Zte | AR | HV Substation | HV Substation -MV/HV Transformer | Standards | 1.23.7 | IEC 60076 | 1 |  | 1 |  |  |  |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  |  |  | 1 |  | Pass
Zte | AR | HV Substation | HV Substation -MV/HV Transformer | Standards | 1.23.7 | IEC 60085 | 1 |  |  |  | 1 | to be confirmed |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  |  |  | 1 |  | Open
Zte | AR | HV Substation | HV Substation -MV/HV Transformer | Standards | 1.23.7 | IEC 60214 | 1 |  |  |  | 1 | to be confirmed |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  |  |  | 1 |  | Open
Zte | AR | HV Substation | HV Substation -MV/HV Transformer | Standards | 1.23.7 | IEC 60137 | 1 |  |  |  | 1 | to be confirmed |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  |  |  | 1 |  | Open
Zte | AR | HV Substation | HV Substation -MV/HV Transformer | Standards | 1.23.7 | ASTM d-3487 | 1 |  |  |  | 1 | to be confirmed |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  |  |  | 1 |  | Open
Zte | AR | HV Substation | HV Substation -MV/HV Transformer | Quality Assurance | 1.23.7 | Factory witness testing shall be required for MV/HV transformer and switchgear to be installed at this project. | 1 |  |  |  | 1 | to be confirmed |  | Cannot be evaluated at this stage |  |  |  | 1 |  | Open
Zte | AR | HV Substation | HV Substation -MV/HV Transformer | Quality Assurance | 1.23.7 | Type test reports from an independent reputable laboratory shall be submitted with the bid. | 1 |  |  |  | 1 | to be confirmed | [5 empty] | 1 |  | Open
Zte | AR | HV Substation | Due Diligence | Quality Assurance | 1.23.7 | The cost of the due diligence for the HV station to be carried by the Employer through an independent technical consultant will be taken over by the successful bidder up to an amount of 30,000 USD. | 1 |  |  |  | 1 | to be confirmed | [5 empty] | 1 |  | Open
Zte | AR | HV Substation | HV Substation -MV/HV Transformer | Design | 1.23.8 | The separating equipment shall be installed with visible disconnection (pivotable disconnectors). | 1 |  | 1 |  |  |  |  | Cannot be evaluated at this stage |  |  |  | 1 |  | Pass
Zte | AR | HV Substation | HV Substation -MV/HV Transformer | Design | 1.23.9 | Insulation with PCB (polychlorinated biphenyl) has not been used. | 1 |  |  |  | 1 | to be confirmed | [5 empty] | 1 |  | Open
Zte | AR | HV Substation | HV Substation -MV/HV Transformer | Design | 1.23.10 | The preliminary design of the substation is submitted with the technical bid according to the requirements of Appendix 1 | 1 |  | 1 |  |  | need confirmation to comply with tender requirements |  | Link to Appendix 1 |  |  |  | 1 |  | Pass
Zte | AR | HV Substation | HV Substation -MV/HV Transformer | Energy Metering System | 1.23.11 | The Energy Metering System will be placed on the HV side of the substation | 1 |  |  |  | 1 | to be confirmed | [5 empty] | 1 |  | Open
Zte | AR | HV Substation | HV Substation -MV/HV Transformer | Energy Metering System -NTDC specifications | 1.23.11 | Metering Equipment for Electric Energy Transfer between the Companies (Specification No. P-199-08) | 1 |  |  |  | 1 | to be confirmed | [5 empty] | 1 |  | Open
Zte | AR | HV Substation | HV Substation -MV/HV Transformer | Energy Metering System -NTDC specifications | 1.23.11 | Energy Meters for Grid Metering (Specification No. P-202-2012) | 1 |  |  |  | 1 | to be confirmed | [5 empty] | 1 |  | Open
Zte | AR | HV Substation | HV Substation -MV/HV Transformer | Energy Metering System -NTDC specifications | 1.23.11 | Voltage Transformers for Special Application (Energy Metering; Specifications No. P-206-05) | 1 |  | 1899-12-31 | [8 empty] | 1 |  | Pass
Zte | AR | HV Substation | HV Substation -MV/HV Transformer | Energy Metering System -NTDC specifications | 1.23.11 | Current Transformers for Special Application (spec.No P-205-2005) | 1 |  | 1 |  |  | data to be verified | [5 empty] | 1 |  | Pass
Zte | AR | HV Switchgear | HV Switchgear | Project Schedule | 1.24.1 | The switchgear design and order time, for the 132 kV transmission line is detailed and corresponds with the envisaged project schedule. | 1 |  |  |  | 1 | to be confirmed | [5 empty] | 1 |  | Open
Zte | AR | HV Switchgear | HV Switchgear | Functionalities | 1.24.1 | Nominal system voltage, kV 132 | 1 |  | 1 | [8 empty] | 1 |  | Pass
Zte | AR | HV Switchgear | HV Switchgear | Functionalities | 1.24.1 | Rated voltage of switch gear, kV 145 | 1 |  | 1 | [8 empty] | 1 |  | Pass
Zte | AR | HV Switchgear | HV Switchgear | Functionalities | 1.24.1 | Maximum system voltage, kV 145 | 1 |  | 1 | [8 empty] | 1 |  | Pass
Zte | AR | HV Switchgear | HV Switchgear | Functionalities | 1.24.1 | Rated frequency, Hz 50 | 1 |  | 1 | [8 empty] | 1 |  | Pass
Zte | AR | HV Switchgear | HV Switchgear | Design factors to be provided | 1.24.2 | Rated voltage | 1 |  | 1 | [8 empty] | 1 |  | Pass
Zte | AR | HV Switchgear | HV Switchgear | Design factors to be provided | 1.24.2 | Short-duration power withstand frequency voltage | 3 |  |  |  | 1 | to be confirmed | [5 empty] | 1 |  | Open
Zte | AR | HV Switchgear | HV Switchgear | Design factors to be provided | 1.24.2 | Rated lightning impulse withstand voltage | 3 |  |  |  | 1 | to be confirmed | [5 empty] | 1 |  | Open
Zte | AR | HV Switchgear | HV Switchgear | Design factors to be provided | 1.24.2 | Rated frequency | 3 |  | 1 | [8 empty] | 1 |  | Pass
Zte | AR | HV Switchgear | HV Switchgear | Design factors to be provided | 1.24.2 | Peak-withstand current | 2 |  |  |  | 1 | to be confirmed | [5 empty] | 1 |  | Open
Zte | AR | HV Switchgear | HV Switchgear | Design factors to be provided | 1.24.2 | Short-circuit making current | 2 |  |  |  | 1 | to be confirmed | [5 empty] | 1 |  | Open
Zte | AR | HV Switchgear | HV Switchgear | Design factors to be provided | 1.24.2 | Short-time withstand current | 2 |  |  |  | 1 | to be confirmed | [5 empty] | 1 |  | Open
Zte | AR | HV Switchgear | HV Switchgear | Design factors to be provided | 1.24.2 | Short-circuit breaking current | 2 |  |  |  | 1 | to be confirmed | [5 empty] | 1 |  | Open
Zte | AR | HV Switchgear | HV Switchgear | Design factors to be provided | 1.24.2 | Insulating medium | 2 |  | 1 | [8 empty] | 1 |  | Pass
Zte | AR | HV Switchgear | HV Switchgear | Design factors to be provided | 1.24.2 | Second fault rating | 2 |  |  |  | 1 | to be confirmed | [5 empty] | 1 |  | Open
Zte | AR | HV Switchgear | HV Switchgear | Design factors to be provided | 1.24.2 | Busbars | 3 |  | 1 | [8 empty] | 1 |  | Pass
Zte | AR | HV Switchgear | HV Switchgear | Design factors to be provided | 1.24.2 | Rated normal current for busbars | 3 |  | 1 |  |  | to be vrified | [5 empty] | 1 |  | Pass
Zte | AR | HV Switchgear | HV Switchgear | Design factors to be provided | 1.24.2 | Rated normal current for feeders | 3 |  | 1 |  |  | to be vrified | [5 empty] | 1 |  | Pass
Zte | AR | HV Switchgear | HV Switchgear | Design factors to be provided | 1.24.2 | Degree of protection | 2 |  |  |  | 1 | to be vrified | [5 empty] | 1 |  | Open
Zte | AR | HV Switchgear | HV Switchgear | Design factors to be provided | 1.24.2 | Second internal arc rating | 3 |  |  |  | 1 | to be vrified | [5 empty] | 1 |  | Open
Zte | AR | HV Switchgear | HV Switchgear | Design factors to be provided | 1.24.2 | Circuit breakers: protection and metering | 1 |  |  |  | 1 | to be vrified | [5 empty] | 1 |  | Open
Zte | AR | HV Switchgear | HV Switchgear | Design factors to be provided | 1.24.2 | Protection relay | 1 |  |  |  | 1 | detail scope to be submitted | [5 empty] | 1 |  | Open
Zte | AR | HV Switchgear | HV Switchgear | Design factors to be provided | 1.24.2 | Switch disconnector panel | 2 |  |  |  | 1 | to be vrified | [5 empty] | 1 |  | Open
Zte | AR | HV Switchgear | HV Switchgear | Design factors to be provided | 1.24.2 | Operating temperature range | 1 |  |  |  | 1 | to be vrified | [5 empty] | 1 |  | Open
Zte | AR | HV Switchgear | HV Switchgear | Design factors to be provided | 1.24.2 | Warranty and insurance | 1 |  |  |  | 1 | to be vrified | [5 empty] | 1 |  | Open
Zte | AR | HV Switchgear | HV Switchgear | Design factors to be provided | 1.24.2 | Dimensions and weight | 3 |  |  |  | 1 | to be vrified | [5 empty] | 1 |  | Open
Zte | AR | HV Switchgear | HV Switchgear | Design factors to be provided | 1.24.2 | NEMA enclosure type and IP code | 1 |  |  |  | 1 | to be vrified | [5 empty] | 1 |  | Open
Zte | AR | HV Switchgear | HV Switchgear | Standards | 1.24.2 | IEC 60038 | 1 |  |  |  | 1 | to be vrified |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  |  |  | 1 |  | Open
Zte | AR | HV Switchgear | HV Switchgear | Standards | 1.24.2 | IEC 60095 | 1 |  |  |  | 1 | to be vrified |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  |  |  | 1 |  | Open
Zte | AR | HV Switchgear | HV Switchgear | Standards | 1.24.2 | IEC 62271-200 | 1 |  |  |  | 1 | to be vrified |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  |  |  | 1 |  | Open
Zte | AR | HV Switchgear | HV Switchgear | Standards | 1.24.2 | IEC 60364 | 1 |  |  |  | 1 | to be vrified |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  |  |  | 1 |  | Open
Zte | AR | HV Switchgear | HV Switchgear | Standards | 1.24.2 | Factory witness testing will are required for HV switchgear | 1 |  |  |  |  | to be confirmed |  | Cannot be evaluated at this stage |  |  |  | 0 |  | Open
Zte | AR | HV Switchgear | HV Switchgear | Standards | 1.24.3 | Type test reports from an independent reputable laboratory shall be submitted | 1 |  |  |  |  | to be submitted | [5 empty] | 0 |  | Open
Zte | AR | HV Switchgear | Due Diligence | Quality Assurance | 1.24.3 | The cost of the due diligence to be carried by the Employer through an independent technical consultant will be taken over by the successful bidder up to an amount of 50,000 USD. | 1 |  |  |  |  | to confirm | [5 empty] | 0 |  | Open
Tbea | AR | HV Substation | HV Substation | Specific Requirements | 1.23.1 | The HV Substation includes the respective MV switch gears, Transformer MV/ HV. The HV connection is designed to connect to the HV line. | 3 |  | 1 |  |  | confirm the nomber of MV panel are adequate as per sys requiremnts | [5 empty] | 1 |  | Pass
Tbea | AR | HV Substation | HV Substation | Specific Requirements | 1.23.2 | Availability and delivery time of the chosen components is detailed | 1 |  | 1 |  |  | delivery time missing | [5 empty] | 1 |  | Pass
Tbea | AR | HV Substation | HV Substation -HV part | Specific Requirements | 1.23.3 | The substation is separated into 2 parts: Medium Voltage part including HV transformer and HV portion of the plant excluding the HV transformer | 1 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | AR | HV Substation | HV Substation -HV part | Specific Requirements | 1.23.3 | Double Busbar single breaker scheme shall be designed for HV portion of HV substation | 1 |  | 1 |  |  | detail of CB | [5 empty] | 1 |  | Pass
Tbea | AR | HV Substation | HV Substation -HV part | HV portion components | 1.23.3 | 132 kV Transformer Bays as per design | 1 |  | 1 |  |  | confirm the adequacy of prposed equip. to tender reqirement | [5 empty] | 1 |  | Pass
Tbea | AR | HV Substation | HV Substation -HV part | HV portion components | 1.23.3 | 2x132 kV Line Bays | 1 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | AR | HV Substation | HV Substation -HV part | HV portion components | 1.23.3 | 2x132 kV PT bays | 1 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | AR | HV Substation | HV Substation -HV part | HV portion components | 1.23.3 | 132 kV Bus Coupler Bay | 1 |  |  |  | 1 | missing need confirmatation | [5 empty] | 1 |  | Open
Tbea | AR | HV Substation | HV Substation -HV part | HV portion components | 1.23.3 | Telecom and PLC Equipment | 1 |  |  |  | 1 | detail are missing |  | Which speification are acepted |  |  |  | 1 |  | Open
Tbea | AR | HV Substation | HV Substation -HV part | Standards | 1.23.3 | All the schemes including SCADA, PLC, protection scheme, control and monitoring scheme and other design factors, shall be in compliance with the NTDC grid code. | 1 |  | 1 |  |  |  |  | Link to NTDC grid code |  |  |  | 1 |  | Pass
Tbea | AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | 3-phase, double wound, continuously rated, oil-cooled, enclosed transformers, use of low loss core steel and close coupled copper windings | 1 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | Enclosure specifications (e.g., steel floor, fluid tight, sealed tank) | 1 |  | 1 |  |  | details | [5 empty] | 1 |  | Pass
Tbea | AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | Incoming terminals | 1 |  | 1 |  |  | details | [5 empty] | 1 |  | Pass
Tbea | AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | Outgoing terminals | 1 |  | 1 |  |  | details | [5 empty] | 1 |  | Pass
Tbea | AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | kVA rating | 1 |  | 1 |  |  | confir,m to meet System requirements | [5 empty] | 1 |  | Pass
Tbea | AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | Primary side voltage | 1 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | Secondary side voltage | 1 |  | 1 |  |  | subject to design appproval | [5 empty] | 1 |  | Pass
Tbea | AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | Vector group | 3 |  | 1 |  |  |  |  | to be discussed |  |  |  | 1 |  | Pass
Tbea | AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | Insulation type | 1 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | Frequency rating | 1 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | Short-circuit impedance | 1 |  |  |  | 1 | to submitt | [5 empty] | 1 |  | Open
Tbea | AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | Own consumption | 3 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | No-load losses | 1 |  | 1 |  |  | to submitt as per IEC tolerence | [5 empty] | 1 |  | Pass
Tbea | AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | Efficiency | 1 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | Operating temperature range | 1 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | Maximum ambient temperature and altitude | 1 |  |  |  | 1 | to be confirmed |  | to be discussed |  |  |  | 1 |  | Open
Tbea | AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | Humidity tolerance | 2 |  |  |  | 1 | [5 empty] | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | 1 |  | Open
Tbea | AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | Cooling method | 1 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | Dimensions and weight | 3 |  |  |  | 1 | [5 empty] | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | 1 |  | Open
Tbea | AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | Oil weight | 3 |  |  |  | 1 | [5 empty] | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | 1 |  | Open
Tbea | AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | Protection system | 1 |  | 1 |  |  |  | to be submitted and confirm to meet the requirements |  |  |  |  | 1 |  | Pass
Tbea | AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | Auxiliary service lines | 1 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | Fittings with the transformer | 3 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | Noise levels | 3 |  |  |  | 1 | [5 empty] | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | 1 |  | Open
Tbea | AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | Warranty and insurance | 1 |  |  |  | 1 | [5 empty] | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | 1 |  | Open
Tbea | AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | Tests and inspection routines | 1 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | Operational data shall be logged in central operating system (e.g. oil temperature, oil level, pressure, temperature probes (one per phase): Alarm and trip of cell etc.) | 2 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | AR | HV Substation | HV Substation -MV/HV Transformer | Design factors to be provided | 1.23.6 | All documentation, certificates and test protocols shall be provided | 2 |  |  |  | 1 | [5 empty] | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | 1 |  | Open
Tbea | AR | HV Substation | HV Substation -MV/HV Transformer | Standards | 1.23.7 | IEC 62446 | 1 |  | 1 |  |  |  |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  |  |  | 1 |  | Pass
Tbea | AR | HV Substation | HV Substation -MV/HV Transformer | Standards | 1.23.7 | IEC 60076 | 1 |  | 1 |  |  |  |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  |  |  | 1 |  | Pass
Tbea | AR | HV Substation | HV Substation -MV/HV Transformer | Standards | 1.23.7 | IEC 60085 | 1 |  | 1 |  |  |  |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  |  |  | 1 |  | Pass
Tbea | AR | HV Substation | HV Substation -MV/HV Transformer | Standards | 1.23.7 | IEC 60214 | 1 |  | 1 |  |  |  |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  |  |  | 1 |  | Pass
Tbea | AR | HV Substation | HV Substation -MV/HV Transformer | Standards | 1.23.7 | IEC 60137 | 1 |  | 1 |  |  |  |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  |  |  | 1 |  | Pass
Tbea | AR | HV Substation | HV Substation -MV/HV Transformer | Standards | 1.23.7 | ASTM d-3487 | 1 |  | 1 |  |  |  |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  |  |  | 1 |  | Pass
Tbea | AR | HV Substation | HV Substation -MV/HV Transformer | Quality Assurance | 1.23.7 | Factory witness testing shall be required for MV/HV transformer and switchgear to be installed at this project. | 1 |  |  |  | 1 | to be confirmed |  | Cannot be evaluated at this stage |  |  |  | 1 |  | Open
Tbea | AR | HV Substation | HV Substation -MV/HV Transformer | Quality Assurance | 1.23.7 | Type test reports from an independent reputable laboratory shall be submitted with the bid. | 1 |  | 1 |  |  | to be verified | [5 empty] | 1 |  | Pass
Tbea | AR | HV Substation | Due Diligence | Quality Assurance | 1.23.7 | The cost of the due diligence for the HV station to be carried by the Employer through an independent technical consultant will be taken over by the successful bidder up to an amount of 30,000 USD. | 1 |  |  |  | 1 | [5 empty] | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | 1 |  | Open
Tbea | AR | HV Substation | HV Substation -MV/HV Transformer | Design | 1.23.8 | The separating equipment shall be installed with visible disconnection (pivotable disconnectors). | 1 |  | 1 |  |  |  |  | Cannot be evaluated at this stage |  |  |  | 1 |  | Pass
Tbea | AR | HV Substation | HV Substation -MV/HV Transformer | Design | 1.23.9 | Insulation with PCB (polychlorinated biphenyl) has not been used. | 1 |  | 1 |  |  | confirmation statmenrt is required | [5 empty] | 1 |  | Pass
Tbea | AR | HV Substation | HV Substation -MV/HV Transformer | Design | 1.23.10 | The preliminary design of the substation is submitted with the technical bid according to the requirements of Appendix 1 | 1 |  | 1 |  |  |  |  | Link to Appendix 1 |  |  |  | 1 |  | Pass
Tbea | AR | HV Substation | HV Substation -MV/HV Transformer | Energy Metering System | 1.23.11 | The Energy Metering System will be placed on the HV side of the substation | 1 |  |  |  | 1 | need confirmation | [5 empty] | 1 |  | Open
Tbea | AR | HV Substation | HV Substation -MV/HV Transformer | Energy Metering System -NTDC specifications | 1.23.11 | Metering Equipment for Electric Energy Transfer between the Companies (Specification No. P-199-08) | 1 |  |  |  | 1 | need confirmation | [5 empty] | 1 |  | Open
Tbea | AR | HV Substation | HV Substation -MV/HV Transformer | Energy Metering System -NTDC specifications | 1.23.11 | Energy Meters for Grid Metering (Specification No. P-202-2012) | 1 |  |  |  | 1 | need confirmation | [5 empty] | 1 |  | Open
Tbea | AR | HV Substation | HV Substation -MV/HV Transformer | Energy Metering System -NTDC specifications | 1.23.11 | Voltage Transformers for Special Application (Energy Metering; Specifications No. P-206-05) | 1 |  | 1899-12-31 | [8 empty] | 1 |  | Pass
Tbea | AR | HV Substation | HV Substation -MV/HV Transformer | Energy Metering System -NTDC specifications | 1.23.11 | Current Transformers for Special Application (spec.No P-205-2005) | 1 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | AR | HV Switchgear | HV Switchgear | Project Schedule | 1.24.1 | The switchgear design and order time, for the 132 kV transmission line is detailed and corresponds with the envisaged project schedule. | 1 |  |  |  | 1 | need schedule | [5 empty] | 1 |  | Open
Tbea | AR | HV Switchgear | HV Switchgear | Functionalities | 1.24.1 | Nominal system voltage, kV 132 | 1 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | AR | HV Switchgear | HV Switchgear | Functionalities | 1.24.1 | Rated voltage of switch gear, kV 145 | 1 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | AR | HV Switchgear | HV Switchgear | Functionalities | 1.24.1 | Maximum system voltage, kV 145 | 1 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | AR | HV Switchgear | HV Switchgear | Functionalities | 1.24.1 | Rated frequency, Hz 50 | 1 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | AR | HV Switchgear | HV Switchgear | Design factors to be provided | 1.24.2 | Rated voltage | 1 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | AR | HV Switchgear | HV Switchgear | Design factors to be provided | 1.24.2 | Short-duration power withstand frequency voltage | 3 |  |  |  | 1 | [5 empty] | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | 1 |  | Open
Tbea | AR | HV Switchgear | HV Switchgear | Design factors to be provided | 1.24.2 | Rated lightning impulse withstand voltage | 3 |  |  |  | 1 | [5 empty] | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | 1 |  | Open
Tbea | AR | HV Switchgear | HV Switchgear | Design factors to be provided | 1.24.2 | Rated frequency | 3 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | AR | HV Switchgear | HV Switchgear | Design factors to be provided | 1.24.2 | Peak-withstand current | 2 |  |  |  | 1 | [5 empty] | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | 1 |  | Open
Tbea | AR | HV Switchgear | HV Switchgear | Design factors to be provided | 1.24.2 | Short-circuit making current | 2 |  |  |  | 1 | [5 empty] | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | 1 |  | Open
Tbea | AR | HV Switchgear | HV Switchgear | Design factors to be provided | 1.24.2 | Short-time withstand current | 2 |  |  |  | 1 | [5 empty] | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | 1 |  | Open
Tbea | AR | HV Switchgear | HV Switchgear | Design factors to be provided | 1.24.2 | Short-circuit breaking current | 2 |  |  |  | 1 | [5 empty] | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | 1 |  | Open
Tbea | AR | HV Switchgear | HV Switchgear | Design factors to be provided | 1.24.2 | Insulating medium | 2 |  | 1 | [8 empty] | 1 |  | Pass
Tbea | AR | HV Switchgear | HV Switchgear | Design factors to be provided | 1.24.2 | Second fault rating | 2 |  |  |  | 1 | [5 empty] | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | 1 |  | Open
Tbea | AR | HV Switchgear | HV Switchgear | Design factors to be provided | 1.24.2 | Busbars | 3 |  |  |  | 1 | [5 empty] | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | 1 |  | Open
Tbea | AR | HV Switchgear | HV Switchgear | Design factors to be provided | 1.24.2 | Rated normal current for busbars | 3 |  |  |  | 1 | [5 empty] | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | 1 |  | Open
Tbea | AR | HV Switchgear | HV Switchgear | Design factors to be provided | 1.24.2 | Rated normal current for feeders | 3 |  |  |  | 1 | [5 empty] | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | 1 |  | Open
Tbea | AR | HV Switchgear | HV Switchgear | Design factors to be provided | 1.24.2 | Degree of protection | 2 |  |  |  | 1 | [5 empty] | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | 1 |  | Open
Tbea | AR | HV Switchgear | HV Switchgear | Design factors to be provided | 1.24.2 | Second internal arc rating | 3 |  |  |  | 1 | [5 empty] | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | 1 |  | Open
Tbea | AR | HV Switchgear | HV Switchgear | Design factors to be provided | 1.24.2 | Circuit breakers: protection and metering | 1 |  |  |  | 1 | [5 empty] | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | 1 |  | Open
Tbea | AR | HV Switchgear | HV Switchgear | Design factors to be provided | 1.24.2 | Protection relay | 1 |  |  |  | 1 | [5 empty] | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | 1 |  | Open
Tbea | AR | HV Switchgear | HV Switchgear | Design factors to be provided | 1.24.2 | Switch disconnector panel | 2 |  |  |  | 1 | [5 empty] | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | 1 |  | Open
Tbea | AR | HV Switchgear | HV Switchgear | Design factors to be provided | 1.24.2 | Operating temperature range | 1 |  |  |  | 1 | [5 empty] | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | 1 |  | Open
Tbea | AR | HV Switchgear | HV Switchgear | Design factors to be provided | 1.24.2 | Warranty and insurance | 1 |  |  |  | 1 | [5 empty] | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | 1 |  | Open
Tbea | AR | HV Switchgear | HV Switchgear | Design factors to be provided | 1.24.2 | Dimensions and weight | 3 |  |  |  | 1 | [5 empty] | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | 1 |  | Open
Tbea | AR | HV Switchgear | HV Switchgear | Design factors to be provided | 1.24.2 | NEMA enclosure type and IP code | 1 |  |  |  | 1 | [5 empty] | Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria. | 1 |  | Open
Tbea | AR | HV Switchgear | HV Switchgear | Standards | 1.24.2 | IEC 60038 | 1 |  | 1 |  |  |  |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  |  |  | 1 |  | Pass
Tbea | AR | HV Switchgear | HV Switchgear | Standards | 1.24.2 | IEC 60095 | 1 |  | 1 |  |  |  |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  |  |  | 1 |  | Pass
Tbea | AR | HV Switchgear | HV Switchgear | Standards | 1.24.2 | IEC 62271-200 | 1 |  | 1 |  |  |  |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  |  |  | 1 |  | Pass
Tbea | AR | HV Switchgear | HV Switchgear | Standards | 1.24.2 | IEC 60364 | 1 |  | 1 |  |  |  |  | Do we need to know some parameter values according to standards mentioned or just a statement of complience with the standard would be sufficient? |  |  |  | 1 |  | Pass
Tbea | AR | HV Switchgear | HV Switchgear | Standards | 1.24.2 | Factory witness testing will are required for HV switchgear | 1 | [6 empty] | Cannot be evaluated at this stage |  |  |  | 0 |  | Open
Tbea | AR | HV Switchgear | HV Switchgear | Standards | 1.24.3 | Type test reports from an independent reputable laboratory shall be submitted | 1 |  |  |  | 1 | to submitt | [5 empty] | 1 |  | Open
Tbea | AR | HV Switchgear | Due Diligence | Quality Assurance | 1.24.3 | The cost of the due diligence to be carried by the Employer through an independent technical consultant will be taken over by the successful bidder up to an amount of 50,000 USD. | 1 |  |  |  | 1 | to be confirmed | [5 empty] | 1 |  | Open

## ZTE (hidden)
General Questions
Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria.
Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Unclear: We do not understand your proposal, please detail your proposal. Especially confirm that you are compliant with our requested criteria.
Important reasons: due to current uncertainty of the criteria we accept an open status. Please clarify that you acknowledge the criteria and comply unless a reason of high importance will not allow you to comply. In such a situation the parties will seek to agree a compromise.
General understanding: expressions like "shall", "shall be supplied with", "has to be", "must be" have the meaning of "will be delivered"? Please confirm.
Information
well structured documents
good description for non experts
discussing all options (tilt, irr. Sources, structure, …)
11kV MV system
6MW ring systems to 11kV Bus Bar
Listed Standards: 1.TP, p32
3 MV-HV transformers à 40MVA
only 4mm² String cable
2*70mm² double pole in single cable?! | 1.TP, p35
7 irr. Sensors | 1.TP, p35
WR KEHUA: Derating ab >45°C bis max 55°C
Stringbox: RS485 + wireless, IP65, max 55°C (shading!!) | 1.TP, p67
DC 1000 V | 1.TP, p67
Meteo station
Monitoring equipment in HV trafo vicinity | 1.TP, p70
internal roads to inverter: not less than C20 Eurocode2, Din 1045 Betonfestigkeit | 1.TP, p74
Grounding at DIN 18014 | Annex “PV plant grounding diagram”
DC 10-16 strings per combiner
Wording: Battery Pack = Module Rows
It is planned to do afforestation
foundation sub structure with strip footing in Portland Cement is considered Concrete mix design at ACI 318 | 1.TP, p126
Rainwater will be gatered and pumped from site!
Documents
1.TP | D:\8p2\13K4290_Pakistan\Eingang\Anlagendaten\Bids\ZTE\3-Response to Section 2\1-Letter of Technical Bid\Letter of Technical Bid.pdf

## Juwi (hidden)
Questions
Compliance: We assume that your proposal is in compliance with this criteria. Please confirm that your bid is compliant with this criteria.
Location: We can not find the requested criteria in your documents. Please confirm that your bid is compliant with this criteria and show us the reference in your submitted documents.
Unclear: We do not understand your proposal, please detail your proposal. Especially confirm that you are compliant with our requested criteria.
Important reasons: due to current uncertainty of the criteria we accept an open status. Please clarify that you acknowledge the criteria and comply unless a reason of high importance will not allow you to comply. In such a situation the parties will seek to agree a compromise.
General understanding: expressions like "shall", "has to be", "must be" have the meaning of "will be delivered"?
Information
Tilt 20° / 2*20 portrait or 10° - unclear
33kV Transformer / 1800kVA
SMA outdoor 900kW
1000V
DCB Concept
AL DC Main Cable
2 Transformer à 50MW
RMU concept

## ER Checklist
ER Checklist: Confirmations and cross references to documentation |  |  |  |  | Instruction:
Name of Bidder: |  |  |  | IMPORTANT: Some additional information might be required as regards the Employer's Requirment Annexure and clauses. The clause refered in criteria column E refers to section of ER mentioned in column B. | Bidder has to fill in the requested information in columns F, G, and H.
IMPORTANT: Most relevant lines marked in light red. Please be sure to fill these lines thoroughly.
[5 empty] | ONLY to be filled by Bidder |  |  | ONLY to be filled by Employers Consultant
No | Section in Technical Specifications | Topic | Subtopic | Criteria | Confirm Technical Specification [Y/N] | Link to Bidders Document (if applicable) [file name and page] | Remarks / Deviations (if applicable) | Pass =1 | Fail =1 | Open =1 | Question to Bidder for clarification | Comment of 8.2 | Answer of xxxx [date]
1 | 2 |  |  | The PV-Biogas Hybrid System design must be based on proven and highly efficient equipment. The EPC Contractor shall provide a list of all vendors / subcontractors for all main equipment. The PV-Biogas Hybrid System design shall assure a safe, reliable and efficient operation for 20 years’ lifetime under the environmental conditions at the site with minimum operations cost. The EPC Contractor will be required to follow good Engineering and Construction practices. The O&M Contractor will be required to follow good Operation and Maintenance practices. The PV-Biogas Hybrid System has to adhere with all applicable (international and regional) norms, standards and shall be in compliance with the requirements of the Grid Connection Code of Pakistan, and further relevant requirements of the grid operator, including all measures required to ensure compatibility with the net metering policy, if and when it is implemented. Requirements as per Clause considered and met.
2 | 2.1. |  |  | The PV-Biogas Hybrid System, consisting mainly of a PV System, a Biogas System and Battery, will be connected to the medium voltage level of the electricity grid, while the components will be connected to the low voltage level as described in section 3.5.2. All necessary breakers and other equipment of the grid connection required for safety and control of the system shall be included in the bid and their design, delivery and installation will be in the responsibility of the EPC contractor. The Single Line Diagram (SLD) presented in Figure 1 provides an overview of the electric configuration and grid connection of the system as it is foreseen by the Employer. Adaptations are acceptable - subject to approval by the Employer’s Designated Consultants - as long as the Specifications of these Employer’s Requirements are maintained. Details of the grid connection are outlined in section 3.5.2. hereof. Requirements as per Clause considered and met.
3 | 2.2. |  |  | Available Substrates and Functional Requirements as per tables understood and confirmed.
4 | 2.2. |  |  | The Biogas System shall be able to produce the respective amounts of biogas for up to 30 hours, while no biogas generator is operating, the corresponding amount of gas storage needs to be foreseen by the bidder, i.e. a minimum of 2,000 m³. Furthermore, electricity supply for the electric equipment which is required for the safe and efficient operation of the biogas plants must be guaranteed by the system on a 24/7 basis, either by electricity from the grid, or from the PV Biogas Hybrid System itself. For the Biogas Systems, the quality requirements and design recommendations of Annex F: Safety Rules for Biogas Systems, shall be considered for the selection and the installation of each component and equipment of the Biogas System. The described functional requirements of the Biogas System shall be demonstrated, measured and documented within the Performance Acceptance Procedure as described under section 6.3.2. hereof. Requirements as per Clause considered and met.
5 | 2.3. |  |  | Functional Requirements for PV and Battery Systems as per table considered and met.
6 | 2.4. |  |  | Requirements as per Clause considered and met.
7 | 2.5. |  |  | Requirements as per Clause considered and met.
8 | 3.1.1. |  |  | Incomplete bids with information missing or not presented according to the specified structure as defined in Annex C: Information and Structure of Technical Concept of Technical Bid/Schedules A and F might be qualified as unresponsive. This and other requirements as per Clause considered and met.
9 | 3.1.2. |  |  | Timeline and modalities as per Clause considered and agreed.
10 | 3.1.3. |  |  | Requirements as per Clause on field visits considered and met.
11 | 3.1.4. |  |  | Requirements as per Clause on costs for additional Quality Assurance considered and met.
12 | 3.2. | Project Management Plan | - | Requirements as per Clause considered and met.
13 | 3.3.1. | Baseline for Biogas System Plant |  | Considered and understood that this is a proposed design; not mandatory, while component requirements are mandatory.
14 | 3.3.2.1. | Components | Silage platform | The reception tank shall be divided into 2 chambers of 45 m³ each by a middle wall, where the substrate can flow by an overflow from the first into the second chamber.
15 | 3.3.2.1. | Components | Silage platform | The liquid level of the reception tank and the temperature of the substrate mix shall be constantly measured and monitored with the respective sensors.
16 | 3.3.2.4. | Components | Gas Treatment | The required overall biogas storage volume including storage roofs on main digester and the external storage shall be at least 2,000 m³. If statics allow installing a double membrane storage roof on the digester with a total volume of 2,000 m³, and if the EPC Contractor provides a storage volume of 2,000 m³ within the gas membrane roof storage, the external gas storage will not be required.
17 | 3.3.2.6. | Components | Control and Automation | The control and automation concept shall facilitate the complete automatic operation of all mechanical equipment of the Biogas System, document the relevant process parameters and provide a safe and adequate alarm chain. It shall include the following: • Controlling the operation time of pumps, pneumatic and electric valves, agitators and blowers • Setting up the process and alarm hierarchy, e.g. blocking pumps and agitators when certain liquid level is reached, starting safety flare when gas pressure is too high, and starting gas blowers when gas composition and gas pressure in gas storage can allow the operation of the generators, etc. • Measuring and documenting substrate flows, process temperature, liquid levels of reception tank, main digester and separation unit, gas pressure in storages, gas flows, gas composition, gas temperature and tank levels • Visualizing the ongoing process and the relevant parameters and settings for operators • Facilitating remote control via internet access • Allowing manual parameter setting, protected by an operator password
18 | 3.3.2.7. | Components | 100 kWel biogas co-generation units | The biogas conversion shall consist of two generation units.
19 | 3.3.2.1. | Components | Silage platform | Requirements as per Clause considered and met.
20 | 3.4.1. | Components | PV Modules | The EPC Contractor shall provide crystalline type PV Modules of a reputational manufacturer. Every PV module has to have a stabilized power, which is equivalent or greater than its nominal power at STC conditions.
21 | 3.4.1. | Components | PV Modules | The PV modules shall be manufactured in a factory adhering to the standards as defined in Annex F: PV Module Manufacturing Standards. At the time of manufacturing of the Project related PV modules, the EPC Contractor has to ensure the performance of an inspection and production audit witnessed by the Employer and/or its OE. Limitations of access during the inspection and production audit will lead to a rejection of the PV modules without modification of the general project schedule.
22 | 3.4.1. | Components | PV Modules | The Bill of Material (BoM) of the offered PV module type shall be provided with the bid (according to table in Annex E: Information on Bill of Materials (PV Modules). The specific product datasheets of the EVA and the backsheet shall be provided with the bid.
23 | 3.4.1. | Components | PV Modules | The Contractor shall ensure that the BoM of PV modules proposed for the project is identical to the BoM of the PV modules during the certification process according to the IEC standard. In case the proposed BoM is different to the original BoM during certification, the PV modules with the new BoM shall be certified by an independent certified testing laboratory.
24 | 3.4.1. | Components | PV Modules | Manufacturer’s installation guidelines provided with proposal
25 | 3.4.1. | Components | PV Modules | Manufacturer’s confirmation of suitability of PV Module for specific weather conditions and high UV-radiation provided with proposal
26 | 3.4.1. | Components | PV Modules | Provision of guarantees and datasheets provided with proposal
27 | 3.4.1. | Components | PV Modules | Key to module serial numbers in relation to production line and production date provided with proposal
28 | 3.4.1. | Components | PV Modules | Provision of specification and quality test certificates of: glass, encapsulant, cell, EVA, adhesives, busbar, sealant, back sheet, frame, junction box, cable, DC connector provided with proposal
29 | 3.4.1. | Components | PV Modules | Bill of Materials (PV module) provided with proposal
30 | 3.4.1. | Components | PV Modules | Datasheet EVA provided with proposal
31 | 3.4.1. | Components | PV Modules | Datasheet Backsheet provided with proposal
32 | 3.4.1. | Components | PV Modules | Provision of flash test data (upon shipment of PV Modules)
33 | 3.4.2.1. | Components | DC/AC PV Inverter | All documentation, certificates and routine test procedures, shall be provided with the bid.
34 | 3.4.2.1. | Components | DC/AC PV Inverter | The selected inverter shall not only deliver DC to AC conversion for use by the AC load, but also offer the following functionalities: (as per 3.4.2.1.)
35 | 3.4.2.1. | Components | DC/AC PV Inverter | The inverter design shall be in compliance with the applicable standards of Pakistan, the requirements of the Net Metering Grid Connection requirements of Pakistan and further relevant requirements of the grid operator.
36 | 3.4.2.1. | Components | DC/AC PV Inverter | Both string-type and central-type inverters are acceptable. Especially for central-type inverters, the Bidder should explain the concept for minimizing downtime in case of failure.
37 | 3.4.2.2. | Components | DC/AC Battery Inverter (Bi-directional) | The DC/AC Battery Inverter (bi-directional) may be provided as a separate device or as in-built feature of the DC/AC PV Inverter installed at the same location. It shall meet the following technical specifications as minimum.
38 | 3.4.2.2. | Components | DC/AC Battery Inverter (Bi-directional) | The inverter of the battery (see SLD in chapter 2) shall be of hybrid type and be able to work both as grid-tied system (synchronizing to the frequency and voltage of the electric grid from the DISCO connection or established by the biogas generator(s)) as well as an off-grid system (defining and setting the frequency and voltage of the island grid connected to it when both the electricity grid and the biogas generators are not available). In island grid mode, the same 11kV line and main breaker of the system will be used as shown in the SLD in chapter 2, so that all PV power installations can feed into the island grid, and all connected buildings can draw electricity from that same grid, as long as the total demand can be matched by PV and battery.
39 | 3.4.2.2. | Components | DC/AC Battery Inverter (Bi-directional) | Switching between grid-tied mode and off-grid and vice versa shall be performed by the overall control unit. The inverter shall also be able to work as battery charge controller in order to charge the batteries with power from the PV Biogas Hybrid System and grid electricity.
40 | 3.4.2.2. | Components | DC/AC Battery Inverter (Bi-directional) | Additionally, when working in grid-tied mode the inverter shall be able to feed electricity to the grid in case of surplus production and shall be able to use grid electricity for powering the remaining local residual load in case that the generated power does not fully meet the load requirements of the connected loads.
41 | 3.4.2.2. | Components | DC/AC Battery Inverter (Bi-directional) | All documentation, certificates and routine test procedures, shall be provided with the bid.
42 | 3.4.2.2. | Components | DC/AC Battery Inverter (Bi-directional) | The selected inverter shall not only deliver DC to AC conversion, but also offer the following functionalities: (as per 3.4.2.2.)
43 | 3.4.2.2. | Components | DC/AC Battery Inverter (Bi-directional) | The inverter design shall be in compliance with the applicable standards of Pakistan, the requirements of the Net Metering Grid Connection requirements of Pakistan and further relevant requirements of the grid operator.
44 | 3.4.2.3. | Components | DC/AC Battery Inverter (Bi-directional) | To ensure the lifetime of the PV Biogas Hybrid System and its satisfactory performance, a Battery Management System must be used which controls voltages and currents for optimal performance and lifetime of the batteries.
45 | 3.4.3. | Components | Lithium Batteries | The usable storage capacity shall be limited to 90% DoD through the control software of the PV Biogas Hybrid System.
46 | 3.4.3. | Components | Lithium Batteries | The minimum usable storage capacity of the lithium batteries is 25 kWh.
47 | 3.4.3. | Components | Lithium Batteries | The discharge shall be possible within a period of 1.1 hours or less (i.e. C-rate of 0.9C or higher ).
48 | 3.4.4. | Components | Container for Inverters and Batteries | The inverters, batteries, battery charge controller and any protection devices such as fuses and circuit breakers shall be installed in an adequate housing in form of a container or a similar, compact and closed housing
49 | 3.4.4. | Components | Container for Inverters and Batteries | The container shall have a robust locking mechanism in order to prevent any component theft.
50 | 3.4.4. | Components | Container for Inverters and Batteries | Adequate ventilation and cooling shall be present for the container so as to ensure an efficient cooling and prevent excessive heat build-up.
51 | 3.4.4. | Components | Container for Inverters and Batteries | The compartment design shall ensure that each component will be operating within its defined range of operating temperatures (as defined in the corresponding datasheet) for ambient temperatures up to 50°C.
52 | 3.4.4. | Components | Container for Inverters and Batteries | The container shall be sufficiently reinforced in areas with higher static load requirements such as the battery compartment in order to meet static requirements. The enclosure cabinet shall be made out of M.S sheet with 18 standard wire gauge (SWG) or better, powder coated to matt finish.
53 | 3.4.5. | Components | Supporting Structure for PV Modules | The systems shall be fixed-tilted and preferably be south-facing. The tilt angle for the module installation, the angle between the modules and the horizontal plane, shall be of 15° which is the optimum for summer in Punjab region. Having stated this, the exact angle and direction will be finalized between the winning bidder and Employer, and the designated Consultant, during design phase according to the roof orientation of the new buildings etc.
54 | 3.4.5. | Components | Supporting Structure for PV Modules | The modules will be fixed on the building roofs in the quantities as described in 2.3 on the locations as depicted in Annex A: Site Map and Description.
55 | 3.4.5. | Components | Supporting Structure for PV Modules | The height of the modules above rooftop level shall also be carefully chosen, considering factors such as damage from sand driven by wind and clearance from the ground to allow for cooling air to circulate at the back of the module and any condensation of moisture to dissipate.
56 | 3.4.5. | Components | Supporting Structure for PV Modules | Mounting structure to support the module must be made of durable aluminium material, resistant to sandstorms, high wind speeds (up to 40 m/s), corrosion (passing the salt spray test IEC 61701, among other verification), and UV induced degradation.
57 | 3.4.5. | Components | Supporting Structure for PV Modules | The material must be compatible with the module frame material so as to avoid any adverse electrolytic/galvanic effects.
58 | 3.4.5. | Components | Supporting Structure for PV Modules | In general, lightweight structures of aluminium with no need for roof manipulation (like drilling) shall be used. Any other proposed design shall be explicitly explained in the bid in terms of avoidance of rooftop damage.
59 | 3.4.5. | Components | Supporting Structure for PV Modules | The bidders shall provide detailed drawings of any foundations they plan to use.
60 | 3.4.5. | Components | Supporting Structure for PV Modules | All fastening structures must be verified for durability and resistance to environmental degradation for 25 years, the lifetime requirement of the complete structure. Stainless steel fasteners with anti-seize lubricant are required. The structural elements shall consist of anodized aluminium or materials with equivalent if not better properties. The applicable construction codes for each structural element should be quoted.
61 | 3.4.5. | Components | Supporting Structure for PV Modules | The mounting structure must come with an anti-theft protection to impede demounting of modules.
62 | 3.4.5. | Components | Supporting Structure for PV Modules | The mounting structures must be earthed for maximum short-circuit current and lightning protection. A racking design that removes the need of module to module grounding by using the common rail for the grounding is recommended.
63 | 3.4.5. | Components | Supporting Structure for PV Modules | The supporting structure shall match the specific requirements of the roof conditions (including rainwater drainage) / ground conditions and rodents at site.
64 | 3.4.5. | Components | Supporting Structure for PV Modules | Standards: • IEC 61730 (as above) • STS 531
65 | 3.4.6. | Components | DC Cables | The main design requirement is to reduce ohmic losses of DC cabling, without adversely affecting the cost trade-off, to < 1 % at full power under STC conditions. Design calculations through cable loss simulation have to be provided by the bidder for review & approval.
66 | 3.4.7. | Components | DC Connectors | If Multi Contact MC4 compatible DC connectors are used, a combination of different manufacturers is allowed. MC4 compatible connectors have to be certified in written by the manufacturer Multi Contact.
67 | 3.4.7. | Components | DC Connectors | The compatibility between the chosen DC connectors and the DC connectors attached to the PV Modules (if different) needs to be certified by both manufacturers.
68 | 3.4.7. | Components | DC Connectors | AC cables shall be made of copper. Rated voltage, nominal voltage between phase and neutral and nominal voltage between phases shall be according to Pakistani grid code.
69 | 3.4.8. | Components | AC Cabling | AC cables shall be made of copper. Rated voltage, nominal voltage between phase and neutral and nominal voltage between phases shall be according to Pakistani grid code.
70 | 3.4.8. | Components | AC Cabling | AC cables shall be suitable for the environmental conditions at the Project site, including UV protection and rodents.
71 | 3.4.8. | Components | AC Cabling | The main design requirement is to reduce ohmic losses of AC cabling, without adversely affecting the cost trade-off, to below 0.5 % under STC conditions. Design calculations through cable loss simulation to be provided by the bidders for review & commenting.
72 | 3.5.1.2 | Overall Control System | Minimum Functionalities | The system is connected to the electric grid when the grid is available.
73 |  | Overall Control System | Minimum Functionalities | When the grid goes off, the system will disconnect a branch of the grid from the main grid and establish a mini-grid (island mode).
74 |  | Overall Control System | Minimum Functionalities | When grid comes back, the system synchronizes and re-connects to the grid.
75 |  | Overall Control System | Minimum Functionalities | When operating in island mode, solar, biogas and battery parts are synchronized so they can all feed into the mini-grid at the same time.
76 |  | Overall Control System | Optimization | Supply to the connected mini-grids is as close to a 24/7 power supply as possible and economically feasible. If a small number of hours per year of outages occur, there is no penalty associated with them.
77 |  | Overall Control System | Optimization | At grid outages like load shedding, a short interruption is permitted. However, the startup of the island grid needs to be quick and automatic.
78 |  | Overall Control System | Optimization | Storage resources, i.e. biogas and battery storage are used intelligently to provide power supply during load shedding hours as much as possible.
79 |  | Overall Control System | Optimization | Secondary to the first guideline, generation costs per kWh shall be minimized as much as possible.
80 |  | Overall Control System | Optimization | Solar power is utilized as much as possible, either through direct load consumption, grid export or charging of batteries for later usage. An intelligent battery charging mechanism is therefore required.
81 |  | Overall Control System | Optimization | The biogas power system generators (CHP and/or generator) are operated as much as possible in their preferred operating range. Intelligent control between the two biogas generators as well as intelligent supporting charge and discharge of battery power is mandatory to achieve this.
82 |  | Overall Control System | Further development | The system shall be designed such that it can further be optimized during operation. This means, for example, that actual grid availability data as well as load data during island grid operation are logged so that the battery charging and discharging strategy can be adapted, i.e. that the thresholds/control functions for control of storage resources, generators etc. can be adjusted so that the intelligent power supply can be continuously improved based on real-world load profiles acquired during operation.
83 |  | Overall Control System | Interaction with biogas control | The overall control system communicates with and controls the CHP and generators for start-up, shut-down, output power set points etc. The overall control system receives a signal on biogas storage level from the biogas storage via a pressure sensor (or directly from the biogas control system) to estimate the remaining generation hours available from biogas storage. The biogas control system does not control the CHP / generators; it only gives a “CHP/generator available” signal to the overall control system when the conditions are met for the CHP/generator to run.
84 |  | Overall Control System | Indicative input parameters | Understood indicative parameters and understood that they are for reference only.
85 |  | Overall Control System | Indicative output parameters | Understood indicative parameters and understood that they are for reference only.
86 | 3.5.1.2 | Monitoring | Functional Requirments | Automated monitoring and preventive maintenance . Reliable, up-to-date monitoring information on the status of devices, systems, and processes to the system operator. User interface view of alarms and events and acknowledgement. Log control system data to a hard disk at user-specified intervals. Human Machine Interface (HMI) / Supervisory Control and Data Acquisition (SCADA)
87 |  | Monitoring | Displays/Graphic screens | Site plan, SLDs,parameters and sub-system screens. Alarm screen Event log. Etc.
88 |  | Monitoring | Add-ons | IT compatibility
89 |  | Monitoring | Add-ons | Web access
90 |  | Monitoring | Add-ons | Data storage back-up
91 |  | Monitoring | Add-ons | Charts and time plots
92 |  | Monitoring | Add-ons | Export to CSV and XLS
93 |  | Monitoring | Integration of Devices | Integration of all devices via suitable communication/protocol. Etc.
94 |  | Monitoring | Time Synchronization | Time stamps and GMT reference. Etc.
95 |  | Monitoring | Alarm and Event Management | The system shall gather and locally store historical operation/fault.
96 |  | Monitoring | Alarm and Event Management | The system shall foresee the option of automatic email generation with the error text message upon alarm events.
97 |  | Monitoring | Alarm and Event Management | All alarms and associated alarm information will be recorded in an alarm log.
98 |  | Monitoring | Access | At least two access levels as specified in clause.
99 | 3.5.1.3 | System Solution – Non-Functional | Architecture | PLC+user-friendly HMI
100 |  | System Solution – Non-Functional | Architecture | Remote monitoring
101 |  | System Solution – Non-Functional | On-line help | Help system provided as per clause.
102 | 3.5.2 | Grid Connection | - | The PV Biogas Hybrid System shall be connected to the electricity grid.The only connection to the DISCO grid will be at the 200 kVA transformer at the biogas site. The switching between grid and island mode shall be automatic and be operated by the control system of the PV Biogas Hybrid System.
103 | 3.6 | Site Preparation | - | The site layout plant will be part of the design documents and will be subject to approval by the Consultant.
104 | 3.7.1. | Earthing | _ | A comprehensive description and drawing of the earthing concept shall be provided by the bidder as per Clause considered and met.
105 | 3.7.2. | Safety | _ | Requirements as per Clause considered and met.
106 | 3.8. | Labelling | _ | Requirements as per Clause considered and met.
107 | 3.9. | PV Biogas Hybrid System Documentation | _ | The complete as-built documentation of the PV Hybrid Systems shall be provided in compliance with IEC 62446. Additionally, all serial numbers of the PV modules shall be listed including its individual location within the PV Hybrid Systems.
108 | 3.9. | PV Biogas Hybrid System Documentation | _ | Flash report list and electroluminescence images of all PV modules shall be provided in digital form.
109 | 3.9. | PV Biogas Hybrid System Documentation | _ | For the biogas system, the Contractor shall provide all necessary documentation of each equipment, component, part and materials in English language including the declarations of conformity. For the biogas plant, the Contractor shall provide a detailed operation manual including maintenance plan, safety guidelines and fire protection plan according to the local standards. Besides the instructions on the daily safe operation of the biogas plant, the operation manual shall include instructions for initial startup, restart and a safe shut down of the biogas plant, operations instruction in the case of malfunction of equipment, an alarm and hazard defense plan.
110 | 3.10. | Spare Parts Inventory | _ | By or before the operations start date, the Contractor shall setup a spare parts inventory at a location identified in South Punjab and to be approved by the Employer as per Clause considered and met.
111 | 3.11.1. | Equipment and System Warranty | PV Module Product Warranty | The Contractor shall provide a PV module product warranty of at least 10 years.
112 | 3.11.1. | Equipment and System Warranty | PV Module Performance Guarantee | The Contractor shall provide a PV module Performance Guarantee (ensuring the maximum annual degradation of the PV modules) which shall be linear with a fixed annual factor over 25 years.
113 | 3.11.1. | Equipment and System Warranty | Battery Warranties | The Contractor shall provide a product warranty for the batteries of at least 2 years and a performance of 8 years.
114 | 3.11.1. | Equipment and System Warranty | Supporting Structure Warranty | The Contractor shall provide a product warranty for the supporting structure of at least 10 years.
115 | 3.11.2. | Equipment and System Warranty | Construction Product Warranty | The EPC Contractor shall provide a product warranty for all tanks, buildings, pipelines and fundaments of at least 5 years.
116 | 3.11.2. | Equipment and System Warranty | Product Warranty for electrical and mechanical equipment | The EPC Contractor shall provide a product warranty for electrical and mechanical equipment of at least 1 year.
117 | 3.12. | Miscellaneous | _ | A state of the art PV Biogas Hybrid System is required. The fulfilment of all relevant updated IEC and Pakistani Norms, standards and regulations is in full responsibility of the Contractor.
118 | 4. | O&M | Scope of O&M Works | The PV Biogas Hybrid System is designed for an operation lifetime of at least 25 years. Its optimal performance is sensitive to best-in-class O&M practices, which will ensure the best performance during the 25-years period. The bidder is required to describe in detail his definite plans how to execute the below described requirements for the O&M period.
119 | 4.1. | O&M | General Scope of Work | Requirements as per Clause considered and met. The Contractor shall provide operational guarantee for the PV Biogas Hybrid System for the first 2 (two) years after commissioning. Any repair or replacement of component(s) shall be at the expense of the Contractor. The Contractor will provide the complete O&M service during this duration at his own expense.
120 | 4.1. | O&M | General Scope of Work | Due to nature of the batteries, it is possible that the batteries may have completed the guaranteed number of charge cycles before the end of the expected lifetime of 5 years. In such case, the Contractor has to prove that a specific battery reached its maximum number of charge cycles in order to successfully claim the end of battery’s lifetime.
121 | 4.1. | O&M | General Scope of Work | 24/7 on-site monitoring and control of the PV Biogas Hybrid System
122 | 4.1. | O&M | General Scope of Work | Substrate management, incl. coordination of the logistics, substrate purchase, quality assurance, storage, feeding and digestate disposal
123 | 4.1. | O&M | General Scope of Work | Technical operation of the PV Biogas Hybrid System including presence of O&M personnel close to the Project site as required to fulfil all O&M Contract obligations.
124 | 4.1. | O&M | General Scope of Work | Preventive maintenance according to maintenance programs, such as periodic preventive maintenance of inverters, batteries, pumps, motors, valves, agitators, gas membranes, filters, generators and PV modules etc., according to manufacturers’ requirements.
125 | 4.1. | O&M | General Scope of Work | Scheduled inspection routines: e.g. PV modules to check for discoloration, first signs of delamination, loose wires in the electronics, corrosion of mounting structures, erosion.
126 | 4.1. | O&M | General Scope of Work | Maintenance of spare parts inventory (prompt replenishment of used spare parts) including continuous reporting of status and consumption.
127 | 4.1. | O&M | General Scope of Work | Corrective maintenance with guaranteed response and reaction times, including all repair and replacement costs.
128 | 4.1. | O&M | General Scope of Work | Daily cleaning of the PV Biogas Hybrid System site, preventive and corrective maintenance of civil works and cabinets.
129 | 4.1. | O&M | General Scope of Work | Ensuring smooth functioning of data communications over Remote Monitoring System.
130 | 4.1. | O&M | General Scope of Work | Provision of quarterly service reports about performance, repairs, maintenance, and tests.
131 | 4.1. | O&M | General Scope of Work | Ensuring that any warranties and insurance policies for the PV Biogas Hybrid System are assignable / transferrable to Employer in case of change of Contractor.
132 | 4.1. | O&M | General Scope of Work | Provision of all O&M personnel, trained and certified as far as applicable. The staffing concept and selected key employees shall be presented to the Employer for approval.
133 | 4.1. | O&M | General Scope of Work | Arrangement of service contracts with specialized sub-contractors, permitting the requested response and reaction times and quality of work required to maintain the PV Biogas Hybrid System.
134 | 4.1. | O&M | General Scope of Work | Report of O&M activities in a monthly report.
135 | 4.1.1. | O&M | Hiring/ Training Period/ Intial Inspection | The Contractor’s Personnel must be nominated by the Contractor no later than 8 weeks prior to operations start date of the first PV Biogas Hybrid System and contractually hired no later than 4 weeks prior to operations start date of the first PV Biogas Hybrid System.
136 | 4.1.1. | O&M | Hiring/ Training Period/ Intial Inspection | During the construction phase of the PV Biogas Hybrid System, the Contractor’s Personnel shall familiarize itself with the PV Biogas Hybrid System and its documentation, to enable an efficient operation & maintenance from handover day. The Contractor shall also understand all pending items (e.g. punch-list) and performance deficits (if any) for which the EPC Contractor is responsible for, after operations start date.
137 | 4.1.1. | O&M | Hiring/ Training Period/ Intial Inspection | The O&M Contractor shall familiarize itself with the specific PV Biogas Hybrid System equipment and maintenance requirements as imposed by the component manufacturers and Employer. In addition, the O&M Contractor shall arrange and provide all training as a prerequisite for the selected staff, and provide the respective certificates.
138 | 4.1.1. | O&M | Hiring/ Training Period/ Intial Inspection | The EPC Contractor will be required to deliver at least 16 hours of theoretical and hands‐on training to the operators and further individuals as selected by the Employer. The training should include a maintenance and safety plan for the installed equipment and the corresponding documentation, as well as for information about hazards that results from the installation conditions.
139 | 4.1.2. | O&M | Allocation of Operating Staff | The contractor will provide operating staff, trained and certified, for each of the plants. The staffing schedule shall ensure that there is always one operator present on site on a 24/7 basis throughout the year. Operator shall be sufficiently trained to operate the plant and control system, make adjustments to operating parameters, perform safety measures such as emergency shutdowns, inspect all components etc.
140 | 4.1.3. | O&M | Operational Manual | The EPC Contractor shall develop an operational manual for the PV Biogas Hybrid System and all its components and raw and operating materials (such as substrate, active carbon and other consumables etc.), including the appropriate technical specifications, operation safety guidelines, fire and explosion protection plan and maintenance instructions.
141 | 4.1.4. | O&M | Allocation of O&M Personnel | Requirements as per Clause considered and met.
142 | 4.1.5. | O&M | Bank Guarantee | A bank guarantee of 10% of the total EPC and O&M contract value will be handed over by the Contractor to the Owner of the plant. This guarantee will only be returned after the successful completion of the two-year O&M period. Any remaining shortcomings by the O&M contractor during this period will have to be fully rectified or financially compensated before the returning of the bank guarantee.
143 | 4.2.1. | O&M | Daily Operation of the Biogas System | The biogas system requires the 24/7 availability of at least one trained person in charge (in the following: the operator) for the safe and efficient operation of the plant. The operator will conduct the following tasks.
144 | 4.2.1.1. | O&M | Substrate management and feeding | • Acquisition and payment coordination of input substrate and logistics (in cooperation with the O&M Contractor`s financial department) • Quality control and adequate storage and management of incoming substrate. Quality control of the substrate should at least be visual. Impurities, such as stones etc. shall be removed immediately during reception, storage and feeding. • Manual feeding of the reception tank according to the process instructions. The feeding intervals shall be conducted constantly in small charges (at least twice per day) in order not to destabilize the biogas process. • Coordination and storage of the solid digestate for fertilizer purposes • Coordination of distribution of liquid digestate, if necessary
145 | 4.2.1.2. | O&M | Maintaining of Daily Operation Log | The operator shall document the main process parameters on daily basis in the operation log, which includes: a) Amount and type of fed substrates for biogas plants b) Maintenance works and results c) Unusual incidents and undertaken measures
146 | 4.2.1.3. | O&M | Plant Control and Management | The operator shall monitor and adjust the operation of all relevant equipment which assure the expected biogas production yield and quality and the respective electricity generation. Substrate quality, outside temperature, malfunctions and other conditions and circumstances may require the adjustment of operation time and intervals of pumps, agitators, valves, separator, blowers and generators, which shall be done by the respectively trained operator.
147 | 4.2.1.4. | O&M | Standby-duty for malfunctions, unexpected damages and hazards | The Operator needs to make sure that any failures of equipment are detected immediately, and measures are established to avoid any damage to the plant, environmental or person injury of involved staff or the neighboring communities. The standby-duty requires a reaction time of maximum one hour on all automatic alarms and alerts, visual or other danger notices, e.g. from thirds, to ensure human safety and avoid damage of any system component. All set malfunction alerts of lower impact, e.g. failure of monitoring sensors, must be checked by direct personal inspection of the respective equipment.
148 | 4.2.2. | O&M | Regular Inspections and Maintenance of the Biogas System | Independent of the following maintenance instructions, the operating instructions of the manufacturers of all individual components must be observed, such as for pumps, agitators, blowers, valves, compressors, gas membranes, flare, meters and sensors, generators and flares, etc.
149 | 4.2.2.1. | O&M | General Inspection Requirements | • During filling and emptying of tanks and vessels, attention must be given to pressure fluctuations and good accessibility to the operating equipment (pumps, agitators, blowers, valves, etc.) must be ensured. • All kinds of ignition sources in the clarified zones of explosion protection must be avoided.
150 | 4.2.2.2. | O&M | Daily Inspection Requirements | • Recording of the operation data further detailed under section 4.3 • Check of motor oil level of the generators • Check of the process visualization, whether the malfunction lights are illuminated • Check of water pressure in the substrate heating system • Functional check of the air-dosing pump of the desulfurization system • Selection of agitation and substrate feeding intervals, so that no layer of scum or sediment develops • For all inlets and outlets, assure that the substrate flow is maintained according to the process regulations • The injected airflow for desulphurization must be matched to the current gas production rate (max. 6% vol.) • Check of fill levels of reception tank, main digester, separation tank and slurry pond • Check of membranes connectors of the gas storages
151 | 4.2.2.3. | O&M | Weekly Inspection Requirements | • Check of fill level of the sealing liquids in the overpressure and under-pressure protectors and condensate separators; if necessary, in the case of a danger of frost, check the antifreeze agent (if the weather warrants, daily checks are also required) • Functional check of submerged pumps and agitators (propeller), observe whether vibrations are present • Visual inspection of all electric motors (pumps, agitators, blowers, compressors, etc.) and the connection lines • Check of biogas flare, gas pipeline valves for function, contamination and tightness • Analysis of dry matter content and organic matter content of all input substrates and the digestate
152 | 4.2.2.4. | O&M | Monthly Inspection Requirements | • Actuation of all mechanically moving equipment a few times so that they are not stuck • Possibly remove the oil deposits in the CHP unit and clean the oil catch basin
153 | 4.2.2.5. | O&M | Bi-annual Inspection Requirements | • Functional check of the ventilation and exhaust in the machine room of the generators and in the control room • Inspection of the electrical systems for damage • Functional check of the under-pressure monitor of the gas system • Functional check of the gas sensors, fire detector
154 | 4.2.2.6. | O&M | Annual Inspection Requirements | • Check of gas-carrying system parts for damage, tightness and corrosion • Calibration of gas sensors and meters according to the manufacturers specification • Functional check of the fire extinguishers (every 2 years)
155 | 4.2.2.7. | O&M | Inspections and Maintenance Requirements for the generators | For the maintenance of the biogas generators and the CHP unit, the requirements of the manufacturers must be strictly followed and only trained personnel from service companies with the respective manufacturer`s references shall conduct all these maintenance activities which go beyond visual inspection and other activities, which the generator`s manufacturer authorizes to be conducted by the operator after the respective training. For this regard and especially if the Contractor is not the manufacturer of the generators, it is strongly recommended to contract a full maintenance service with the manufacturer or the local distributor of the generators.
156 | 4.2.3. | O&M | Bi-annual Inspections of the PV System | The Contractor shall perform biannual inspections of the PV Biogas Hybrid System, preferably in spring and autumn, within a period of five (5) to seven (7) months from the previous inspection date. The first inspection takes place six (6) months after operations start date. The biannual inspections must follow the detailed inspection procedure and documented accordingly.
157 | 4.2.3.1. | O&M | PV Modules and Supporting Structure | Requirements as per Clause considered and met.
158 | 4.2.3.2. | O&M | Inverters | Requirements as per Clause considered and met.
159 | 4.2.3.3. | O&M | Battery Management System | Requirements as per Clause considered and met.
160 | 4.2.3.4. | O&M | Batteries/Electricity Storage | Requirements as per Clause considered and met.
161 | 4.2.3.5. | O&M | Container for Inverters and Batteries | Requirements as per Clause considered and met.
162 | 4.2.3.6 | O&M | Security System / Theft protection | Requirements as per Clause considered and met.
163 | 4.2.3.7 | O&M | Additional Inspections | Requirements as per Clause considered and met.
164 | 4.2.4. | O&M | Performance of Maintenance and Repair Works | The results of the inspection and maintenance works, as well as the deactivations, must be documented in a report (blank maintenance report example shall be delivered by the Contractor as part of the O&M Works).
165 | 4.2.4. | O&M | Performance of Maintenance and Repair Works | For the performance of the contractual services, the Contractor will be obliged to observe and respect the component manufacturer’s maintenance and operation specifications and regulations (especially for the PV modules, inverters and batteries), in particular during the warranty period.
166 | 4.2.4. | O&M | Performance of Maintenance and Repair Works | For the performance of the contractual services, the Contractor will be obliged to observe and respect local laws, regulations and international PV standards.Throughout the duration of the Contract, the Contractor will be held responsible for public safety at the PV Hybrid System.
167 | 4.2.5. | O&M | Fault management | Requirements as per Clause considered and met.
168 | 4.2.7. | O&M | Repair Works Documentation | All major repair works (defined as all repair works which require spare parts not fully provided by the spare parts inventory) and insurance compensations must be documented in the corresponding monthly reports.
169 | 4.2.8. | O&M | Inspection of Repair Works | The Employer reserves the right to inspect the repair works within three months (90 days) of receiving the repair works documentation. Employer reserves the right to consult an independent expert in the event that any doubt arises as to the Contractor’s performance.
170 | 4.2.9. | O&M | Spare Parts Inventory and Maintenance Tools | The Contractor will provide a spare parts inventory by the start of O&M Period at the latest. The spare parts inventory will be located in a specific container (or separate section of battery or control system housings) with safety locks and connected to a security surveillance system. The Contractor shall operate and maintain the spare parts inventory during the term of the O&M Period. The Contractor will be responsible for the immediate replenishment of the spare parts. The Contractor is responsible to cover all cost for the replenishment of the spare parts inventory within its annual remuneration under the Agreement.
171 | 4.2.9. | O&M | Spare Parts Inventory and Maintenance Tools | The status and consumption of the spare parts inventory must be included in the corresponding monthly reports. The Contractor must provide the necessary set of maintenance tools to perform the services.
172 | 4.2.10. | O&M | Scope of operation of the PV Biogas Hybrid System | Requirements as per Clause considered and met.
173 | 4.3. | O&M | Reporting of all O&M Activities | Requirements as per Clause considered and met.
174 | 4.4.1. | O&M | Change of Inspection and Maintenance Work Procedures | The Contractor shall perform the work in accordance with all applicable laws. In case of conflict between the specified requirements and the applicable law, the Contractor shall propose a solution to adapt the works accordingly and resolve the matter in a mutual sense for Employer’s approval.
175 | 4.4.2. | O&M | Person in Control of PV Hybrid Systems | The Contractor must propose at least one main responsible and suitable person in charge of the PV Hybrid Systems for schools for each district, the “O&M Managers”. These persons must fulfil all local requirements, permits and standards, must have sufficient experience and be approved by Employer. Any replacement or substitute of these persons will be subject to approval by Employer.
176 | 4.4.3. | O&M | Handover of Documentation after end of O&M Contract | Within one month after the end of the O&M Contract, the Contractor must hand over the complete electronic, printed and written documentation for the O&M of the PV Hybrid Systems. This includes the complete documentation which was previously handed over to the Contractor by Employer or its service provider. This also includes the complete raw data of the PV Hybrid System monitoring acquired though the remote monitoring system.
177 | 4.5. | O&M | Codes, Standards,Regulations, Permit, etc. | State of the art O&M is required. The fulfilment of all relevant IEC and Pakistani norms, standards and regulations is the full responsibility of the Contractor.
178 | 5.1. | Independent Quality Assurance and Validation of the Components | Quality Assurance for PV Modules Pre-Shipment | Pre-shipment flash tested data shall be provided for each PV module. The sun simulator must meet the class AAA requirements of IEC 60904-9. The sun simulator must be calibrated with a reference cell, which itself was calibrated by a member of the WPVS scheme, with a maximum uncertainty of Isc of 1%. The flash testing report shall contain the unique barcode and labelled performance headlines (maximum power, short- circuit current, open-circuit voltage,) of the PV module. The flash-test data must be equal to or higher than the single nameplate ratings of the PV module supply. The testing and calibration may be witnessed by the Employer or its OE / laboratory selected by the OE.
179 | 5.1. | Independent Quality Assurance and Validation of the Components | Quality Assurance for PV Modules Pre-Shipment | A narrow range of PV module power tolerances is expected.
180 | 5.1. | Independent Quality Assurance and Validation of the Components | Quality Assurance for PV Modules Pre-Shipment | All PV modules must undergo Electroluminescence (EL) inspection with a resolution of minimum 4 Mega Pixel prior to shipment. The EL pictures must be provided to Employer at the time of the shipment. A maximum of 5 minor defects and no major defects per PV module are allowed.
181 | 5.1. | Independent Quality Assurance and Validation of the Components | Quality Assurance for PV Modules Pre-Shipment | A sufficient EVA cross linking of 75% has to be verified per production line through a gel content test supervised by an accredited independent certified PV module testing agency (accepted by Employer).
182 | 5.2. | Independent Quality Assurance and Validation of the Components | Quality Assurance for PV Modules Post-Shipment | 3 PV module samples shall be taken by a testing laboratory which is selected by the Consultant, in order to perform Electroluminescence inspection tests (EL imaging). The analysis shall be performed in order to ensure that no transport damage occurred to the PV modules as basis for the operations start date acceptance. In case of there is a clear evidence of shipment damage, where multiple major defect(s) are found in the PV modules, the delivery container shall be rejected. In this case the Contractor may request to inspect all PV modules on-site and replace the PV modules with major defects at its own cost. The cost of such additional testing is not in included in the quality assurance cost of the PV Biogas Hybrid Systems.
183 | 5.3. | Independent Quality Assurance and Validation of the Components | Quality Assurance for Inverters | Factory acceptance tests of the inverters shall be well documented for gauging quality standards of the inverter.
184 | 5.3. | Independent Quality Assurance and Validation of the Components | Quality Assurance for Inverters | Check of protection against overload, short-circuit, grid-failure, internal failure, over-temperature (de-rating), surge protection, detection of insulation faults of AC cables.
185 | 5.3. | Independent Quality Assurance and Validation of the Components | Quality Assurance for Inverters | Test run in the field for maximum and European efficiency of all inverters
186 | 5.3. | Independent Quality Assurance and Validation of the Components | Quality Assurance for Inverters | The Contractor shall deliver detailed protocols of performance test run (warm power test) for every single inverter.
187 | 5.3. | Independent Quality Assurance and Validation of the Components | Quality Assurance for Inverters | After commissioning, sample inverters may be measured for the following on-site, by an approved independent technical consultant on behalf of the Employer. The following tests will be performed: o DC-AC conversion efficiency (maximum and European efficiency). o Thermography / temperature measurement.
188 | 5.4. | Independent Quality Assurance and Validation of the Components | Component Inspections after Delivery | The components and equipment of the PV Biogas Hybrid System shall be checked and evaluated based on the laboratory tests, datasheets, quantity and requirements defined in the Employer’s Requirements.
189 | 6. | Acceptance Procedure | Financial Acceptance Procedure | Requirements as per Clause considered and met.

## Annex B Component Info
Annex B: Description of Components |  |  |  |  | Instruction:
Name of Bidder: |  |  | IMPORTANT: Some additional information might be required as regards the Employer's Requirment Annexure and clauses. |  | Bidder has to fill in the requested information in columns G and H.
IMPORTANT: Most relevant lines marked in light red. Please be sure to fill & fulfill these lines thoroughly.
[5 empty] | ONLY to be filled by Bidder |  | ONLY to be filled by Employers Consultant
No | Section in Technical Specifications | Component | Characteristic | Required Value/Function (if any) | Actual Value of Proposed Component | Link to Bidders Document (if applicable) [file name and page] | Pass =1 | Fail =1 | Open =1 | Question to Bidder for clarification | Comment of 8.2 | Answer of xxxx [date]
1 | 3.3.2.1 | Silage platform | Features | Asphalted platform with a drainage system surrounded by concrete walls with a protection layer) for up to 500 tons of silage (e.g. area of 25 m x 8 m with 3 m side walls)
2 | 3.3.2.1 | Asphalted storage platform | Features | Asphalted storage platform for up to 50 tons of dung surrounded by concrete walls
3 | 3.3.2.1 | Underground reception tank | Features | Partly open underground reception tank of 90 m³ (stainless-steel or acid-resistant concrete) with electronic level meter, temperature meter and connection for water dosification, height: max. 5 m, width: ca. 3 m, length ca. 6 m. If installed with concrete, the material specifications for the concrete are as follows: Material: in-situ reinforced concrete, compression strength class >= C25/30, exposition class XA2, high water entrance resistance, used cement should be highly resident against sulphate
4 | 3.3.2.1 | Propeller stirrer for reception tank | Specifications: | 2 x 7,5 kW 3-blade high efficiency designed for substrate dry matter content of up to 15 %, substrate temperature of up to 55°C, pH-value 5 - 8.2, propeller diameter of min. 600mm, including mast and cable for height (+-2m) and direction shifting (+-120°), completely sealed motor housing and epoxy coating for agitator protection (type IP 68)
5 | 3.3.2.2 | Substrate distributer | Features | Stainless steel substrate distributer for substrate distribution connected to reception tank, main digester, separator and open slurry pond. The system shall be installed in a container or a roofed building.
6 | 3.3.2.2 | Rotatory lobe pumps | Mechanical power | 5 kW volume flow of and 8 m height,
7 |  |  | Volume flow | up to 15 m³/h
8 |  |  | Height | 8 m
9 |  |  | Features | capable for pumping substrates with high solid contents (operating intermittent)
10 | 3.3.2.2 | Compressor station | Features | Compressor station for pneumatic valves
11 | 3.3.2.2 | Pneumatic valves | Features | min. 6 pneumatic valves for substrate distributor including sealings, connecting tubes and fittings, DN 200 (suction side) – DN 150 (pressure side), PN 10, epoxy coated, metal-to-metal sealing, stainless steel gate, min. pressure 10 bar, open-close system
12 | 3.3.2.2 | Manual valves | Features | min. 7 manual valves for sealing of tubes from main digester and separator, including sealings and fittings, DN 200 (suction side) – DN 150 (pressure side), PN 10, epoxy coated, metal-to-metal sealing, stainless steel gate, min. pressure 10 bar, lockable in all positions
13 | 3.3.2.2 | Substrate pipeline | Features | HDPE, PN 10, SDR 17, DN 200 (suction side) – DN 150 (pressure side), overall length according to the final piping design of the Contractor, connecting distances should be kept as short as possible
14 | 3.3.2.2 | Heat exchanger system | Features | 50 kW thermal power for substrate preheating, which preheats recirculated substrate from the main fermenter or internal heating system installed in concrete walls and fundament of the main digester. The heating system shall facilitate the maintaining of the required process temperature of 35°C inside the main digester throughout a minimum outside temperature of -5°C.
15 | 3.3.2.2 | Overflows between main digester and slurry pon | Features | Overflows between main digester and slurry pond as an additional way to direct the substrate within the process flow
16 | 3.3.2.2 | Flow meters | Features | 2 electronically readable flow meters to constantly measure and document the pumped substrate flow on the substrate distributor in all directions
17 | 3.3.2.2 | Separation system for digestate | Features | Separation system for digestate consisting in press screw separator of 3-5kW to separate around 3 m³/h of digestate with a DM input of around 5-8%, including reception tank, if needed, and integration into existing biogas system by recirculation into main digester. The solid output of the separator shall reach a minimum dry matter content of 25%.
18 | 3.3.2.3 | Insulated digester concrete tank | Digesting volume | min. 1,500 m³
19 |  |  | Overall height | 6.5 m
20 |  |  | Max. liquid level height | 6 m
21 |  |  | Diameter | 18 m
22 |  |  | Thickness of concrete wall | 0.25-0.3 m depending on final static requirements
23 |  |  | Material | in-situ reinforced concrete, compression strength class >= C25/30, exposition class XA2, high water entrance resistance, used cement should be highly resident against sulphate
24 |  |  | Features | • Thermal insulation with at least normal combustibility, e.g. B2 DIN 4102, in the area of 1 m around gas openings, the insulation must be made from hard material that is difficult to ignite, e.g. B1 DIN 4102, min. thermal conductivity of 0.04 W/m²K • Weather protection layer (e.g. aluminium) for thermal insulation • Epoxy protection layer of upper 2-3 m of the inner tank wall • Concrete fundament according to local water/leakage protection standard (incl. geomembranes, leakage visualization, etc.)
25 | 3.3.2.3 | Working platform | Features | Working platform on upper level of the digester with stairs and bullseye to the digester
26 | 3.3.2.3 | Sample take-out including valve | Features | -
27 | 3.3.2.3 | Double membrane | Features | Double membrane for roof gas storage incl. roof blower, fixing system and security valve with ASTM standard. The external membrane shall fulfil at least following technical requirements: permeability of CH4: < 1000 cm³/m²d bar, low flammability, Adhesion > 150 N/5cm, destruction resistance > 800 g/m²
28 | 3.3.2.3 | Synthetic safety-net plus wooden beam support | Features | Synthetic safety-net plus wooden beam support covering the digester below the gas membranes for maintenance purposes and for capturing solid sulphur after internal desulfurization
29 | 3.3.2.3 | Concrete column | Features | Concrete column in the centre of the digester to maintain wooden beam as a support for the grid
30 | 3.3.2.3 | Pressure sensor | Features | Electronic pressure sensor in gas hood
31 | 3.3.2.3 | Level meters/sensor | Features | Electronic liquid level meters/sensor inside digester
32 | 3.3.2.3 | Temperature sensor | Features | Electronic temperature sensor inside digester
33 | 3.3.2.3 | Slow running agitator | Features | Slow running agitator for high DM contents, 11 kW for fermenters with gas-hood, outside motor, with 2 stainless steel or polymer/steel core propellers (diameters 2.650 and 1.500 mm)
34 | 3.3.2.3 | Fast running propeller stirrer | Features | Fast running propeller stirrer, 1 x 7.5 kW 3-blade high efficiency propeller stirrer for a substrate dry matter content of up to 10 %, substrate temperature up to 55°C, pH-value 6.5 - 8.2, propeller diameter of min. 600 mm, including mast and cable for height (+-2m) and direction shifting (+-120°), completely sealed motor housing and epoxy coating for agitator (type IP 68).
35 | 3.3.2.4 | UV-resistant biogas pipeline | Features | UV-resistant biogas pipeline, stainless steel or HDPE, DN 150. The biogas pipes must have a specific inclination and should be equipped with condensate traps. The biogas piping installed over ground must be made of stainless steel or polyethylene. For underground installations, non-UV resistant pipes can be used.
36 | 3.3.2.4 | Gas flow meter | Features | Gas flow meter (electronical readable) for constant measuring and documentation of biogas flows between 5 and 150 Nm³/h
37 | 3.3.2.4 | Semiautomatic safety flare | Features | Semiautomatic safety flare 150m³/h
38 | 3.3.2.4 | Internal biological desulfurization system | Features | Internal biological desulfurization system by air injection into the gas hood of the main digester
39 | 3.3.2.4 | External desulfurization unit | Features | External desulfurization unit with activated carbon filtration
40 | 3.3.2.4 | Gas analyser | Features | Gas analyser for CH4, H2S, O2 for constant measuring and documentation of biogas flows between 5 and 100 Nm³/h
41 | 3.3.2.4 | Biogas chiller | Features | Biogas chiller for cooling and condensation (de-moisturing) for the required biogas flow, humidity and temperature
42 | 3.3.2.4 | Biogas condensation tank | Features | Biogas condensation tank with submergible pump and piping for pumping condensation water into storage lagoon
43 | 3.3.2.4 | Biogas blower | Features | Biogas blower up to 150 m³/h and 250 mbar incl. safety valves
44 | 3.3.2.4 | External gas storage balloon | Features | • Single-membrane type • Min. volume: 2.000m³ - V (roof storage main digester) • Technical specifications: permeability of CH4: < 1000 cm³/m²d bar, low flammability, Adhesion > 150 N/5cm, destruction resistance > 800 g/m²
45 | 3.3.2.5 | Open Lagoon | Features | 5,000 m³ digestate including geomembrane/soil cover which complies with local ground water protection standards
46 | 3.3.2.6 | Control cabinet and automation unit(s) | Features | Control cabinet and automation unit(s) for feeding, pumping, stirring, managing of CHP & flares, alarm settings regarding temperature, liquid levels, pressure, pH, CH4, H2S and regarding the handling of other installed equipment (blowers, valves etc.)
47 | 3.3.2.6 | Housing for control interface (HMI) | Features | Adequate container or housing for control interface (HMI) (ideally same as for the overall control system)
48 | 3.3.2.7 | 100 kWel biogas co-generation units | Features | Cogeneration units including heat exchangers for exhaust gas and cooling water, thermal capacity min. 100 kW, el. efficiency of min. 35%, thermal efficiency of min. 35%, cooling unit for thermal energy, catalysator, internal control cabinet, minimum methane content of biogas = 50%, the generator shall be designed according to the following standards: CEI 2-3, IEC 34-1, EN 60034-1, VDE 0530, BS 4999-5000, C22.2 No14- 95-No100-95, max. exhaust emissions with catalysator: NOx: 500 mg/Nm³, CO: 300 mg/Nm³, Formaldehyde: 40 mg/Nm³, Dust Particles: 20 mg/Nm³, SO2: 35 mg/Nm³
49 | 3.3.2.7 | Insulated heat buffer tank | Features | 5 m³ insulated heat buffer tank and respective heating system incl. pumps, valves and connection for heating circuit 90/70°C (for further connection to substrate heating system)
50 | 3.3.2.7 | Biogas generator | Features | 100 kW biogas generator, el. efficiency of min. 35%, design based on standard conditions according to DIN ISO 3046-1
51 | 3.3.2.7 | Electric integration of all components and equipment | Features | Electric integration of all components and equipment
52 | 3.3.2.7 | Sound-proof canopy | Features | Sound-proof canopy, building or container for CHP and generator
53 | 3.4.1 | PV Module | Manufacturer and model
54 |  |  | Type of equipment | Mono- or polycrystalline
55 |  |  | Maximum rated power | 265 Wp or higher (60 cell modules only)
56 |  |  | Rated power tolerances (+/-) | Positive tolerance only
57 |  |  | Power conversion efficiency at STC
58 |  |  | Power at 200 W/m² (25°C, AM 1.5) | Linear behavior with power not less than 95% of the expected output
59 |  |  | Maximum efficiency at 200 W/m² (25°C, AM 1.5) | Linear behavior with power not less than 95% of the expected output
60 |  |  | Series fuse rating
61 |  |  | PV module product warranty | Minimum of 10 years
62 |  |  | PV module performance guarante | Minimum of 25 years
63 |  |  | Power output within 10 years | Shall not fall below 90%
64 |  |  | Power output within 25 years | Shall not fall below 80%
65 |  |  | Type of Performance Guarantee | Shall be linear
66 |  |  | Voltage at the maximum power point (Vmpp)
67 |  |  | Current at the maximum power point (Impp)
68 |  |  | Open-circuit voltage (Voc)
69 |  |  | Short-circuit current (Isc)
70 |  |  | Maximum system voltage (Vmax)
71 |  |  | Temperature coefficient of short-circuit current (TC Isc)
72 |  |  | Temperature coefficient of open-circuit voltage (TC Uoc)
73 |  |  | Temperature coefficient of maximum power (TC Pmpp) | 0.43% / C or less
74 |  |  | Tolerance to wind (maximum load) and hailstone impact
75 |  |  | No. of integrated bypass diodes
76 |  |  | Dimensions
77 |  |  | Weight
78 |  |  | No. of cells in series
79 |  |  | Type of frame
80 |  |  | Ingress Protection (IP) rating of junction box | IP67
81 |  |  | Cable length
82 |  |  | DC Connector manufacturer and type
83 |  |  | Ingress Protection (IP) rating of DC Connectors
84 |  |  | Total no. of PV Modules and total kWp
85 |  |  | Manufacturer’s installation guidelines
86 |  |  | Manufacturer’s confirmation of suitability of PV Module for specific weather conditions and high UV-radiation
87 |  |  | Provision of guarantees and datasheets
88 |  |  | Key to module serial numbers in relation to production line and production date.
89 |  |  | Provision of specification and quality test certificates of: glass, encapsulant, cell, EVA, adhesives, busbar, sealant, back sheet, frame, junction box, cable, DC connector
90 |  |  | Bill of Materials (PV Module)
91 |  |  | Datasheet EVA
92 |  |  | Datasheet Backsheet
93 |  |  | Certifications | IEC61215 & IEC 61730 IEC 60904-1, IEC 60904-3
94 |  |  | Cable | 4 mm2 (IEC), 1000mm or above flexible (tin coated) , UV resistive , IEC compliant with IP 65 weather proof clips
95 |  |  | Extended lifetime tests OR BOM | IF OPTION A: Following test reports from independent certified lab must be provided if the bidder is not using critical items of the BOM as set forth in Annex E. The following extended lifetime test result must be provided. IF OPTION B: See Annex E (sheet) - Details of BOM
96 | 3.4.2.1 | DC/AC PV Inverter | Inverter Rated Power (AC) (Output) | As per design
97 |  |  | IP Rating | IP 20 or higher
98 |  |  | Output Type | Pure Sine wave, hybrid inverter (grid interactive (feedback enabled)/ on-grid hybrid inverters) Grid feed-in function should be controllable
99 |  |  | THD | < 3%
100 |  |  | EU/CEC efficiency | >95%
101 |  |  | Safety Standards | Must meet IEC62109-1/2 certifications
102 |  |  | EMC | IEC 61000 family or equivalent
103 |  |  | Grid Connection requirements | The grid tied inverter must meet grid connection certificate for a country with utility voltage & frequency similar to local grid. Any certification such as VDE 126-1-1, VDE 4015, G83, G59, AS/ NZS 4777.2, AS / NZS 4777.3 will be acceptable.
104 |  |  | Manufacturer | Renowned and verifiable brand having successful history in similar climatic conditions.
105 |  |  | Warranty | 5-year transferable warranty from the original inverter manufacturer shall be provided
106 |  |  | Type/Model number
107 |  |  | Datasheet
108 |  |  | Certifications
109 |  |  | Installation Guide
110 |  |  | Manual
111 | 3.4.2.2 | DC/AC Battery Inverter (Bi-directional) | Inverter Rated Power (AC) (Output) | As per design
112 |  |  | IP Rating | IP 20 or higher
113 |  |  | AC input | 170 Vac – 250 Vac per phase
114 |  |  | Safety Standards | Must meet IEC62109-1/2, IEC62477-1 or equivalent certifications
115 |  |  | EMC | IEC 61000 family or equivalent
116 |  |  | EU/CEC efficiency | > 90 %
117 |  |  | Manufacturer | Renowned and verifiable brand
118 |  |  | Warranty | 5-year transferable warranty
119 |  |  | Battery Management System | Adequate BMS for proper control of battery charging and maximum lifetime
120 |  |  | Type/Model number
121 |  |  | Datasheet
122 |  |  | Certifications
123 |  |  | Installation Guide
124 |  |  | Manual
125 | 3.4.3. | Battery Storage System | Manufacturer/Supplier
126 |  |  | Supplier experience with BSS | At least 5 units delivered and operating for off-grid and/or hybrid applications
127 |  |  | Supplier operational experience in BSS market | At least 1 year
128 |  |  | Type/Model number
129 |  |  | Datasheet
130 |  |  | Certifications
131 |  |  | Warranties
132 |  |  | Installation Guide
133 |  |  | Manual
134 | 3.4.3. | Batteries / Electricity Storage System | Battery type & technology | Lithium based battery
135 |  |  | Individual battery voltage | As per proposed design (recommended 48 Volt nominal)
136 |  |  | Battery life | >4500 cycles @ 90% DoD or better
137 |  |  | C-rate | 0.9C or higher for charge and discharge
138 |  |  | Battery Management System | Integrated
139 |  |  | Self-discharge | <4%/month with BMS connected
140 |  |  | Certifications | IEC 62619 or equivalent
141 |  |  | Manufacturer | Renowned international supplier with fully automated production facilities
142 |  |  | Manufacturing date | < 6 months before installation
143 |  |  | Type/Model number
144 |  |  | Datasheet
145 |  |  | Warranties
146 |  |  | Installation Guide
147 |  |  | Manual
148 | 3.4.4 | Contrainer for Inverters and Batteries | M.S sheet with standard wire gauge (SWG), powder coated to matt finish | 18 standard wire gauge (SWE) or higher
149 |  |  | IP rating | IP 54 or higher
150 |  |  | Design/drawing of the container(s)
151 |  |  | Material specifications
152 |  |  | Documentation which proves the suitability for Project
153 |  |  | Datasheet
154 |  |  | Brief documentation of cooling system (design cooling load, datasheets of cooling devices, brief concept description )
155 | 3.4.5. | Roof Mounting System | Inclination angle | 15 Degrees
156 |  |  | Orienation | Mostly south orientation but following the general orientation of the roof. A more eastern orientation (SEE maximum) would be preferable to a western deviation (SSW maximum) as the electrical load requirement will be mostly before noon.
157 |  |  | System | Low ballast without penetrating the roof skin
158 |  |  | Dead load | Maximum 1000 N/m2
159 |  |  | Windspeed tolerance | Up to 40 m/s
160 |  |  | Corrosion resistant/proof | Passing the salt spray test IEC 61701, among other verification
161 |  |  | Durability and resistance to environmental degradation | At least twenty five (25) years
162 |  |  | Structural Elements | Anodized aluminium, galvanized steel as per ASTM A123/A 123M, or materials with equivalent if not better properties and compatible to the PV module frame
163 |  |  | Fasteners | Stainless Steel with anti-seize lubricant
164 |  |  | Grounding | maximum short-circuit current and lightning protection
165 |  |  | Clamps | Suitable for the fram height of proposed PV module
166 |  |  | Manufacturer information
167 |  |  | General Design/Drawing of mounting structure
168 |  |  | Material specifications
169 |  |  | Datasheet
170 |  |  | Design calculations / structural analysis
171 |  |  | Applicable construction codes
172 |  |  | Certifications
173 |  |  | Warranties
174 | 3.4.6 | DC Cables | Ohmic losses of DC cabling under STC conditions | < 1 %
175 |  |  | String cables | single conductor type, copper, cross-sectional area of 4 mm² or higher, 1000 V / Class II (according to protection class II / 1000V, IEC 61140, single core cable, tinned copper conductor, XLPE Insulation, double EVA jacket (resistant to heat and cold, resistant to ozone, UV, oil and chemicals), Temperature: 90 º C (Temperature Max. allowable: 120 º C), Halogen free
176 |  |  | Manufacturer information
177 |  |  | Datasheet
178 |  |  | Detailed technical specifications
179 |  |  | Certifications
180 |  |  | Cable loss simulation (during implementation phase)
181 |  |  | Warranties
182 | 3.4.7 | DC Connectors | Design Factors to be met | High current rating
183 |  |  |  | Minimal contact resistance
184 |  |  |  | Convenient handling
185 |  |  |  | Broad compatibility
186 |  |  |  | Incompatibility with AC connectors to avoid mistakes during installation
187 |  |  |  | Force required to unlock connectors from cables, whether a tool is required for it or not
188 |  |  |  | Minimum Ingress Protection (IP) rating: IP 67
189 |  |  | Manufacturer information
190 |  |  | Datasheet
191 |  |  | Certifications
192 |  |  | Warranties
193 |  |  | Compatibility statements
194 | 3.4.8 | AC Cabling | Conductor | Copper
195 |  |  | Rated Voltage
196 |  |  | Ohmic losses of AC cabling under STC conditions | below 0.5 %
197 |  |  | Features | suitable for the environmental conditions at the Project site, including UV protection and rodents
198 |  |  | Manufacturer information
199 |  |  | Datasheet
200 |  |  | Certifications
201 |  |  | Warranties
202 | 3.5.2 | Grid Connection | Compliance with Net Metering Scheme
203 |  |  | Meter Supplier and Model
204 | 3.5.3 | MV Switchgear | Features | The MV Switchgear shall be SF6 gas insulated or VCB (Vacuum circuit breaker). The MV Switchgear shall be automatic so that it can be controlled by the control system. The separating equipment shall be installed with visible disconnection (pivotable disconnectors).Interlocks will also be mechanically interlocked between line MV switchgears.
205 |  |  | Manufacturer information
206 |  |  | Datasheet including:  System nominal voltage  System maximum voltage  Rated lightning impulse voltage  Rated power frequency withstand voltage  Rated short circuit current  Rated duration of short circuit current
207 |  |  | Certifications
208 |  |  | Warranties
209 |  |  | Standards and certifications |  IEC 62446  IEC 62271-200  IEC 60529  Other applicable standards
210 | 3.5.4 | Surge Protection Devices and Lightening Protection | Type | 1) Grid input side – Type 2 2) PV input side – Type 2
211 |  |  | Standards and certifications | The SPD supplied must be certified according to IEC 61643-11
212 |  |  | Manufacturer information
213 |  |  | Datasheet
214 |  |  | Certifications
215 |  |  | Warranties

## Annex E BOM
Annex E | If the Bidder opts for option B of section 3.4.1., both tables shall be filled and sub-suppliers from below have to be used. Otherwise, one table is sufficient.
Name of Bidder:
Alternative 1: |  | ONLY to be filled by Bidder
No | Material | Supplier | Type and Description
1 | Cell
2 | Glass (Front Cover)
3 | Backsheet
4 | Encapsulation
5 | Frame
6 | Junction Box
7 | Adhesive (For Frame)
9 | Ribbon
Alternative 2:
No | Material | Supplier | Type and Description
1 | Cell
2 | Glass (Front Cover)
3 | Backsheet
4 | Encapsulation
5 | Frame
6 | Junction Box
7 | Adhesive (For Frame)
9 | Ribbon
Permitted sub-suppliers:
No | EVA
1 | Bridgestone Corporation (G.M.G Corporation)
2 | 3M
3 | Hangzhou First PV Material Co., Ltd
4 | Changzhou Sveck Technology Co., Ltd
5 | Shanghai HIUV New Materials Co., Ltd
6 | Guangzhou Lushan New Materials Co., Ltd
No | Backsheet
1 | KREMPEL-GROUP (KREMPEL GmbH)
2 | Isovoltaic AG
3 | Taiflex Scientific Co., Ltd
4 | Coveme S.p.a.
5 | SFC Co., Ltd
6 | Cybrid Technology Inc
7 | Jolywood (Suzhou) Sunwatt Co., Ltd
8 | Hangzhou First PV Material Co., Ltd
9 | Changshu Top Solar Material Co., Ltd
10 | Zhongtian Photovoltaic Materials Co., Ltd

## For info - Annex C Evaluation
Evaluation of Technical Bid - for Bidders' information
No | Topic | Subtopic | Points | Criteria | Comments 8.2 | Comments of Bidder | Comments 8.2 | Comments of Bidder
1 | Functional requirements (Schedule A to Bid) | Description of the system proposed by the bidder in words: general overview, functionality, special features etc. | 10 | Complete, understandable, fulfills functional requirements, shows Bidder's competence
2 |  | SLD of overall system for both sites separately, with protection functions, including all required protection devices, ratings of components and overall functional design to demonstrate inter-compatibility of the individual components, in line with specifications from 2.1 | 10 | Complete, understandable, fulfills functional requirements, shows Bidder's competence
3 |  | Layouts of Biogas System for both sites separately. This also includes a preliminary flow-sheet diagram with all relevant civil and electro-mechanic components and equipment and a general layout of the constructions (tanks, pipelines, platforms, housings) for all main components of the biogas system. The layouts may be similar or different as the proposed designs as per Annex D: Flow Diagram for Biogas Systems Plant Site 1 and Annex E: Flow Diagram for Biogas Systems Plant Site 2, but they must fulfill the functional requirements as per 2.2. | 20 | Complete, understandable, fulfills functional requirements, shows Bidder's competence
4 |  | General layout drawing of PV and Battery Systems of the PV Biogas Hybrid System including layout of the PV modules, inverter, batteries, container, etc. for both sites separately (minimum SLD and string plan including main breakers; rough physical layout). Must fulfill functional requirements as per 2.3. | 10 | Complete, understandable, fulfills functional requirements, shows Bidder's competence
5 | Schedule D to Bid | Rough description of Project Management Plan as per 3.2. and Schedule D to Bid. A full-fledged Project Management Plan is NOT required before selection of winning bidder. | 5 | Complete, understandable, fulfills functional requirements, shows Bidder's competence
7 | Component information: List of major electromechanical equipment suppliers, final product data, datasheets and specifications. (Schedule F to Bid / Annex B Component Info Excel sheet) | Biogas: Supplier and model name for all major components of both plants as listed in 2.2; incl. data sheets for the following components: membranes, pumps, agitators, generators and CHP. Description and supplier of biogas control; all component information as specified in the relevant chapters (see 3.3, 3.4) | (pass check, no grading)
8 |  | PV: All component information as specified in the relevant chapters (see 3.5) | (pass check, no grading)
9 |  | Grid connection and switchgears: Supplier and model name for all switchgears (automated and manual) and safety and surge protection devices. Must be compliant with 3.6.2, 3.6.3, 3.6.4. | (pass check, no grading)
10 | (Schedule F to Bid) | Control: Description of the planned control system: Supplier and model name for main hardware (PLC), software solution description (platform, self- or third-party developed, if possible 2-3 screenshots of HMI etc.). Must be compliant with 3.6.1. Must explain background of how the required functionalities (island grid operation, optimization of parameters etc.) is achieved. | 15 | Complete, understandable, fulfills functional requirements, shows Bidder's competence
11 |  | Description of Component Warranties: Must comply with 3.12. | 5 | Complete, understandable, fulfills functional requirements, shows Bidder's competence
12 | O&M Scope (Schedule A to Bid) | Brief description of planned maintenance concept: staff, schedules, relationships with equipment suppliers. Must meet 4. | 5 | Complete, understandable, fulfills functional requirements, shows Bidder's competence
13 |  | Brief description of planned operation concept: staff, schedules, fault management, operation quality assurance and optimization. Must meet 4. | 5 | Complete, understandable, fulfills functional requirements, shows Bidder's competence
| Bidding Documentation (Annex B Component Info Excel sheet and ER checklist) | Proper and complete information on ER Requirements (sheet 1), Component info (sheet 2), and links provided. | 10
|  | Documentation on components provided in soft copy (manuals, warranties, data sheets etc. as per ER chapters) | 5
| Total points: |  | 100
| Points required for passing technical evaluation: |  | 65

## For info - Completeness check
No | Chapter/Clause in RfP | Topic | Subtopic | Additional Evaluation Heading | Criteria | Check | Link to Bidders Documents ( if applicable) | Question to Bidder for clarification | Comments 8.2 | Comments of Bidder
ITB, APPENDIX A: EVIDENCE OF BIDDER’S CAPABILITY
1 | 1 |  | Name of Bidder, business address and country of incorporation. |  | Provided as per Schedule
2 | 2 |  | Type of firm whether individually owned, partnership, corporation or joint venture and the names of its owners or partners. |  | Provided as per Schedule
3 | 3 |  | Location and address of manufacturing facilities as applicable. |  | Provided as per Schedule
4 | 4 |  | Detailed description of the quality control testing and research facilities. If the equipment is manufactured under license, the name of the licensee and details of the licensing arrangements, such as the duration of the license, the facilities provided to the Bidder by the licensee and whether future improvements are available or not etc. A copy of the license agreement may be attached. Quality Control/ Quality assurance plan must also be submitted. |  | Provided as per Schedule
5 | 7 | a | Names, qualifications and experience of the key technical personnel along with Resumes. |  | Provided as per Schedule
6 | 7 | b, i | Nos. of total permanent staff on roll of the company. |  | Provided as per Schedule
7 | 7 | b, ii | Nos. of total qualified |  | Provided as per Schedule
8 | 8 |  | The detailed description of the O&M experience of the Bidder or the O&M subcontractor on behalf of the Bidder of satisfactory system performance from the current owners of installed and operated systems or its clients at the time it installed, operated and maintained the system. The information shall contain at least: |  | Provided as per Schedule
9 | 8 | i | (i) Detailed list of all the sites with the affirmation that the bidder played the O&M role in the turnkey installation of these systems. |  | Provided as per Schedule
10 | 8 | ii | (ii) Ground mounted PV turnkey installations >1 MWp with stating of actual MWp per project, project location, date of commissioning, module type, Inverter type and the details of O&M role performed. |  | Provided as per Schedule
11 | 8 | iii | (iii) Biogas installations >50 kW or 100 m3 with stating of actual MWp per project, project location, date of commissioning, Design Type, Construction materials, Biogas Generators and the details of O&M role performed. |  | Provided as per Schedule
12 | 8 | iv | (iv) References and contact data (mail and phone) from owners of all installations > 500 kW with quotes of the corresponding system, Performance Ratios, as well as system performance vs. initial yield assessment per year since the installation. |  | Provided as per Schedule
13 | 8 | v | (v) Approval from bidder to owners or owner Representatives to answer questions freely regarding the past performance of the bidder and performance of the system against contractual obligations. |  | Provided as per Schedule
14 | 9. |  | The time since the manufacturer has been in this business and the time since he has been doing work of similar nature. |  | Provided as per Schedule
15 | 10 |  | The time since the particular equipment offered has been manufactured and the time for which it has been in service. The manufacturer shall have the experience stated in Sub-Clause IB 13.4(a). |  | Provided as per Schedule
16 | 11 |  | Reference lists of similar works done by the Bidder in its country and abroad indicating the name of customer, description and quantity of product, year of supply and the approximate value. This is an important consideration and should be filled in with full details (attach separate sheet if needed) |  | Provided as per Schedule
17 | 12 |  | Details of projects under execution and future contractual commitments (for each partner, in case of a joint venture). |  | Provided as per Schedule
18 | 13 |  | Banking reference, names of banks and addresses may be given to whom reference regarding financial capability of the Bidder may be made, with authority to make inquiries from the Bidder’s bankers and clients regarding any financial and technical aspects (for each partner, in case of a joint venture) |  | Provided as per Schedule
19 | 13 | a | (a) Detail of OD limit allowed to the firm by the bank for the business including amount and its validity period. |  | Provided as per Schedule
20 | 14 |  | Health, Safety and emergency plan as well as Risk Management plan for the project. Bidder should provide ISO certifications or other similar proof. |  | Provided as per Schedule
21 | 15 |  | Detailed/ Integrated work plan along with methodology to complete the assignment. |  | Provided as per Schedule
22 | 16 |  | Training and Employment plan of local work force. |  | Provided as per Schedule
23 | 17 |  | Information on any litigation or arbitration resulting from contracts completed or under execution by the Bidder over the last ten (10) years. The information shall indicate the parties concerned, the matter of dispute, the disputed amounts and the result thereof (for each partner, in case of a joint venture). |  | Provided as per Schedule
Schedules to Technical Bid
24 | Schedule A |  | Specific Works Data |  | Any Guaranteed characteristics as per Schedule
25 | Schedule B |  | Project Organization |  | Complete Project organization information provided as per Schedule
26 | Schedule C |  | Method of Performing Works |  | Details on Mobilization Schedules ( if required)
27 | Schedule D |  | Proposed Program of Works |  | Details on proposed Construction Schedule
28 | Schedule E |  | Proposed Sub-contractors |  | List of proposed sub-contractors and Equipment Manufacturers as per Schedule
29 | Schedule F |  | Equipment |  | Details on the Equipment provided as per Schedule
30 | Schedule G |  | JV agreement |  | Any JV agreements as per Schedule
Schedules to Financial Bid
31 | Schedule J |  | Integrity Pact |  | Provided as per Schedule
32 | Schedule K |  | Estimated Progress Payments |  | Price for the individual plant equipment, services and spare parts provided as per schedule
33 | Schedule L |  | Lump Sum Cost Breakup for Major Cost Items |  | Price for the individual plant equipment, services and spare parts provided as per schedule
34 | Section 8 |  | Bid Security |  | Provided as per Section 8.
35 |  |  | Summary of Bid Price |  | Price for the individual plant equipment, services and spare parts provided as per schedule
[8 empty] | engineers on roll of the | company.